Ovation

Basic Functions

Software Validation Test Procedure

Software Validation Test Procedure Revision 1.X

SW Version:   Ov 4.0.0

Start Date:       11/02/2024

Tester Name:   Gaurav Agarwal

Product Development Department

Emerson

Power and Water Solutions

1000 Westinghouse Drive

Suite 500

Cranberry Township, PA 16066

This document contains information that is proprietary to Emerson Automation Solutions; it is intended for internal Emerson use only. This document, and the information that it contains, are to be held against public access and should not be disclosed or transmitted, in whole or in part, without the written authorization of Emerson Automation Solutions.

# Document Revisions Index (page 1)

| Rev | Date | Section | Description | Reviser |
| --- | --- | --- | --- | --- |
| 1.0 | 06-19-03 06-25-03 06-30-03 | All All All | Original SVT. Misc. additions per Validator comments and new 5.5, 5.6 and 5.7. Comments per Validator review. | IC IC IC |
| 1.1 | 08-01-03 | All | Minor Changes per Val and Dev review. | IC |
| 1.2 | 10-21-03 | 5.8 | Added Simulator and Advanced Controller test. | IC |
| 1.3 | 06-14-04 | 5.7, 5.9 | Addressed SVTP Fidings #7, 11. | IC |
| 1.4 | 04-04-05 | 5.1 | Addressed fidings #632, 633, and 634. | IC |
| 1.5 | 04-14-05 | All | Updated to latest standard template. | IC. GM |
| 1.6 | 10-27-05 | 6, 8, 9 | Change per Finding #1147, 1571. | IC |
| 1.7 | 05-02-07 | 7 | F#3051 (5.7); Added Freelance Test section #10 | IC, GM |
| 1.8 | 08-01-07 | 7, 7, 5, 2 | Clarified menu tests, added printer tests, alarm printer test, and membrane keyboard test. | IC |
| 1.9 | 11-30-07 | 7, 4, 7, 9 | F #3876, 3660, 4029, 3487. | IC |
| 1.A | 05-01-08 |  | F #4385 | IC |
| 1.B | 05-28-08 | 6 | F #16522, Added tests from “System Functions SVTP” so its not needed/maintained. | IC, JCM |
| 1.C | 08-04-08 | 9, 7, 4, 8 | F# 4656, 4635, 4636, 4679. | IC |
| 1.D | 08-22-08 | 4, SO, | F# 4562, 4738. | IC |
| 1.E | 02-24-09 | 2, 4, 7 | F# 4981, 5005, 5010. | IC |
| 1.F | 2-27-09 | 13, 14 | Add Windows and Solaris CD Verification Tests | IC, JCM |
| 1.G | 5-14-09 | 11, 12 | Added Point Viewer. Added details to OPH test. | IC |
| 1.H | 2-02-10 | 7, 7, 15 | F#5579, 5837. Added Specialty Module tests. | IC |
| 1.I, 1.J | 2010 |  | Re-wrote Multi Net tests. Messed up file rev somehow. | IC |
| 1.K | 02-10-11 | 7, 7, 9, 5, 7, 3, 7, 7, 7,11,11, 11 | F#6740, 6808, 6836, 6916, 6918, 6920, 6925, 6926, 6934, 6943, 6946, 6949. Fixed 5.3.4 which caused errors in TOC. | IC |
| 1.L | 07-05-11 | 1, 5, 9, 3&4. 15 | F#7646, 7596, 7289, 7647. Clarified Specialty module test. | IC |
| 1.M | 07-28-11 | 11, 3&4 | Added CB to MultiNet test, F#7705. | IC |
| 1.N | 09-27-12 | 5 | Minor typo corrections. Added VC test 5.8.7. | IC |
| 1.O | 02-21-14 | 12, 5, 15 | Removed HSR, LS, eDB tests. F#10053. Added RVP. | IC |
| 1.P | 07-17-15 | 15 | F#3400. | IC |
| 1.Q | 4-25-16 | 5 | F#34778; Enhanced Section 5.13 to include steps for upgrade and new install; Included HART module test in section 5.15 | IC, CG |
| 1.R | 01-31-17 | 5.8 | Added tests for Controller with new flash. | Innocenzo Capani (IC) |

# Document Revisions Index (page 2)

| Rev | Date | Section | Description | Reviser |
| --- | --- | --- | --- | --- |
| 1.S | 07-06-17 | 5.8 | Added test 5.810 for Controller IO Modules alarms, etc tests, | Innocenzo Capani (IC) |
| 1.T | 08-01-17 | 5.9, 5.16 | Added test 5.9.8 for System Registration Utility (SRU), Added test case 5.16 for Database Import and Export functionality | Innocenzo Capani (IC), Chandresh Gupta (CG) |
| 1.v | 08-01-19 | 5.10 | Added test 5.10 for Controller Diagnostic | Madhukar Sahay(MS) |
| 1.V | 02-26-21 | 5.18 | Ovation Dektop Layout feature | Alshay Jhamb (AJ) |
| 1.W | 07-29-22 | 5.1 to 5.18 | Modified test of 5.1 to 5.18 | Madhukar Sahay(MS),Praishtha (PRS), Ashish Goyal (ASG), Jayakumari (JJ),Vijay Pandey (VP), Puneet Sharma (PSH) |
| 1.X | 9-10-24 | 5.1, 5.2 5.5,5.6 & 5.8 | Mentioned tests for Automation Updated Emerson Address | Sangeeta Chouksey (SC) Madhukar Sahay(MS) |

# Table Of Contents

1.0	Software Test Identifier	6

2.0	Purpose	6

3.0	Approach	6

4.0	Functions To Be Tested And Pass/Fail Criteria	7

5.0	Procedure Steps	8

5.1	TEST CASE 1: Point Functionality	9

5.2	TEST CASE 2: Graphic Functionality	11

5.3	TEST CASE 3: Algorithm Functions Using Graphics	12

5.4	TEST CASE 4: Algorithm Functions Using Sheets	13

5.5	TEST CASE 5:  Alarm Functions	14

5.6	TEST CASE 6:  Trend Functions	16

5.7	TEST CASE 7 : Menu Functions	17

5.8	TEST CASE 8:  Controller Functions	20

5.9	TEST CASE 9:  Engineering Functions	23

5.10	TEST CASE 10: Controller Diagnostics	25

5.11	TEST CASE 11: Freelance Tests	26

5.12	TEST CASE 12: Multi-Net Functions	27

5.13	TEST CASE 13:   Historian Functions	31

5.14	TEST CASE 14 : Windows Release CDs/DVD Verification	31

5.15	TEST CASE 15 : Solaris Release  CDs Verification	36

5.16	TEST CASE 16 : Specialty Modules	38

5.17	TEST CASE 17 : Database Import and Export Functionality	40

5.18	TEST CASE 17 : Ovation desktop tools	40

6.0	Approvals	42

7.0	Test Sign-Off Form	44

- Software Test Identifier

This document is the Ovation Basic Functions Test Procedure.

- Purpose

The purpose of this test procedure is to detail the tests which are to be done to validate the basic functionality of Ovation. This test is for regression testing purposes.

- Approach

The test will be conducted as described below.

- An Ovation database must be created. This database will contain points necessary to exercise the features listed in section 4.

- Perform appropriate tests as listed in section 4. Section 5 details these tests.

- Any problems found will be reported as findings.

- As needed or upon completion, a status shall be generated by the validators and sent to the appropriate personnel via email.

- The standard documentation on the company Intranet will be referenced throughout the testing.  Any recommended changes will be reported as findings for the Technical Writing Group.

- Functions To Be Tested And Pass/Fail Criteria

Please refer to the appropriate documentation for details on the features to be tested. Refer
to section 5.0  for details on the testing of  these features. If the features don’t function as described, the test fails. The results should be marked by “Pass”, “Fail”, or “NA” (not applicable).

  - FUNCTION 1 -  Point Functionality

  - FUNCTION 2 -  Graphic Functionality

  - FUNCTION 3 -  Algorithm Functions Using Graphics

  - FUNCTION 4 -  Algorithm Functions Using Sheets

  - FUNCTION 5 -  Alarm Functions

  - FUNCTION 6 -  Trend Functions

  - FUNCTION 7 -  Menu Functions

  - FUNCTION 8 – Controller Functions

  - FUNCTION 9 -  Engineering Functions

  - FUNCTION 10 -  Freelance Tests

  - FUNCTION 11 – Multi-Net Functions

  - FUNCTION 12 – Historian Functions

  - FUNCTION 13 – Windows Release Master CDs Verification

  - FUNCTION 14 – Solaris Release Master CDs Verification

  - FUNCTION 15 – Specialty Modules

  - FUNCTION 16 – Database Import and Export Functionality

- Procedure Steps

Test Configuration:

The following software configuration is needed to perform the tests in this procedure.

- Ensure that the associated software packages are at the proper released level.  This includes the Controller, Control Builder, Engineer Station and Opcon software.

Test Setup:

The following  test setup must be performed before this test procedure can be run.

- Ensure that the Drop has database (points) applicable to the features being 
  tested.

  - TEST CASE 1: Point Functionality

| 5.1.1 Test: Run the listed tests using point information. Mark each test result as “P” or “F” (Pass/ Fail). Note: This test should run through Automation except 5.1.1a & C. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP | DU |  |
| a-Scan Off |  |  | NA |  |  |  | NA |  |  |  | NA |  |  | NA | NA |  |
| b-Enter Value (Force On & Off for LP & DP) |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| c-Scan On |  |  | NA |  |  |  | NA |  |  |  | NA |  |  | NA | NA |  |
| d-Go into Alarm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e-Alarm Chk Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| f-Alarm Chk On |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| g- Change Alarm Limits |  | NA | NA |  |  | NA | NA |  | NA |  | NA |  | NA | NA | NA |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1.2 Test: Using points with live I/O, verify that the value displays on point information. Note the current value (a). Pull out the I/O card note the results (b). Push the card in, note results (c). Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast Scan LA | Fast ScanLD | Fast ScanLP | Fast ScanDA |  | Fast Scan DD | Fast Scan DP | Slow Scan LA | Slow Scan LD |  | Slow Scan LP | Slow ScanDA | Slow ScanDD | Slow ScanDP |  |  |
| a-Current HW Value Update |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b- Bad HW Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c- Good HW Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.1.3 Test: PI Tabs. Verify the correct operation of all the functions of the Point Information tabs. Note : This |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 5.1.4 Test: PI Hardware Tab. Verify the values of I/O Scale (YS) and I/O Bias (YB) should be 0.016 and 0.004, respectively for LA points of any of the 4-20mA analog output module. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  | Initials: |  | Pass/Fail | Findings# |  |  |
| Comments: |  |  |  |  |  |  |  |
| 5.1.5 Test: PI Value Tab. Verify that the value ribbon tab provide the value of each specific bit in the second row buttons for: |  |  |  |  |  |  |
| Date: | Initials: |  | Findings# |  |  |  |
| a) Long Packed Point. |  |  |  |  |  | P/F/F#: |
| b) Deluxe Packed Point. |  |  |  |  |  | P/F/F#: |
| 5.1.6 Test: PI Value Tab. Verify that for the Forced bits, the background color is “Orange” in the second row of value ribbon tab for: |  |  |  |  |  |  |
| Date: | Initials: |  | Findings# |  |  |  |
| a) Long Packed Point. |  |  |  |  |  | P/F/F#: |
| b) Deluxe Packed Point. |  |  |  |  |  | P/F/F#: |
| 5.1.7 Test: PI Value Tab. Verify that when the point is configured for inversion, “” symbol displayed after the value on the current value bar for: |  |  |  |  |  |  |
| Date: | Initials: |  | Findings# |  |  |  |
| a) Long Packed Point. |  |  |  |  |  | P/F/F#: |
| b) Deluxe Packed Point. |  |  |  |  |  | P/F/F#: |
| c) Long Digital Point. |  |  |  |  |  | P/F/F#: |
| d) Deluxe Digital Point. |  |  |  |  |  | P/F/F#: |
| 5.1.8 Test: PI Value Tab. Verify that when the point is configured for inversion, “” symbol has foreground color set to white and the background color is set to black for: |  |  |  |  |  |  |
| Date: | Initials: |  | Findings# |  |  |  |
| a) Long Packed Point. |  |  |  |  |  | P/F/F#: |
| b) Deluxe Packed Point. |  |  |  |  |  | P/F/F#: |
| c) Long Digital Point. |  |  |  |  |  | P/F/F#: |
| d) Deluxe Digital Point. |  |  |  |  |  | P/F/F#: |
| 5.1.9 Test: PI Value Tab. Verify that when the point is configured for inversion, tooltip clarifies the inversion symbol {“” symbol} for: |  |  |  |  |  |  |
| Date: | Initials: |  | Findings# |  |  |  |
| a) Long Packed Point. |  |  |  |  |  | P/F/F#: |
| b) Deluxe Packed Point. |  |  |  |  |  | P/F/F#: |
| c) Long Digital Point. |  |  |  |  |  | P/F/F#: |
| d) Deluxe Digital Point. |  |  |  |  |  | P/F/F#: |
| 5.1.10 Test: Verify that for a point opened in PI, clicking on “where used” and then “Go to Reference”, the signal diagram opens: |  |  |  |  |  |  |  |
| Date: |  | Initials: |  | Pass/Fail | Findings# |  |  |
| Comments: |  |  |  |  |  |  |  |

  - TEST CASE 2: Graphic Functionality

| 5.2.1 Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). Note : This test should run through Automation except 5.2.1 j. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD | Slow OPP LP |  | Slow OPPDA | Slow OPPDD | Slow OPPDP | DU |  |
| a-Scan Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| b-Enter Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| c-Scan On |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| d-Go into Alarm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e-Alarm Ack |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f-Alarm Reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| g-Alarm Chk Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| h-Alarm Chk On |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| i-HW Value Update |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| j- Bad HW Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.2.2 Test: Using dual Opcons display 8 different Custom Graphics, 4 on one Opcon and 4 on the other. Verify correct operation. NOTE: for Ovation 3.2.0 and newer, display 16 total. 8 on one Opcon and 8 on the other. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  | Pass/Fail |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.2.3 Test: Verify Membrane Keyboard operation Attach a Membrane Keyboard to a workstation. Verify correct operation of the keyboard. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  | Pass/Fail |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

  - TEST CASE 3: Algorithm Functions Using Graphics

| 5.3.1 Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# |  |  |  |  |  |
| MASTATION | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: |  | Other Basic Functionality: |
| XMA2 | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias (NA for Sol Sys): | Digital Entry Output : |  | Other Basic Functionality: |
| SETPOINT | NA | NA |  | Raise/Lower Output: | NA |  |  | Other Basic Functionality: |
| PID | NA | NA |  | NA | NA | NA |  | Other Basic Functionality: |
| DIGITAL FACEPLATE; NA; NA; NA; NA. |  | NA |  | NA | NA | NA |  |  |
| Comments: |  |  |  |  |  |  |  |  |

| 5.3.2 Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Findings# |  |  |  |  |  |  |  |
|  | KEYBOARD | HIGHLOWMON |  | TRANSFER | ONESHOT |  |  |  | DIGITAL DEVICE MACRO |
| Basic Functionality |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |
| 5.3.3 Test: Verify the Basic Functionality of the Graphic Builder Mark each test result as “P” or “F” (Pass/ Fail). Note : This test should be marked as NA for Solaris Windows Opcons. Note : This test should run through Automation.Except 5.3.3 a to i. |  |  |  |  |  |  |  |  |  |
| Date: | Initials: | Findings# |  |  |  |  |  |  |  |
| a) verify an existing graphic can be edited and saved. |  |  |  |  |  |  |  | Pass/Fail: |  |
| b) verify that the same graphic can be compiled and loaded. |  |  |  |  |  |  |  | Pass/Fail: |  |
| c) verify that the same graphic displays and updates correctly. |  |  |  |  |  |  |  | Pass/Fail: |  |
| d) Create a new graphic and repeat tests a, b, and c. |  |  |  |  |  |  |  | Pass/Fail: |  |
| e) Change the type of graphics and verify it gets saved. |  |  |  |  |  |  | Pass/Fail: |  |  |
| f) Change the size of mainscreen,subwindow,window and verify it gets updated. |  |  |  |  |  |  | Pass/Fail: |  |  |
| g) Verify that Integrated source editor and generic text editor is opened correctly. |  |  |  |  |  |  | Pass/Fail: |  |  |
| h) Verify that macro parameters dialog is opening from main screen. |  |  |  |  |  |  | Pass/Fail: |  |  |
| i) Verify that resize options are working correctly in the main screen. |  |  |  |  |  |  | Pass/Fail: |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |
| 5.3.4 Test: Verify screen copies of the following items can be done. |  |  |  |  |  |  |  |  |  |
| a) Custom Graphics |  |  | P/F/F#: |  |  | Initials, Date: |  |  |  |
| b) Error Screen |  |  | P/F/F#: |  |  | Initials, Date: |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |

  - TEST CASE 4: Algorithm Functions Using Sheets

| 5.4.1Test: Run the listed tests using sheets. Mark each test result as “P” or “F” (Pass/ Fail). Note: This test can be excuted by algtest.exe. Need to explore and create testcase. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# Pass/Fail |  |  |  |  |  |
| XPID | Manual/Auto/Cascade: | Raise/Lower Setpoint: |  | Raise/Lower Output: | Digital Entry Setpoint: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| MASTATION | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| XMA2 | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| SETPOINT | NA | NA |  | Raise/Lower Output: | NA | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| PID | NA | NA |  | NA | NA | NA | Change Tuning Contants: | Other Basic Functionality: |
| DIGITAL DEVICE MACRO |  | NA |  | NA | NA | NA | Change Tuning Contants: |  |
| Comments: |  |  |  |  |  |  |  |  |

| 5.4.2 Test: Run the listed tests using sheets. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# |  |  |  |  |  |  |  |  |
|  | KEYBOARD |  | HIGHLOWMON |  |  | TRANSFER | ONESHOT |  |  |  | AVALGEN,ONDELAY,GAINBIAS,RESETSUM |
| Basic Functionality |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| 5.4.3 Test: Using Dual Opcons : open 4 Signal Diagrams on each monitor. Display 4 different Ladder Sheets on one monitor and 4 different Control Sheets on the other monitor. Perform the tests below, |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  |  |  |  |  |  |  |  |
| a) Verify the workstation still operates even though CPU may be near 100% |  |  |  |  |  |  |  |  |  | P/F/F#: |  |
| b) Verify the sheets display and update normally. |  |  |  |  |  |  |  |  |  | P/F/F#: |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| 5.4.4 Test: The Control Logic Navigation application – Verify the basic functionality of the Control Logic Navigator. |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  | Pass/Fail/NA: |  |  |  | Findings # |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

  - TEST CASE 5:  Alarm Functions

| 5.5.1Test: Run the listed tests using while monitoring the Alarm List and Alarm History. Mark each test result as “P” or “F” (Pass/ Fail). Note : This test should run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  | Initials: |  |  |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Operation |  | Fast OPP LA | Fast OPPLD |  |  | Fast OPPLP |  | Fast OPPDA |  | Fast OPP DD | Fast OPP DP |  |  |  | Slow OPP LA | Slow OPP LD |  |  | Slow OPP LP |  | Slow OPPDA |  |  |  | Slow OPPDD | Slow OPPDP |  | DU |  |  |
| a- Cause point to go into Alarm. Verify the alarm appears on Alarm List & History. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b- Cause analog point to have an incremental alarm Cause Packed points to have other bits go into alarm. Verify the alarm changes appears on the Alarm List & History. |  |  | N/A |  |  |  |  |  |  | N/A |  |  |  |  |  | N/A |  |  |  |  |  |  |  |  | N/A |  |  |  |  |  |
| c- Cause point to return from Alarm. Verify the return appears on Alarm List & History. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e-Alarm Ack |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f-Alarm Reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.2 Test: Consistent Alarm Lists . Using two Operator stations, display and compare that the lists are consistent. Generate new alarms, verify consistency. Ack alarms, verify consistency. Reset alarms, verify consistency. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  |  |  |  |  | Pass/Fail |  |  |  |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.3 Test: Consistent Alarm Lists (after Opcon Reset) . Open alarm windows on two Operator stations (say drop x & drop y) & check alarms are consistent. Example – Generate an alarm1, check both Operator stations are showing it, put drop x off highway and generate another alarm2, check it on drop y. Now put drop x on highway, check both drops x & y are showing alarm 1 & 2. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  |  |  |  |  | Pass/Fail |  |  |  |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.4 Test: Alarm powering off Eng/Opcon : Power off an Engineer’s Station/Opcon . Verify that Alarm List and History report the event. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  |  |  |  |  | Pass/Fail |  |  |  |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.5 Test: Verify Alarm Printer functionality Attach an Alarm Printer to a workstation. Verify operation. Note: This test should be marked as NA for Solaris Windows opcon releases. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials:: |  |  |  |  |  |  |  |  | Pass/Fail/NA: |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.6 Test: Verify Audio Alarms Verify that Audio Alarms function correctly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials:: |  |  |  |  |  |  |  |  | Pass/Fail/NA: |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.7 Test: Verify the Alarm Check Remove tab is renamed as Alarm Suppressed in Alarm Window and its functionality is working fine. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials: |  |  |  |  |  |  |  |  | Pass/Fail: |  |  |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.8 Test: Verify the UC (Seconds)/UD (Nanoseconds) fields for Alarm Check ON/OFF reflects correct time in Point Information Window as in Alarm suppressed tab in Alarm Window . |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials: |  |  |  |  |  |  |  |  | Pass/Fail: |  |  |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.9 Test: Verify that the ribbon bar button and point menu right click option is added for writing comment /reason, when Alarm Check OFF is perfomed. As like in Ovation Point Information window for Alarm Check ON/OFF and right click options are available. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials: |  |  |  |  |  |  |  |  | Pass/Fail: |  |  |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.10 Test: Verify the ability to store/display an 80 byte ASCII comment/reason entered by user when Alarm Check ON/OFF is performed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  | Initials: |  |  |  |  |  |  |  |  | Pass/Fail: |  |  |  |  |  |  |  |  |  |  | Findings # |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Take any point into alarm and performe alarm check OFF operation ,Verify at the schduled task time Reconfirm alarm check remove window popup appears along with the countdown time as mentioned in the Count Down Time at the network level on configured drop. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Create a point take it to alarm state and then activate Alarm Shelving feature verify the shelving status from the code column in Alarm suppress tab in Alarm Window. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Shelve the points. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Verify comment field (RE) appears. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Verify if entered comments are saved. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Enter shelve duration and Shelve the point,verify the Return To Service Time is “Time of Alarm Check Remove/Shelve + shelve duration” present in Alarm tab of Point Information and also verify it is functioning. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Enter Shelve duration and Shelve the point , verify the Return To Service Time is “Time of Alarm Check Remove/Shelve + shelve duration” present in Alarm tab of Point Information and Unshelve it manually before Return To Service Time expires & also verify it is Unshelved. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| - Verify Alarm Cutout Functionality is working fine. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Verify the Alarm Check Remove overrides the alarm shelving feature for all points. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | P/F/F#: |  |  |  |  |  |  | Date: |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.11 Test: Alarm summary Test Verify Alarm Summary option is working fine for Remote network alarms. Configure Alarm Summary for current network as well as on any of the configured Remote network. Configure Alarm Server and Enable Alarm Summary option. Download and Reboot the Alarm Collector , Dataserver drop/s of current network as well as on of the configured Remote network. Perform below tests and Mark your results.. Date:; Initials:; Pass/Fail:; Findings #. Current Network and Remote Network Name:. - Verify Alarm Summary point for the Remote network is going in alarm when any of the point in that network is in alarm.; P/F/F#:; Date:. - Verify for this Remote network, only Summary point is visible in Alarm Window. Any other point of this Remote network should not be visible.; P/F/F#:; Date:. - Right click on Alarms summary point and verify Remote Alarm Summary window can be opened to view this Remote Network’s point in alarm.; P/F/F#:; Date:. |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.5.11 Test :Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  |  |  |  | Ovation level of Net 1: |  |  |  |  |  |  |  |  |  |  | Note Ovation level of Net 2 : |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  |  |  |  |  |  |  |  |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |  |  |  |  |  |  |  |  |
| Function to Test: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a) Verify the new fields (UC,,UE,,UG,Cutout Status,PW,Return To Service Time,RE & DM are displayed in Point Information Window. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |  |  |  |  |  |  |  |
| b)General Point Information Display Functions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d) Graphics Display |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f) Live Trend Display |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| g) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| h) Alarm Display |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i) Alarm Clear/Ack |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| j) Point Review, Point Viewer/SPD(System Point Directory) Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD (System Point Directory) is local only and NA for Solaris. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| k) Alarm Check ON/OFF |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| l) Alarm Shelve/Unshelve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |  |  |  |  |  |  |  |
| m)Limit Check On/Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

  - TEST CASE 6:  Trend Functions

| 5.6.1 Test: Perform Live Trends using the point types listed. Verify the Trend Values and Trend Timestamps are both correct. Mark each test result as “P” or “F” (Pass/ Fail). Note: This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
|  | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP |  |  |
| Values OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Timestamps OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.2 Test: Perform Historical Trends using the point types listed. Verify the Trend Values and Trend Timestamps are both correct. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP |  |  |
| Values OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Timestamps OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.3 Test: Trend configuration –change default values for analog/digital points ( in Studio-Configuration-Trend-Trend default for Windows), check the same in trend window of operator station. Verify correct operation. Note:This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.4 Test: Display 4 different Live Trends on the available windows of the Opcon. Verify correct operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| 5.6.5 Test: Display 4 different Historical Trends on the available windows of the Opcon. Verify correct operation and timestamp. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.6 Test: Tabular Trend. Verify the Trend Values and Trend Timestamps are both correct. Mark each test result as “P” or “F” (Pass/ Fail). Note: This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Trend Values Pass/Fail/F#: |  |  |  |  | Trend Timestamps Pass/Fail/F#: |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.6.7 Test: Trend Groups : verify correct operation of live and historical trend groups. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

  - TEST CASE 7 : Menu Functions

| 5.7.1 Test: Exercise the “Point Menu” functions (Pt Info, Trend, Summary, Signal) by right clicking on a point in the locations listed below. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |
| Point Location |  | Review | Trend |  | Graphic |  | Point Info |  | Alrm List | Alrm Hist |  | Alrm Unack |  | Alm Reset |
| Pass/Fail : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.7.2 Test: Exercise the “Ovation Applications” Menu functions Verify that each program launches and functions correctly. This test applies to Windows Ovation only.Mark each test result as “P” or “F” (Pass/ Fail). This applies to Windows Ovation only. NOTES: 1) Signal Diagram is for 3.1.x or newer only. Mark NA for other releases 2) Viewer should be marked as NA for Ovation 3.3.1 and newer.. Date:; Initials:; Findings#. Menu Item; Alarms; Error Log; Graphics; Historical Review; Online Help; Point Info; Review; Trend; Viewer; Signal Diagrm. Pass/Fail :. Comments:. |

| 5.7.3 Test: Verify Printing of Ovation Application screens Verify displays associated with Ovation applications can be printed.using the Applicaton’s print function and the operating system screen copy. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Function |  |  |  |  |  |  |  |  | Date, Initials |  |  | Screencopy P/F/NA/F# |  |  | Print Using Application P/F/NA/F# |  |  |  |  |
| a) Trend Display |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b) Alarm List |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| c) 11x17 and 8..5x11 Functional Drawings printed from Control Builder. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| d) 11x17 and 8..5x11 Functional Drawings printed from Signal Diagram. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e) Error Log |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f) Point Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| g) System Viewer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| h) Point Review |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i) Note printer model(s) used: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.7.4 Test: Exercise the Point Review functions. Use the point types listed. Verify that all functions operate correctly. Mark each test result as “P” or “F” (Pass/ Fail). Note: Ovation Solaris does NOT allow filter selection based on Frequency. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Operation |  | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP |  | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA |  | Slow OPPDD | Slow OPPDP |  |  |  |
| Pass/Fail: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 5.7.5 Test: Exercise the “Command Line switches” for Point Information. Enter the commands in command prompt. Verify that each command launches and functions correctly.Mark each test result as “P” or “F” (Pass/ Fail). This applies to Windows Ovation only. For detailed description of this test case please refer manual OVMAN20, Section 18. |  |  |  |
| --- | --- | --- | --- |
| Initials: |  | Findings# |  |
| Commands: | Date: |  | Pass/Fail : |
| Pi.exe [pointname] |  |  |  |
| Pi.exe [ /loadsid ] |  |  |  |
| Pi.exe [/loadpoint ] |  |  |  |
| Comments: |  |  |  |

| 5.7.6 Test: Exercise the “Command Line switches” for Point Review. Enter the commands in command prompt. Verify that each command launches and functions correctly.Mark each test result as “P” or “F” (Pass/ Fail). This applies to Windows Ovation only. For detailed description of this test case please refer manual OVMAN20, Section 18. |  |  |  |
| --- | --- | --- | --- |
| Date: |  | Initials: | Findings# |
| Commands: Review.exe [/source <database ¦ groups>] […] |  |  |  |
| If /source is set to database: |  | Review.exe /source database [/live <[true ¦ false]>] [/netunit <netunitname>] [/drops<dropids>] [/ptname <pointname>] [/desc <engdesc>] [/charst <characteristics>] [/rectypes <recordtypes>] [/freq <frequencies>] [/livefilters <filters>] [/columns <columns>][/execute] |  |
| Operation; Fast OPP LA; Fast OPPLD; Fast OPPLP; Fast OPPDA; Fast OPP DD; Fast OPP DP; Slow OPP LA; Slow OPP LD; Slow OPP LP; Slow OPPDA; Slow OPPDD; Slow OPPDP. Pass/Fail:. |
| Comments: |  |  |  |
| If /source is set to groups: |  | Review.exe /source groups <ptgroupname groupname> <ptgroupnumber groupnumber><ptgrouptype pds ¦ trend> [/live <[true ¦ false]>] [/rectypes <recordtypes>] [/freq<frequencies>] [/livefilters <filters>] [/columns <columns>] [/execute] |  |
| Operation; Fast OPP LA; Fast OPPLD; Fast OPPLP; Fast OPPDA; Fast OPP DD; Fast OPP DP; Slow OPP LA; Slow OPP LD; Slow OPP LP; Slow OPPDA; Slow OPPDD; Slow OPPDP. Pass/Fail:. |

  - TEST CASE 8:  Controller Functions

| 5.8.1 Test: Hard Failover : Power off the primary controller. Verify that the backup takes control and operates correctly. Check that the active alarm list reports this. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: 11/2/2024 | Initials: GA |  |  |  | Pass/Fail P |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.8.2 Test: Soft Failover : Perform a clear and load of the primary controller. Verify that the backup takes control and operates correctly. Check that the active alarm list is correct. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: 11/2/2024 | Initials: GA |  |  |  | Pass/Fail P |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.8.3 Test: Diagnostics Check : Check the status of all the loaded sheets in Controller Diagnostics under the “Sheet Information” and “Control Task Information” tabs. Verify this information reflects the correct operation of the controller. Note:This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: 11/2/2024 | Initials: GA |  |  |  | Pass/Fail P |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.8.4 Test: Simulator Check : Verify that the Controller can be converted to a Simulator. Verify that as a Simulator that it functions correctly. Verify that the simulator can be converted back to a standard Controller. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: 11/2/2024 | Initials: GA |  |  |  | Pass/Fail P |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.8.5 Test: Advanced Controller Check : Verify that the Controller can be converted to an Advanced Controller. Using a Control Builder with Advanced Control capability, add one of each advanced algorithms to the Controller. Verify that the Controller runs normally. Verify that the advanced algorithms can be monitored and tuned. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.8.6 Test: Add, modify, and delete Controller points Verify that the listed point types can be added, modified, and deleted in a Controller. Note:This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: 11/2/2024 | Initials: GA |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
|  | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP |  |  |
| Pass/Fail: | P | P | P | P |  | P | P | P | P |  | P | P | P | P |  |  |
| Comments: On Behalf of Automation team |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 5.8.7 Test: Virtual Controller Check : Verify the basic fucntionality of the Virtual Controller (VC) and Virtual Controller Host. |  |  |
| --- | --- | --- |
| Date: 11/2/2024 | Initials: GA | Pass/Fail/Findings#: |
| Comments: On Behalf of respected team |  |  |

| 5.8.8 Test: Ensure Controllers With New (blank) Compact Flash Start Up Using a controller with a new (blank) compact flash, perform the normal startup steps to ensure the controller starts up normally: -Place a new/blank flash in the controller and power it on -Download, Reboot, and clear the controller -load the controller -check that the controller is operating normally Perform these steps for each of the controller types listed below Note: This test run through Automation except the flash clean. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| Controller Type to be Tested: | Date | P/F/F# |
| a) OCR400 |  |  |
| b) OCR1100 G01 |  |  |
| c) OCR1100 G03 |  |  |
| d) OCR1100 G04 |  |  |
| Comments: |  |  |

| 5.8.9 Test: Creation of New Virtual Controller Host CH) and Virtual Controllers (VCs) Perform the functions listed below to verify a new VCH with new VCs can be configured on a workstation. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| Controller Type to be Tested: | Date | P/F/F# |
| a) Verify a new VCH can be configured on a workstation. |  |  |
| b) Verfiy a new OCR1100 VC can be configured and loaded. |  |  |
| c) Verify a new OCR400 VC can be configured and loaded. |  |  |
| d) Verify a new Advanced OCR1100 VC can be configured and loaded. |  |  |
| Comments: |  |  |

| Test 5.8.10: IO Module sensor alarms, limit alarms, failure alarms, and runtime tests. For the IO module already present in your Controller, when applicable to the module, please verify: -the module reports low & high sensor alarms properly -low and high limit alarms are reported properly -alarms are reported when a module is removed from its slot -alarms return when the module is re-inserted -the module operates normally in a steady-state for 2-3 days or more Add more lines after line “g” as required. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Initials: |  |  |  |  |  |
| IO Module and IO Slot | Low & High Sensor Alarms (P/F/F#/NA) | Low & High Limit Alarms (P/F/F#/NA) | Remove and Re-insert Module (P/F/F#/NA) | Steady State Operation (P/F/F#/NA) | Date(s) of Tests |
| a) |  |  |  |  |  |
| b) |  |  |  |  |  |
| c) |  |  |  |  |  |
| d) |  |  |  |  |  |
| e) |  |  |  |  |  |
| f) |  |  |  |  |  |
| g) |  |  |  |  |  |
| Comments: |  |  |  |  |  |

  - TES CASE 9:  Engineering Functions

| 5.9.1 Test: Windows System : Open Viewer. Verify correct operation. Solaris System : Open SPD List. Verify correct operation. Note: For Ovation Windows 3.3.1 and newer, the Viewer is removed, so this test is NA. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Pass/Fail/NA: |  |  |  |  | Findings# |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.9.2 Test: Clear and Load Operator Station. Verify correct operation. Verify that the RAIMA updates correctly. Note: this test is NA for the Solaris Win Opcon. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.9.3 Test: Tuning Parameters Reconcile : Change tuning parameters from the OPCON PDS window, reconcile the changes in to the database & verify that the changed parameters are reported in the reconciliation window. This is to certify the presence of the changed tuning values in the target controller. Note: this test is NA for the Solaris Win Opcon. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.9.4 Test: Add, modify, and delete Workstation points Verify that the listed point types can be added, modified, and deleted on an Engineering Workstation. Cautions: 1) please be aware of the behavior of EWS points as documented in Findings 3171, 3172, and 3173. 2) This test is NA for the Solaris Win Opcon. Note: This test run through Automation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP |  |  |  |
| Pass/Fail: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.9.5 Test: Power Tools or Studio Verify the basic functionality of the Power Tools for Solaris releases or Studio for Windows releases. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5.9.6 Test: Security Verify the basic functionality of the system Security functions. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| 5.9.7 Test: Control Builder Verify the basic functionality of the Control Builder. Note: This test run through Automation except the flash clean. |  |  |  |
| --- | --- | --- | --- |
| Date: | Initials: |  |  |
| a) verify an existing sheet can be edited and saved. |  |  | Pass/Fail/F#: |
| b) verify that the same sheet can be compiled and loaded. |  |  | Pass/Fail/F#: |
| c) verify that the same sheet displays and updates correctly. |  |  | Pass/Fail/F#: |
| d) Create a new sheet and repeat steps a, b, and c. |  |  | Pass/Fail/F#: |
| Comments: |  |  |  |
| 5.9.8 Test: System Registration Utility (SRU) Verify the SRU runs and collects the system data correctly. Run the SRU on all of the major systems in use for the release. Store the data file on the root directory of the Val release. |  |  |  |
| Date: | Initials: |  |  |
| A1) Verify the SRU runs collects the System #1 data correctly. |  |  | Pass/Fail/F#: |
| B1) Note name of System #1 and location (Pgh/GEC): Note name and location of SRU data file for System #1: |  |  | Pass/Fail/F#: |
| A2) Verify the SRU runs collects the System #2 data correctly. |  |  | Pass/Fail/F#: |
| B2) Note name of System #2 and location (Pgh/GEC): Note name and location of SRU data file for System #2: |  |  | Pass/Fail/F#: |
| A3) Verify the SRU runs collects the System #3 data correctly. |  |  | Pass/Fail/F#: |
| B3) Note name of System #3 and location (Pgh/GEC): Note name and location of SRU data file for System #3: |  |  | Pass/Fail/F#: |
| A4) Verify the SRU runs collects the System #4 data correctly. |  |  | Pass/Fail/F#: |
| B4) Note name of System #4 and location (Pgh/GEC): Note name and location of SRU data file for System #4: |  |  | Pass/Fail/F#: |
| Comments: |  |  |  |

  - TEST CASE 10: Controller Diagnostics

| 5.10.1 Test: Create new control tasks and verify that new as well as old control tasks appear in the Controller Diagnostics window. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date: | Initials: | Pass/Fail/NA: | Findings# |  |
| Comments: |  |  |  |  |
| 5.10.2 Test: Create new control sheets and verify that new as well as old sheets appear in the Controller Diagnostics window. |  |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |  |
| Comments: |  |  |  |  |
| 5.10.3 Test: Create new points and verify that new as well as old points appear in the Controller Diagnostics window. |  |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |  |
| Comments: |  |  |  |  |
| 5.10.4 Test: Add a any bus Ovation module and check that Download Available Firmware functionality is available for the module. |  |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |
| 5.10.5 Test: Verify the Flash Health of a controller in the Controller Diagnostics window. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |  |  | Pass/Fail/NA: | Findings# |
| 5.10.6 Test: Verify that any module can be rebooted from the controller diagnostic. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |
| 5.10.7 Test: Verify the Software Versions tab in the Controller Diagnostics window. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |
| 5.10.8 Test: Verify the OS Version, Kernel Version, and Controller Version fields in the Controller Diagnostics window. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |
| 5.10.9 Test: Verify the Update Backup functionality in the Controller Diagnostics window. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |
| 5.10.9 Test: Verify the “What’s This” functionality in the Controller Diagnostics window. |  |  |  |
| Date: | Initials: | Pass/Fail/NA: | Findings# |
| Comments: |  |  |  |

  - TEST CASE 11: Freelance Tests

| 5.11.1 Test: Freelance Tests. Execise the areas / functions assigned in the STP (or self selected). Briefly list the test performed and the result (Pass/ Fail Finding #)). Add more lines as needed. |  |  |  |
| --- | --- | --- | --- |
| Date: | Initials: | Findings# |  |
| Test Description and Comments : |  |  | P/F/F# |
| d) |  |  |  |
| e) |  |  |  |
| f) |  |  |  |
| Comments: |  |  |  |

  - TEST CASE 12: Multi-Net Functions

| 5.12.1 Test: Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Ovation level of Net 1: |  | Note Ovation level of Net 2 : |  |
|  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |
| Function to Test: |  |  |  |  |  |
| a)General Point Information Display Functions |  |  |  |  |  |
| b) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |
| c) Graphics Display |  |  |  |  |  |
| d) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |
| e) Live Trend Display |  |  |  |  |  |
| f) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |
| g) Alarm Display |  |  |  |  |  |
| h) Alarm Clear/Ack |  |  |  |  |  |
| i) Point Review, Point Viewer/SPD Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD is local only and NA for Solaris. |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be viewed and values update properly. |  |  |  |  |  |
| k) For Ov 3.1 and newer: Verify CB sheets can be tuned. |  |  |  |  |  |
| l) For Ov 3.1 and newer: Verify CB sheets can be added, modified, and deleted. |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| 5.12.2 Test: Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Ovation level of Net 1: |  | Note Ovation level of Net 2 : |  |
|  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |
| Function to Test: |  |  |  |  |  |
| a)General Point Information Display Functions |  |  |  |  |  |
| b) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |
| c) Graphics Display |  |  |  |  |  |
| d) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |
| e) Live Trend Display |  |  |  |  |  |
| f) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |
| g) Alarm Display |  |  |  |  |  |
| h) Alarm Clear/Ack |  |  |  |  |  |
| i) Point Review, Point Viewer/SPD Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD is local only and NA for Solaris. |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be viewed and values update properly. |  |  |  |  |  |
| k) For Ov 3.1 and newer: Verify CB sheets can be tuned. |  |  |  |  |  |
| l) For Ov 3.1 and newer: Verify CB sheets can be added, modified, and deleted. |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| 5.12.3 Test: Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Ovation level of Net 1: |  | Note Ovation level of Net 2 : |  |
|  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |
| Function to Test: |  |  |  |  |  |
| a)General Point Information Display Functions |  |  |  |  |  |
| b) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |
| c) Graphics Display |  |  |  |  |  |
| d) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |
| e) Live Trend Display |  |  |  |  |  |
| f) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |
| g) Alarm Display |  |  |  |  |  |
| h) Alarm Clear/Ack |  |  |  |  |  |
| i) Point Review, Point Viewer/SPD Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD is local only and NA for Solaris. |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be viewed and values update properly. . |  |  |  |  |  |
| k) For Ov 3.1 and newer: Verify CB sheets can be tuned. |  |  |  |  |  |
| l) For Ov 3.1 and newer: Verify CB sheets can be added, modified, and deleted. |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| 5.12.4 Test: Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Ovation level of Net 1: |  | Note Ovation level of Net 2 : |  |
|  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |
| Function to Test: |  |  |  |  |  |
| a)General Point Information Display Functions |  |  |  |  |  |
| b) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |
| c) Graphics Display |  |  |  |  |  |
| d) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |
| e) Live Trend Display |  |  |  |  |  |
| f) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |
| g) Alarm Display |  |  |  |  |  |
| h) Alarm Clear/Ack |  |  |  |  |  |
| i) Point Review, Point Viewer/SPD Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD is local only and NA for Solaris.i) |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be viewed and values update properly. |  |  |  |  |  |
| k) For Ov 3.1 and newer: Verify CB sheets can be tuned. |  |  |  |  |  |
| l) For Ov 3.1 and newer: Verify CB sheets can be added, modified, and deleted. |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| 5.12.5 Test: Exercise Operator Functions in Multi-Network Configuration Verify the listed operations can be done as follows : 1) On Net 1 when accessing data of a remote network (Net 2) 2) On Net 2 when accessing data of a remote network (Net 1) Notes: . -Refer to the test plan for the network levels that should be exercised. -Net 1 refers to the release which is being validated, Net 2 to an existing, released network level. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Ovation level of Net 1: |  | Note Ovation level of Net 2 : |  |
|  |  |  | Verify when on Net 1 and accessing Net 2 Date, P/F/NA/F#: |  | Verify when on Net 2 and accessing Net 1 Date, P/F/NA/F#: |
| Function to Test: |  |  |  |  |  |
| a)General Point Information Display Functions |  |  |  |  |  |
| b) Point Operations : On/Off Scan, Enter Value |  |  |  |  |  |
| c) Graphics Display |  |  |  |  |  |
| d) Graphics : Auto/Manual, Raise/Lower Operations |  |  |  |  |  |
| e) Live Trend Display |  |  |  |  |  |
| f) Historical Trend Display Note : this is NA for Solaris HSR. |  |  |  |  |  |
| g) Alarm Display |  |  |  |  |  |
| h) Alarm Clear/Ack |  |  |  |  |  |
| i) Point Review, Point Viewer/SPD Utils Notes: 1. Viewer is NA for Ovation 3.3.1 and newer. 2. SPD is local only and NA for Solaris. |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be viewed and values update properly. |  |  |  |  |  |
| j) For Ov 3.1 and newer: Verify CB sheets can be tuned. |  |  |  |  |  |
| k) For Ov 3.1 and newer: Verify CB sheets can be added, modified, and deleted. |  |  |  |  |  |
| Comments: |  |  |  |  |  |

  - TEST CASE 13:   Historian Functions

| 5.13.1 Test: Verify the Basic Functionality of the Ovation Process Historian (OPH). |
| --- |
| Record OPH SW Level: |  |  |
| Initials: | Date(s): | P/F/F#: |  |
| a) Verify scanners can be placed on the system to process SOE, Alarm, and Point data. |  |  |  |
| b) Verify scanners are providing SOE, Alarm, and Point data correctly for the Historian. |  |  |  |
| c) Historical Trend : verify analog and digital points (long and deluxe) are trended correctly. |  |  |  |
| d) Historic Point Review: verify analog and digital points (long and deluxe) are reviewed correctly. |  |  |  |
| e) Historic Alarm Review: verify analog and digital points (long and deluxe) alarms are reviewed correctly. |  |  |  |
| f) Verify correct operation of the SOE collection and review. |  |  |  |
| g) Verify correct operation of Operator Events collection and review. |  |  |  |
| h) Verify Reports can be scheduled and triggered. |  |  |  |
| Comments: |  |  |  |

  - TEST CASE 14 : Windows Release  DVD/.iso image

5.14.1.1 Test : Upgrade Ovation Database Server using the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

Existing Version:; Upgrade Version: Date of upgrade:.

- Remove older version of Ovation by following section “To remove Ovation from your computer”; Date:; P/F/F#:. - Follow section “To create an Ovation Database Server” and setup Database Server using release DVD; Date:; P/F/F#:.

Comments:

5.14.1.2 Test : Upgrade Ovation Security Server using the Release DVD by following steps mentioned in Software installation manual.. Initials:.

Existing Version:; Upgrade Version: Date of upgrade:.

- Remove older version of Ovation by following section “To remove Ovation from your computer”; Date:; P/F/F#:. - Follow section “To create an Ovation Security Server” and setup OSS using release DVD or release .iso image release DVD; Date:; P/F/F#:.

Comments:

5.14.1.3 Test : Upgrade Ovation Operator Station using the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

Existing Version:; Upgrade Version: Date of upgrade:.

- Remove older version of Ovation by following section “To remove Ovation from your computer”; Date:; P/F/F#:. - Follow section “To create an Ovation Operator Station on a Windows 7 system” and setup EWS using release DVD or ISO; Date:; P/F/F#:.

Comments:

5.14.1.4 Test : Upgrade Ovation Base Station using the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

Existing Version:; Upgrade Version: Date of upgrade:.

- Remove older version of Ovation by following section “To remove Ovation from your computer”; Date:; P/F/F#:. - Follow section “To create an Ovation Base Station on a Windows 7 system” and setup BS using release DVD or ISO; Date:; P/F/F#:.

Comments:

5.14.1.5 Test : Upgrade Ovation Virtual Controller Host using the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

Existing Version:; Upgrade Version: Date of upgrade:.

- Remove older version of Ovation by following section “To remove Ovation from your computer”; Date:; P/F/F#:. - Follow section “To create an Ovation Operator Station on a Windows 7 system” and setup VCH using release DVD or ISO; Date:; P/F/F#:.

Comments:

5.14.1.6 Test : Upgrade Ovation Virtual Controller. Perform below operations by following steps mentioned in Virtual Controller User Guide.. Initials:.

- Download the Virtual Controller drop; Date:; P/F/F#:. - Reboot the Virtual Controller drop; Date:; P/F/F#:. - Clear the Virtual Controller drop; Date:; P/F/F#:.

- Load the Virtual Controller drop; Date:; P/F/F#:.

Comments:

5.14.1.7 Test : Upgrade Ovation Controller. Perform below operations by following steps mentioned in Developer Studio User Guide.. Initials:.

- Download the Controller drop; Date:; P/F/F#:. - Reboot the Controller drop; Date:; P/F/F#:. - Clear the Controller drop; Date:; P/F/F#:. - Load the Controller drop; Date:; P/F/F#:. - Deltree (or Clear Flash) of the Controller drop; Date:; P/F/F#:. - Reload the Controller drop; Date:; P/F/F#:. Comments:

5.14.2.1 Test : Install a new Ovation Database Server from the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

- Install Windows Server 2012 R2 Standard Edition - English version - 64-bit on the machine; Date:; P/F/F#:. - Promote Windows Server 2012 R2 machine to a Primary Domain; Date:; P/F/F#:. - Verify the promotion of the Primary Domain Controller; Date:; P/F/F#:. - Configure the DNS to only listen/respond to the Ovation NIC; Date:; P/F/F#:. - Install security patches for Windows Server 2012 R2 operating system; Date:; P/F/F#:. - Install OHI driver and configure OHI NICs. Refer section “Installing and configuring drivers”; Date:; P/F/F#:. - Reconfigure the DNS client settings as part of prerequisite; Date:; P/F/F#:. - Follow section “To create an Ovation Database Server” and setup Database Server using release DVD or ISO; Date:; P/F/F#:.

- Install Licenses; Date:; P/F/F#:.

- Create System, Network and Unit folder; Date:; P/F/F#:. - Configure system drops as needed; Date:; P/F/F#:.

Comments:

5.14.2.2 Test : Install a new Ovation Security Server from the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

- Install Windows Server 2012 R2 Standard Edition - English version - 64-bit on the machine; Date:; P/F/F#:. - Promote Windows Server 2012 R2 machine to a Primary Domain; Date:; P/F/F#:. - Verify the promotion of the Primary Domain Controller; Date:; P/F/F#:. - Configure the DNS to only listen/respond to the Ovation NIC; Date:; P/F/F#:. - Install security patches for Windows Server 2012 R2 operating system; Date:; P/F/F#:. - Install OHI driver and configure OHI NICs. Refer section “Installing and configuring drivers”; Date:; P/F/F#:. - Reconfigure the DNS client settings as part of prerequisite; Date:; P/F/F#:. - Follow section “To create an Ovation Security Server” and setup OSS using release DVD or ISO; Date:; P/F/F#:. Comments:

5.14.2.3 Test : Install a new Ovation Operator Station from the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

- Install Windows 7 English version - 64-bit on the machine; Date:; P/F/F#:. - Install security patches for Windows 7 64-bit operating system; Date:; P/F/F#:. - Install OHI driver and configure OHI NICs. Refer section “Installing and configuring drivers”; Date:; P/F/F#:. - Join the computer to a domain in order for it to become part of the Ovation system; Date:; P/F/F#:. - Follow section “To create an Ovation Operator Station on a Windows 7 system” and setup EWS using release DVD or ISO; Date:; P/F/F#:. Comments:

5.14.2.4 Test : Install a new Ovation Base Station from the Release DVD or ISO by following steps mentioned in Software installation manual.. Initials:.

- Install Windows 7 English version - 64-bit on the machine; Date:; P/F/F#:. - Install security patches for Windows 7 64-bit operating system; Date:; P/F/F#:. - Install OHI driver and configure OHI NICs. Refer section “Installing and configuring drivers”; Date:; P/F/F#:. - Join the computer to a domain in order for it to become part of the Ovation system; Date:; P/F/F#:. - Follow section “To create an Ovation Base Station on a Windows 7 system” and setup BS using release DVD or ISO; Date:; P/F/F#:. Comments:

5.14.2.5 Test : Configuring Ovation Virtual Controller Host / Virtual Controller by following steps mentioned in Virtual Controller User Guide.. Initials:.

- Reload an Ovation Station and configure it as Virtual Controller Host; Date:; P/F/F#:. - Configure Ovation VCH drop port; Date:; P/F/F#:. - Create and configure network bridge for VCH; Date:; P/F/F#:. - Create and Configure Ovation Virtual Controller; Date:; P/F/F#:. Comments:

5.14.2.6 Test : Configuring Ovation Controller by following steps mentioned in Developer Studio User Guide. Note: This test run through Automation except 5.14.2.6 a,f.. Initials:.

- Insert Controller drop; Date:; P/F/F#:. - Download the Controller drop; Date:; P/F/F#:. - Reboot the Controller drop; Date:; P/F/F#:. - Clear the Controller drop; Date:; P/F/F#:. - Load the Controller drop; Date:; P/F/F#:. - Deltree (or Clear Flash) of the Controller drop; Date:; P/F/F#:. - Reload the Controller drop; Date:; P/F/F#:. Comments:

  - TEST CASE 15 : Solaris Release  CDs Verification

| 5.15.1 Test : Starting from a known release version, upgrade the system to the Release software. Record the existing version and the upgrade version. System: Ovation –Solaris |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Existing Version: |  |  | Upgrade Version and date of upgrade : |  |  |
| Comments : |  |  |  |  |  |
| 5.15.2 Test : Install a new System with the Release Software - Check Solaris Patches Installation - Check Ovation Packages Installation - Check Installation of Third Party Software - Check Installation of Ovation Licenses |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.3 Test : Reload an Ovation Station as an Engineering Station |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.4 Test : Reload an Ovation Station as an Operator Station. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.5 Test : Reload Historian Report Server. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.6 Test : Reload Remote DataServer. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.7 Test : Download and Reboot Controller. Note: This test run through Automation. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.8 Test : Clear and Reload Controller. Note: This test run through Automation. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.9 Test : Deltree (or Clear Flash) and reload Controller. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |

| 5.15.10 Test : Starting from a known release version, upgrade the system to the Release software. Record the existing version and the upgrade version. System: Ovation Win Opcon |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Existing Version: |  |  | Upgrade Version and date of upgrade : |  |  |
| Comments : |  |  |  |  |  |
| 5.15.11 Test : Update Network Drivers from Release CD |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.12 Test : Reinstall Win Opcon. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |
| 5.15.13 Test : Upgrade Win Opcon. |  |  |  |  |  |
| Date: | Initials: | SW Level: |  | Pass/Fail/NA: | SDR/Findings# |
| Comments : |  |  |  |  |  |

  - TEST CASE 16 : Specialty Modules

| 5.16.1 Test : Final Regression for the Specialty Modules (HART Hi P AI / Hi P AO, Fieldbus, Profibus, Devicenet, RSR, Ethernet Link Controller, etc. modules) Using the module type assigned in the test plan, peform the tests below to verify that updated modules work properly. NOTE: If the STP assigns you more than one type of module, copy this test (5.16.1) as 5.16.1.1, 5.16.1.2, etc as needed. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| a) Note the module type as assigned to you in the STP | Module Type: |  |
| b) Verify the module operates correctly before the Ovation system SW is updated. | Date: | P/F/F#: |
| c) Verify the the module operates correctly after the Ovation system SW is updated. | Date: | P/F/F#: |
| d) Verify that the FW of a module can be updated. | Date: | P/F/F#: |
| e) Verify the module boots up correctly after the FW update. | Date: | P/F/F#: |
| f) Verify the module and its devices communicate normally after the FW update. | Date: | P/F/F#: |
| g) In the comments section, add details as to which module was updated, which controller was used, which devices were checked, etc. | Date: | P/F/F#: |
| h) Record the FW files of the assigned module type: In Controller Diagnostics, display the Download FW GUI for the assigned module type. Make a screen copy and save it on Val\Tests\x\Approvals\x_ModuleType_FW.jpg. Where x = release level, ModuleType = ELC/Ff/etc. | Date: | P/F/F#: |
| Comments: |  |  |

| 5.16.2 Test : Final Regression for the Specialty Modules – RVP Peform the tests below to verify that an RVP module works properly. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| a) Note the module type as assigned to you in the STP | Module Type: |  |
| b) Verify a new module can be added in studio | Date: | P/F/F#: |
| c) Verify that the FW of the module can be updated. | Date: | P/F/F#: |
| d) Verify an existing module operates normally after a FW download. | Date: | P/F/F#: |
| f) In the comments section, add details as to which module was updated, which controller was used, what functions were performed. | Date: | P/F/F#: |
| Comments: |  |  |

  - TEST CASE 17 : Database Import and Export Functionality

| 5.17.1 Test : Ovation Database Import using “OvPtImport” tool Perform database import functionality using below mentioned import command and verify that it works properly for the mentioned options. Use import data from the Ovation levels noted in the STP. Ovptimport -u ptadmin@ptdb <options> <importfile> NOTE: Refer OW360_15 for more details on import functionality and its options. Full import example including SIS: Ovptimport -u ptadmin@ptdb –f –esi C:\backup\fullexport.txt Note: This test run through Automation. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| a) Option ‘-f’ = Full import. | Date: | P/F/F#: |
| b) Option ‘-n’ = New objects only. | Date: | P/F/F#: |
| c) Option ‘-esi’ = Enables the import of safety items. | Date: | P/F/F#: |
| Comments: |  |  |

| 5.17.2 Test : Ovation Database Export using “OvPtExport” tool Perform database export functionality using below mentioned export command and verify that it works properly for the mentioned options. Ovptexport -u ptadmin@ptdb -o <outputfile> <options> NOTE: Refer OW360_15 for more details on export functionality and its options. Full export example including SIS: OvPtExport -u ptadmin@ptdb –o C:\backup\FullExport.txt –mm -Xsis Note: This test run through Automation. |  |  |
| --- | --- | --- |
| Initials: |  |  |
| a) Option ‘-a’ = Output all attribute definitions. | Date: | P/F/F#: |
| b) Option ‘-mm’ = Minimal module definitions. | Date: | P/F/F#: |
| c) Option ‘-Xsis’ = Include safety items. | Date: | P/F/F#: |
| Comments: |  |  |

5.18  TEST CASE 18 : Ovation Desktop Layout

| 5.18.1 Test: Verify that Ovation Desktop Layout application can be launched from Ovation Utilities folder. |  |  |
| --- | --- | --- |
| Date: | Initials: | Pass/Fail: |
| Comments: |  |  |

| 5.18.2 Test : Verify that Ovation Desktop Layout feature allows user to Save and then Load the desired or current layout of below mentioned Ovation application windows. |  |  |
| --- | --- | --- |
| Initials: |  |  |
|  | Module Type: |  |
| a) Alarms application window. | Date: | P/F/F#: |
| b) Graphics application window. | Date: | P/F/F#: |
| c) Trend application window. | Date: | P/F/F#: |
| d) Point review application window. | Date: | P/F/F#: |
| e) System viewer application window. | Date: | P/F/F#: |
| f) Historical review application window. | Date: | P/F/F#: |
| g) Point Information application window. | Date: | P/F/F#: |
| Comments: |  |  |

| 5.18.4 Test: Verify that Ovation Desktop Layout feature allows user to delete the previously saved layouts of different applications windows. |  |  |
| --- | --- | --- |
| Date: | Initials: | Pass/Fail/F#: |
| Comments: |  |  |

| 5.18.5 Test: Verify that the layouts can be stored based on different roles and users. |  |  |
| --- | --- | --- |
| Date: | Initials: | Pass/Fail/F#: |
| Comments: |  |  |

| 5.18.6 Test: Verify that the user will be able to save and load the remote client layout, default drop layout and an overall default layouts. |  |  |
| --- | --- | --- |
| Date: | Initials: | Pass/Fail/F#: |
| Comments: |  |  |

- Approvals

This section contains the Test Review Approval Form (TRAF) for this Software Validation
 Test procedure.

---------------------------------------------------------------------------------------------------

Note:

The Test Review Approval Form is used only during the review of this SVTP. 

It should NOT be filled in when executing this test procedure.  

Any recommended changes to this test procedure which are discovered during testing should be filed as a SVTP fndings in the findings system.

SVTP Approval Form

SVTP:  BASIC_FUNCTIONS_SVTP_rev1.X.doc

NOTE : This form is to be used only during the SVTP review process.

-Validation Engineer checks “Yes” if procedure has been modified else checks “No” :

Test Procedure – modified? 	Yes  ____ 	No ____

- Validation Engineer checks appropriate entry. If “b:” is selected, chapter numbers must be listed. If “c” is checked, development review and signature is not required.

Modification Type:	Dev. Review Required

a. New Test Procedure - 	Yes  ____

(Requires review of whole procedure)

b. Significant Test Procedure modifications - 	Yes  ____

(Requires review of Chapters ___________________)

c. No change or Minor Test Procedure modifications -	No    ____

# Development Review:	____Responsible Engineer

Print Name of Dev Engineer for ”a” or “b” type changes:     _______________________

Check if Test Procedure was Reviewed and Approved: 	               _______________

Check if Test Procedure was Reviewed and requires changes:          _______________

-Sign-off, both Dev and Val for “a” or “b” changes, Val only for “c” changes :

Development Engineer Signature:	__________________	__/__/__

Validation Engineer Signature:	__________________	__/__/__

- Test Sign-Off Form

This section includes the test sign-off form for this Software Validation Test procedure.

---------------------------------------------------------------------------------------------------

Instructions:

For Each Administarive  Section (1 – 4), give a ‘Pass’ mark if the description and reference information is accurate and complete.

In Section 5, for each Test Section (or feature), give a ‘Pass’ mark if all actions and results were executed correctly with no errors.

If any part of the test failed, give the test section a ‘Fail’ mark.

In case of a test procedure error or a required test modification, mark the ‘TP’ column.

If a section of the test is Not Applicable to the tested  Software Release, mark the ‘N/A’ column.

If any SDRs were written against the Test section, mark the ‘Yes’ box in the ‘SDR’s Written’ section. Otherwise mark the ‘No’ Box.

If an SDR  was written, attach a copy of the source file (when applicable) which was used to
discover the problem.

When a section of the test is skipped, mark the ‘Pass’ column as ‘SK’ and add a short explanation in the Comments box (e.g. No Hardware, Feature not released, etc.).  Also, make sure there is a detailed explanation in the Test Section for the reason why this section of the test was skipped

Fill in the required Test information at the top of the form, Sign and Date the form at the bottom.

---------------------------------------------------------------------------------------------------

Test Record Sign-Off

SVTP:  BASIC_FUNCTIONS_SVTP_rev1.X.doc

| Record Software and Equipment Used Information |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item: | Drop # | OS | Model | Other Info |
| Ovation Software Level |  |  |  | Ovation 4.0 |
| Database Server | Drop 100 | Windows Server 2025 | T550 | NET82 |
| Opcon/Engineering Station |  |  |  |  |
| Controller | Drop 43/93 | VxWorks | OCR1100 G06 |  |
| IO Modules |  |  |  |  |

| Test Procedure Section |  | Test Score |  |  |  | Comments |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Pass | Fail |  | N/A |  |  |
| Document Revision Index and Record of Changes |  |  |  |  |  |  |  |
| 1.0 Software Test Identifier |  |  |  |  | X |  |  |
| 2.0 Purpose |  |  |  |  | X |  |  |
| 3.0 Approach |  |  |  |  | X |  |  |
| 4.0 Features |  |  |  |  | X |  |  |
| 5.0 Procedure Steps |  |  |  |  | X |  |  |
| 5.1 Point Functionality |  |  |  |  | X |  |  |
| 5.2 Graphic Functinality |  |  |  |  | X |  |  |
| 5.3 Algorithms on Graphics |  |  |  |  | X |  |  |
| 5.4 Algorithms on Sheets |  |  |  |  | X |  |  |
| 5.5 Alarm Functions |  |  |  |  | X |  |  |
| 5.6 Trend Functions |  |  |  |  | X |  |  |
| 5.7 Menu Functions |  |  |  |  | X |  |  |
| 5.8 Controller Functions |  | X |  |  |  |  |  |
| 5.9 Engineering Functions |  |  |  |  | X |  |  |
| 5.10 Controller Diagnostic |  |  |  |  | X |  |  |
| 5.11 Freelance Tests |  |  |  |  | X |  |  |
| 5.12 Multi-Net Functions |  |  |  |  | X |  |  |
| 5.13 Historian Functions |  |  |  |  | X |  |  |
| 5.14 Windows Release Master CDs/DVD Verification |  |  |  |  | X |  |  |
| 5.15 Solaris Release Master CDs Verification |  |  |  |  | X |  |  |
| 5.16 Specialty Modules |  |  |  |  | X |  |  |
| 5.17 Database Import and Export |  |  |  |  | X |  |  |
| 5.18. Ovation desktop tools |  |  |  |  | X |  |  |
| Tester Name: Gaurav Agarwal | Tester Initails: GA |  |  | Tester Signature: GA |  |  | Date: 5/28/2025 |  |

Emerson Automation Solutions

Product Development Department

200 Beta Drive

Pittsburgh, Pa 15238