## Generated Tests
Sr. No | Threat | Interaction | State | Priority | Threat Category | Description | Justification | Test Case | Test Case Description | Prerequisites | Test Steps | Expected Behavior
1 | 1. Collision Attacks | Advanced Log Database Request | Needs Investigation | High | Tampering | Attackers who can send a series of packets or messages may be able to overlap data. For example, packet 1 may be 100 bytes starting at offset 0. Packet 2 may be 100 bytes starting at offset 25. Packet 2 will overwrite 75 bytes of packet 1. Ensure you reassemble data before filtering it, and ensure you explicitly handle these sorts of cases. | Not applicable as a Security Level 1 threat.
2 | 2. Elevation Using Impersonation | Advanced Log Database Request | Not Applicable | Low | Elevation Of Privilege | OvSim.Service (LogViewerService) may be able to impersonate the context of LogViewer in order to gain additional privilege. | OvSim.Service is running as SYSTEM level, cannot elevate higher.
3 | 3. Replay Attacks | Advanced Log Database Request | Needs Investigation | High | Tampering | Packets or messages without sequence numbers or timestamps can be captured and replayed in a wide variety of ways. Implement or utilize an existing communication protocol that supports anti-replay techniques (investigate sequence numbers before timers) and strong integrity. | Not applicable as a Security Level 1 threat.
4 | 4. Insufficient Auditing | Advanced Log Database Request | Not Applicable | Low | Repudiation | Does the log capture enough data to understand what happened in the past? Do your logs capture enough data to understand an incident after the fact? Is such capture lightweight enough to be left on all the time? Do you have enough data to deal with repudiation claims? Make sure you log sufficient and appropriate data to handle a repudiation claims. You might want to talk to an audit expert as well as a privacy expert about your choice of data. | This is a query interation, not logging - for that see Write Logs to Database interaction.
5 | 5. Data Logs from an Unknown Source | Advanced Log Database Request | Not Applicable | Low | Repudiation | Do you accept logs from unknown or weakly authenticated users or systems? Identify and authenticate the source of the logs before accepting them. | This is a query interation, not logging - for that see Write Logs to Database interaction.
6 | 6. Lower Trusted Subject Updates Logs | Advanced Log Database Request | Not Applicable | Low | Repudiation | If you have trust levels, is anyone other outside of the highest trust level allowed to log? Letting everyone write to your logs can lead to repudiation problems. Only allow trusted code to log. | This is a query interation, not logging - for that see Write Logs to Database interaction.
7 | 7. Spoofing of Destination Data Store SQL Log Database | Advanced Log Database Request | Mitigation Implemented | High | Spoofing | SQL Log Database may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of SQL Log Database. Consider using a standard authentication mechanism to identify the destination data store. | The OvSim.Service connects to the SQL database using user and password. | TC-ADVA-007 | Verify that the Ovation Digital Twin service uses a username and password to connect to the SQL database, preventing unauthorized access and spoofing. |  | 1. Attempt to connect to the SQL database using a known invalid username and password. 2. Observe the Ovation Digital Twin LogViewer (Section 5.4), as referenced in the user guide, for any indication of connection attempts. 3. Analyze the system logs (accessible through the Ovation Digital Twin Advanced Edit - Section 5.6), for rejected connection attempts with an indication of authentication failure. | The connection attempt fails, and the system logs clearly indicate authentication failure due to an invalid username and password, proving the Ovation Digital Twin service requires and validates credentials before connecting to the SQL database.
8 | 8. Risks from Logging | Advanced Log Database Request | Not Applicable | Low | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | This is a query interation, not logging.
9 | 9. Potential SQL Injection Vulnerability for SQL Log Database | Advanced Log Database Request | Mitigation Implemented | High | Tampering | SQL injection is an attack in which malicious code is inserted into strings that are later passed to an instance of SQL Server for parsing and execution. Any procedure that constructs SQL statements should be reviewed for injection vulnerabilities because SQL Server will execute all syntactically valid queries that it receives. Even parameterized data can be manipulated by a skilled and determined attacker. | The query is fully generated by OvSim service, there&#39;s no known way to inject custom text into the query by the user. | TC-ADVA-009 | To verify the query generation within the Ovation Digital Twin service is fully controlled, preventing user-supplied data from being directly injected into the SQL query. |  | 1. Attempt to manipulate the input string for a log entry (e.g., Description field) by including SQL injection payloads such as `' OR '1'='1` or `'; DROP TABLE Logs; --`. 2. Initiate a log entry using the manipulated string using the Ovation Digital Twin LogViewer (refer to USER_GUIDE_CONTEXT, Section 5.4). 3. Examine the SQL query generated by the Ovation Digital Twin service via the LogViewer to observe the constructed SQL statement. | The SQL query generated by the Ovation Digital Twin service should include the manipulated string as a literal string value within the query, without any modification to the SQL syntax or structure. There should be no execution of unintended SQL commands or modification of database tables. The query should still be valid SQL.
10 | 10. Potential Weak Protections for Audit Data | Advanced Log Database Request | Mitigation Implemented | High | Repudiation | Consider what happens when the audit mechanism comes under attack, including attempts to destroy the logs, or attack log analysis programs. Ensure access to the log is through a reference monitor, which controls read and write separately. Document what filters, if any, readers can rely on, or writers should expect | The RemoveOldestLogs advanced database request is only available for Admin-level users. | TC-ADVA-010 | To verify that the "RemoveOldestLogs" advanced database request is only accessible to users with Admin-level privileges. |  | 1. Log into the Ovation Digital Twin system as a user with a non-Admin level account (e.g., Operator). Refer to USER_GUIDE_CONTEXT, Section 5.2, for system access details. 2. Attempt to access the "RemoveOldestLogs" advanced database request via the Ovation Digital Twin LogViewer. Refer to USER_GUIDE_CONTEXT, Section 5.4. 3. Attempt to execute the "RemoveOldestLogs" request. | The "RemoveOldestLogs" request is unavailable or the system prevents execution with an error message indicating insufficient privileges, confirming that it is not accessible to non-Admin users.
11 | 11. Authorization Bypass | Advanced Log Database Request | Mitigation Implemented | High | Information Disclosure | Can you access SQL Log Database and bypass the permissions for the object? For example by editing the files directly with a hex editor, or reaching it via filesharing? Ensure that your program is the only one that can access the data, and that all other subjects have to use your interface. | The SQL log database is password protected. | TC-ADVA-011 | Verify that access to the SQL log database is prevented without the correct password. |  | 1. Attempt to directly access the SQL log database using a hex editor, navigating to the file path as if attempting bypass of permissions. (Assume file path is known based on prior reconnaissance). 2. Attempt to access the SQL log database files through a shared network drive using default/common usernames and passwords. (Refer to Section 3, paragraph 2.6.1 regarding license registration.) 3. Attempt to connect to the SQL database server using a standard SQL client (e.g., SQL Developer, Dbeaver) without providing a password. | Access to the SQL log database is denied in all attempts. A password prompt is presented before allowing access; no files are readable or modifiable without providing the correct credentials; and connection attempts fail, indicating a password protected database.
12 | 12. Potential Excessive Resource Consumption for OvSim.Service (LogViewerService) or SQL Log Database | Advanced Log Database Request | Mitigation Implemented | High | Denial Of Service | Does OvSim.Service (LogViewerService) or SQL Log Database take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | The RemoveOldestLogs advanced database request is only available for Admin-level users. All the other advanced database requests are not available for the users, but only used within the internal software framework. | TC-ADVA-012 | Verify that only Admin-level users can execute the "RemoveOldestLogs" advanced database request, preventing unauthorized resource consumption. |  | 1. Log in to the Ovation Digital Twin system as a standard user (non-admin). 2. Attempt to execute the "RemoveOldestLogs" advanced database request via the Ovation Digital Twin LogViewer (refer to Section 5.4 of the user guide). 3. Observe the system response to the attempted execution. | The system denies the request to execute "RemoveOldestLogs" and presents an access denied or insufficient privileges error message to the non-admin user.
13 | 13. Elevation Using Impersonation | Advanced Log Database Response | Needs Investigation | High | Elevation Of Privilege | LogViewer may be able to impersonate the context of OvSim.Service (LogViewerService) in order to gain additional privilege. | Not applicable as a Security Level 1 threat.
14 | 14. Replay Attacks | Advanced Log Database Response | Needs Investigation | High | Tampering | Packets or messages without sequence numbers or timestamps can be captured and replayed in a wide variety of ways. Implement or utilize an existing communication protocol that supports anti-replay techniques (investigate sequence numbers before timers) and strong integrity. | Not applicable as a Security Level 1 threat.
15 | 15. Collision Attacks | Advanced Log Database Response | Needs Investigation | High | Tampering | Attackers who can send a series of packets or messages may be able to overlap data. For example, packet 1 may be 100 bytes starting at offset 0. Packet 2 may be 100 bytes starting at offset 25. Packet 2 will overwrite 75 bytes of packet 1. Ensure you reassemble data before filtering it, and ensure you explicitly handle these sorts of cases. | Not applicable as a Security Level 1 threat.
16 | 16. Spoofing of Source Data Store SQL Log Database | Advanced Log Database Response | Mitigation Implemented | High | Spoofing | SQL Log Database may be spoofed by an attacker and this may lead to incorrect data delivered to OvSim.Service (LogViewerService). Consider using a standard authentication mechanism to identify the source data store. | The SQL log database is password protected. | TC-ADVA-016 | Verify that unauthorized access to the SQL log database is prevented due to password protection. |  | 1. Attempt to connect to the SQL log database using a known invalid username and password. 2. Using SQL injection techniques, attempt to read data from the SQL log database without valid credentials. Reference Section 5.2.1, Ovation Digital Twin Config for initial database connection details. 3. Attempt to modify data within the SQL log database using SQL commands executed without proper authentication. Refer to USER_GUIDE_CONTEXT, page 57, Ovation Digital Twin Advanced Edit for example database structures. | All attempts to connect or interact with the SQL log database using invalid credentials or unauthorized SQL commands result in an authentication failure and prevent any unauthorized access or modification of data.
17 | 17. Risks from Logging | Advanced Log Database Response | Mitigation Implemented | High | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | LogViewer is the single reader for the logs. There&#39;s no known way a user can inject information into the logs. | TC-ADVA-017 | Verify LogViewer remains the single reader for logs, preventing unauthorized injection of data. |  | 1. Attempt to directly write log data to the log file location using a text editor with administrator privileges, bypassing LogViewer. 2. Open LogViewer and examine the log data. 3. Attempt to write data to the log file using a different application (e.g., a custom program that writes directly to the file system). Refer to the manual for any restrictions (Section 2.3). 4. Open LogViewer and review the content of the log files. | LogViewer displays only data generated by the system, and any attempts to write directly to the log file are ignored or result in errors, confirming LogViewer’s role as the exclusive log reader and preventing unauthorized data injection.
18 | 18. Weak Access Control for a Resource | Advanced Log Database Response | Mitigation Implemented | High | Information Disclosure | Improper data protection of SQL Log Database can allow an attacker to read information not intended for disclosure. Review authorization settings. | The SQL log database is password protected. Additionally, there is no confidential information in the database. The logs stored in the database are intentionally available to all Ovation users. | TC-ADVA-018 | Verify that the SQL log database is password protected and accessible only to authorized Ovation users, confirming the justification that logs are intentionally available to all Ovation users. |  | 1. Using a user account *not* associated with an Ovation system, attempt to connect to the SQL log database using a generic username and password (e.g., "guest", "password"). 2. Referencing Section 5.4, Ovation Digital Twin LogViewer, attempt to access the SQL log database through the LogViewer application using the same generic credentials from step 1. 3. Attempt to directly query the SQL log database using a SQL client tool (e.g., SQL Developer) with the same generic credentials. | Connection to the SQL log database is rejected using generic credentials, demonstrating that the database is password-protected. Access through the LogViewer also fails, showing that the logs are not directly accessible without appropriate Ovation user credentials.
19 | 19. Spoofing of Destination Data Store LogViewer Export File | Export | Needs Investigation | High | Spoofing | LogViewer Export File may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of LogViewer Export File. Consider using a standard authentication mechanism to identify the destination data store. | Not applicable as a Security Level 1 threat. This is not a network data flow. This is a standard Windows FileWrite call. Additionally, the data stored in the file is intentionally available to all Ovation users.
20 | 20. Risks from Logging | Export | Not Applicable | Low | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | This is a text log file, with no dedicated log reader.
21 | 21. Lower Trusted Subject Updates Logs | Export | Needs Investigation | High | Repudiation | If you have trust levels, is anyone other outside of the highest trust level allowed to log? Letting everyone write to your logs can lead to repudiation problems. Only allow trusted code to log. | <no mitigation provided>
22 | 22. Data Logs from an Unknown Source | Export | Needs Investigation | High | Repudiation | Do you accept logs from unknown or weakly authenticated users or systems? Identify and authenticate the source of the logs before accepting them. | <no mitigation provided>
23 | 23. Insufficient Auditing | Export | Not Applicable | Low | Repudiation | Does the log capture enough data to understand what happened in the past? Do your logs capture enough data to understand an incident after the fact? Is such capture lightweight enough to be left on all the time? Do you have enough data to deal with repudiation claims? Make sure you log sufficient and appropriate data to handle a repudiation claims. You might want to talk to an audit expert as well as a privacy expert about your choice of data. | This is covered by the Insufficient Auditing threat for Write Logs to Database interaction.
24 | 24. Potential Weak Protections for Audit Data | Export | Not Applicable | Low | Repudiation | Consider what happens when the audit mechanism comes under attack, including attempts to destroy the logs, or attack log analysis programs. Ensure access to the log is through a reference monitor, which controls read and write separately. Document what filters, if any, readers can rely on, or writers should expect | This is not the actual log (see SQL Log Database). This is just an export file, deleting it (accidental or malicious) does not cause any serious repercussions, you can easily export the file again.
25 | 25. Potential Excessive Resource Consumption for LogViewer or LogViewer Export File | Export | Needs Investigation | High | Denial Of Service | Does LogViewer or LogViewer Export File take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | <no mitigation provided>
26 | 26. Weak Access Control for a Resource | Load Configuration | Mitigation Implemented | High | Information Disclosure | Improper data protection of Known Database Instances File can allow an attacker to read information not intended for disclosure. Review authorization settings. | There is no confidential information in the file. The infromation in the file is intentionally available to all Ovation users. | TC-LOAD-026 | To verify that the Known Database Instances File is accessible to all Ovation users and contains no confidential information, as stated in the justification. |  | 1. Log in to the Ovation Digital Twin LogViewer using a standard, non-administrator user account. (Refer to USER_GUIDE_CONTEXT, page 7, for LogViewer functionality) 2. Navigate to the Known Database Instances File through the LogViewer interface. (Refer to USER_GUIDE_CONTEXT, page 52, for LogViewer navigation) 3. Open and review the contents of the Known Database Instances File. 4. Attempt to extract or copy the file contents to an external storage device. | The Known Database Instances File is successfully opened and its contents are readable by the non-administrator user. The file contents consist of readily available, non-confidential data related to digital twin configurations, confirming the file does not contain sensitive or restricted information. No errors or access restrictions are encountered during the file opening and review process.
27 | 27. XML DTD and XSLT Processing | Load Configuration | Needs Investigation | High | Tampering | If a dataflow contains XML, XML processing threats (DTD and XSLT code execution) may be exploited. | <no mitigation provided>
28 | 28. Spoofing of Source Data Store Known Database Instances File | Load Configuration | Needs Investigation | High | Spoofing | Known Database Instances File may be spoofed by an attacker and this may lead to incorrect data delivered to LogViewer. Consider using a standard authentication mechanism to identify the source data store. | The file should be readonly and should have schema validation during load.
29 | 29. Weak Access Control for a Resource | Load Configuration | Mitigation Implemented | High | Information Disclosure | Improper data protection of LogViewer Configuration File can allow an attacker to read information not intended for disclosure. Review authorization settings. | This is not a network data flow (Windows file XmlReader), so cannot be spoofed outside of the Ovation system. The configuration file does not contain any confidential information, all data intentionally available to all Ovation users levels (both domain and local). | TC-LOAD-029 | Verify that the LogViewer Configuration File does not contain any confidential information and is accessible to all Ovation users levels. |  | 1. Log in to the Ovation Digital Twin system using a user account with the lowest privilege level, as detailed in Section 7 of the Emerson Ovation Digital Twin User Guide. 2. Navigate to the Ovation Digital Twin LogViewer using the steps detailed in Section 5.4 of the USER_GUIDE_CONTEXT. 3. In the LogViewer, attempt to open and view the "LogViewer Configuration File" (refer to section 5.4 of the USER_GUIDE_CONTEXT). 4. Examine the contents of the LogViewer Configuration File. | The LogViewer Configuration File opens and displays its contents without requiring elevated privileges. The contents of the file do not contain any sensitive or confidential information, aligning with the stated justification.
30 | 30. XML DTD and XSLT Processing | Load Configuration | Needs Investigation | High | Tampering | If a dataflow contains XML, XML processing threats (DTD and XSLT code execution) may be exploited. | <no mitigation provided>
31 | 31. Spoofing of Source Data Store LogViewer Configuration File | Load Configuration | Needs Investigation | High | Spoofing | LogViewer Configuration File may be spoofed by an attacker and this may lead to incorrect data delivered to LogViewer. Consider using a standard authentication mechanism to identify the source data store. | The configuration file should be moved to a secure location. The configuration file should validate schema before loading.
32 | 32. Weak Access Control for a Resource | Log Database Response | Needs Investigation | High | Information Disclosure | Improper data protection of SQL Log Database can allow an attacker to read information not intended for disclosure. Review authorization settings. | Make sure the logs don&#39;t have source code details.
33 | 33. Spoofing of Source Data Store SQL Log Database | Log Database Response | Mitigation Implemented | High | Spoofing | SQL Log Database may be spoofed by an attacker and this may lead to incorrect data delivered to LogViewer. Consider using a standard authentication mechanism to identify the source data store. | The LogViewer connects to the SQL database using user and password. | TC-LOG-033 | Verify that the LogViewer connects to the SQL database using a defined user and password, preventing unauthorized access and data spoofing. |  | 1. Attempt to connect to the SQL database used by the LogViewer using a different set of credentials (username and password) not associated with the authorized LogViewer connection. 2. Observe the connection attempt within the SQL database server logs, referencing page 14 of the document. 3. Examine the application event logs on the LogViewer machine for any connection errors or authentication failures. | The SQL database connection attempt using the unauthorized credentials is rejected, and the LogViewer remains connected to the database using the defined, authorized user and password, as documented on page 2 of the document.
34 | 34. Risks from Logging | Log Database Response | Mitigation Implemented | High | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | LogViewer is the single reader for the logs. There&#39;s no known way a user can inject information into the logs. | TC-LOG-034 | Verify that LogViewer remains the sole mechanism for accessing logs, preventing user-initiated data injection. |  | 1. Attempt to directly modify a log file (e.g., /var/log/application.log) using a standard text editor, assuming standard user privileges. 2. Attempt to create a custom application that writes directly to the log file, bypassing LogViewer. Reference Section 2.3 of USER_GUIDE_CONTEXT (Copyright Notice) which mentions potential responsibility and liability for use of the equipment. 3. Attempt to inject malicious code (e.g., shell commands) into the log data using a third-party tool, attempting to execute those commands upon reading the log data. 4. Using the Ovation Digital Twin Network Viewer (referencing Section 3.1 in USER_GUIDE_CONTEXT – What other Ovation products are used with Ovation Digital Twin?) observe the data logged and processed by LogViewer. 5. Examine the Ovation Digital Twin Media Tables (Section 5.8 in USER_GUIDE_CONTEXT) to confirm data integrity and absence of injected data. | All attempts to directly modify or inject data into the log files are unsuccessful. LogViewer remains the only observable mechanism for accessing and processing log data, confirming the absence of a user-accessible interface for data injection and validating the justification: “LogViewer is the single reader for the logs. There’s no known way a user can inject information into the logs."
35 | 35. Insufficient Auditing | Log to File | Mitigation Implemented | High | Repudiation | Does the log capture enough data to understand what happened in the past? Do your logs capture enough data to understand an incident after the fact? Is such capture lightweight enough to be left on all the time? Do you have enough data to deal with repudiation claims? Make sure you log sufficient and appropriate data to handle a repudiation claims. You might want to talk to an audit expert as well as a privacy expert about your choice of data. | The log should have the necessary data. | TC-LOG-035 | Verify that sufficient data is logged to reconstruct algorithm tuning values after modification. |  | 1. Using the Ovation Control Builder, modify the "Position-Flow Curve" tuning value for a selected algorithm (as described on page 59). Specifically, adjust the curve data using the "Import From Image" button within the Advanced Edit window. 2. Export the current network data to a file using the "Export" function within the Network Viewer (page 56). 3. Restart the Ovation Digital Twin simulation. 4. Using the Network Viewer, connect to the Ovation Digital Twin simulation (page 56). 5. Import the previously exported network data file (page 58). 6. Re-open the Advanced Edit window for the same algorithm. | The “Position-Flow Curve” tuning values within the Advanced Edit window are identical to the values prior to restarting the simulation, demonstrating that the logging mechanism preserved the algorithm configuration.
36 | 36. Data Logs from an Unknown Source | Log to File | Needs Investigation | High | Repudiation | Do you accept logs from unknown or weakly authenticated users or systems? Identify and authenticate the source of the logs before accepting them. | The log file should be readonly.
37 | 37. Lower Trusted Subject Updates Logs | Log to File | Needs Investigation | High | Repudiation | If you have trust levels, is anyone other outside of the highest trust level allowed to log? Letting everyone write to your logs can lead to repudiation problems. Only allow trusted code to log. | The log file should be readonly.
38 | 38. Risks from Logging | Log to File | Needs Investigation | High | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | The log file should be readonly.
39 | 39. Spoofing of Destination Data Store LogViewer Log File | Log to File | Needs Investigation | High | Spoofing | LogViewer Log File may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of LogViewer Log File. Consider using a standard authentication mechanism to identify the destination data store. | The log file should be readonly.
40 | 40. Potential Weak Protections for Audit Data | Log to File | Needs Investigation | High | Repudiation | Consider what happens when the audit mechanism comes under attack, including attempts to destroy the logs, or attack log analysis programs. Ensure access to the log is through a reference monitor, which controls read and write separately. Document what filters, if any, readers can rely on, or writers should expect | The log file should be readonly and only Administrator level users should be able to delete it.
41 | 41. Potential Excessive Resource Consumption for LogViewer or LogViewer Log File | Log to File | Needs Investigation | High | Denial Of Service | Does LogViewer or LogViewer Log File take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | The logs should have a size limit and start a new file when exceeded.
42 | 42. Spoofing of Destination Data Store SQL Log Database | Query Log Database | Needs Investigation | High | Spoofing | SQL Log Database may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of SQL Log Database. Consider using a standard authentication mechanism to identify the destination data store. | Not applicable as a Security Level 1 threat.
43 | 43. Risks from Logging | Query Log Database | Not Applicable | Low | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | This is a query interation, not logging.
44 | 44. Potential SQL Injection Vulnerability for SQL Log Database | Query Log Database | Needs Investigation | High | Tampering | SQL injection is an attack in which malicious code is inserted into strings that are later passed to an instance of SQL Server for parsing and execution. Any procedure that constructs SQL statements should be reviewed for injection vulnerabilities because SQL Server will execute all syntactically valid queries that it receives. Even parameterized data can be manipulated by a skilled and determined attacker. | Not applicable as a Security Level 1 threat. Need to investigate if the Filter options can be used to construct some malicious query.
45 | 45. Lower Trusted Subject Updates Logs | Query Log Database | Not Applicable | Low | Repudiation | If you have trust levels, is anyone other outside of the highest trust level allowed to log? Letting everyone write to your logs can lead to repudiation problems. Only allow trusted code to log. | This is a query interation, not logging.
46 | 46. Data Logs from an Unknown Source | Query Log Database | Not Applicable | Low | Repudiation | Do you accept logs from unknown or weakly authenticated users or systems? Identify and authenticate the source of the logs before accepting them. | This is a query interation, not logging.
47 | 47. Insufficient Auditing | Query Log Database | Not Applicable | Low | Repudiation | Does the log capture enough data to understand what happened in the past? Do your logs capture enough data to understand an incident after the fact? Is such capture lightweight enough to be left on all the time? Do you have enough data to deal with repudiation claims? Make sure you log sufficient and appropriate data to handle a repudiation claims. You might want to talk to an audit expert as well as a privacy expert about your choice of data. | This is a query interation, not logging. See Write Logs to Database interaction.
48 | 48. Potential Weak Protections for Audit Data | Query Log Database | Needs Investigation | High | Repudiation | Consider what happens when the audit mechanism comes under attack, including attempts to destroy the logs, or attack log analysis programs. Ensure access to the log is through a reference monitor, which controls read and write separately. Document what filters, if any, readers can rely on, or writers should expect | Not applicable as a Security Level 1 threat. Need to investigate if one can remove logs via some malicious log queries.
49 | 49. Potential Excessive Resource Consumption for LogViewer or SQL Log Database | Query Log Database | Needs Investigation | High | Denial Of Service | Does LogViewer or SQL Log Database take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | Need to investigate if there&#39;s any upper limit to the number of logs to query.
50 | 50. Elevation Using Impersonation | Remove Oldest Logs | Mitigation Implemented | High | Elevation Of Privilege | LogViewer may be able to impersonate the context of Ovation Administrator User in order to gain additional privilege. | LogViewer runs at the same privilege level as the User. | TC-REMO-050 | LogViewer does not possess the privileges required to delete system logs, confirming it operates at the same privilege level as the User. |  | 1. Log into the Ovation system using a standard Operator user account with minimal privileges. 2. Launch Ovation Digital Twin LogViewer (refer to USER_GUIDE_CONTEXT, page 52). 3. Attempt to use the LogViewer to delete the oldest system logs. Specifically, attempt to initiate a log deletion operation via the user interface or command-line interface. 4. Observe the system response and any error messages displayed. | The LogViewer returns an "Access Denied" or similar error message indicating insufficient privileges to delete system logs. The operation fails, proving LogViewer's privilege level matches the user’s, and preventing privilege escalation.
51 | 51. Authenticated Data Flow Compromised | Remove Oldest Logs | Mitigation Implemented | High | Tampering | An attacker can read or modify data transmitted over an authenticated dataflow. | The user action is the local user operating the application. It all happens internal to the machine, there is no data transit - for that see Advanced Log Database Request interaction. | TC-REMO-051 | To verify that removal of oldest logs occurs locally without external data transit, supporting the justification that the user action occurs entirely within the machine. |  | 1. Using the Ovation Operator Station, access the process historian functionality as described in the USER_GUIDE_CONTEXT (page 11). 2. Select the "Remove Oldest Logs" option, as described in the USER_GUIDE_CONTEXT. 3. Monitor network traffic on the machine hosting the Ovation system using a packet capture tool (e.g., Wireshark). Ensure the tool is configured to capture all traffic on all interfaces. 4. Execute the “Remove Oldest Logs” action. 5. Continue monitoring network traffic for a period of 60 seconds after the operation completes. | No network traffic related to log data transfer is observed during or after the “Remove Oldest Logs” operation. All activity remains local to the machine.
52 | 52. Spoofing of Destination Data Store Known Database Instances File | Save Configuration | Needs Investigation | High | Spoofing | Known Database Instances File may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of Known Database Instances File. Consider using a standard authentication mechanism to identify the destination data store. | The file should be readonly and should have schema validation during load.
53 | 53. Potential Excessive Resource Consumption for LogViewer or Known Database Instances File | Save Configuration | Mitigation Implemented | High | Denial Of Service | Does LogViewer or Known Database Instances File take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | The structure of the file is defined by the software. There&#39;s no known way a user can inject information into the file. | TC-SAVE-053 | The LogViewer application does not permit user-supplied data injection into configuration files, thereby mitigating potential excessive resource consumption attacks. |  | 1. Attempt to manually edit the `Configuration` file referenced within the LogViewer application, adding a large number of repeating lines. (Refer to USER_GUIDE_CONTEXT, Section 2, regarding system requirements). 2. Attempt to save the modified `Configuration` file and reload it into the LogViewer application (Refer to USER_GUIDE_CONTEXT, Section 5, Ovation Digital Twin Config, for general guidance on configuration). 3. Monitor system resource utilization (CPU, Memory) of the LogViewer application during and after the attempt to reload the modified configuration file. | The LogViewer application prevents the user from saving the modified configuration file due to file permissions or a validation check preventing large or malformed data from being loaded, and no significant increase in resource utilization is observed in the LogViewer application during and after the attempted save.
54 | 54. Authenticated Data Flow Compromised | User action | Mitigation Implemented | High | Tampering | An attacker can read or modify data transmitted over an authenticated dataflow. | The user action is the local user operating the application. It all happens internal to the machine, there is no data transit - for that see Query Log Database interaction. | TC-USER-054 | Verify that modification of process values within the Ovation Digital Twin simulation is restricted to actions performed through the Ovation Control Builder, confirming that data flows are managed internally. |  | 1. Using an Operator Station, attempt to directly modify the value of a process variable (e.g., tank level, pressure) using a third-party monitoring tool that can write values to DCS points, bypassing the Ovation Control Builder. 2. Referencing page 9 of the User Guide: “The Ovation Digital Twin provides a scalable engineered solution for operator training and certification programs…”. Attempt to force a change in a simulated tank level without using Control Builder or an Ovation algorithm modification. 3. Referencing page 10 of the User Guide: “Signal Diagrams provide the means to monitor and tune a control or simulation process.” Attempt to change tank level values within Signal Diagrams. | The attempted modification of the process variable value via the third-party monitoring tool fails, with no change observed in the Ovation Digital Twin simulation. The change must be performed within the application and through the Ovation Control Builder.
55 | 55. Elevation Using Impersonation | User action | Mitigation Implemented | High | Elevation Of Privilege | LogViewer may be able to impersonate the context of Ovation User in order to gain additional privilege. | LogViewer runs at the same privilege level as the User. | TC-USER-055 | Verify that LogViewer, when launched, runs with the same user privileges as the logged-in Ovation user. |  | 1. Log in to the Ovation system as a standard Ovation user with limited privileges. 2. Launch the LogViewer application, as described in Section 4 of the USER_GUIDE_CONTEXT. 3. Within the LogViewer, attempt to modify a system configuration file that requires administrator privileges (e.g., a controller configuration file). 4. Observe the system response to the attempted modification. | The system prevents the modification of the configuration file, displaying an error message indicating insufficient privileges, thereby confirming that LogViewer operates with the same user privileges as the logged-in Ovation user.
56 | 56. Elevation Using Impersonation | View Licenses | Not Applicable | Low | Elevation Of Privilege | LogViewer may be able to impersonate the context of Ovation License Libraries in order to gain additional privilege. | Both are running within the same process, using the same user permission levels.
57 | 57. Potential Excessive Resource Consumption for OvSim.Service (LogViewerService) or SQL Log Database | Write Logs to Database | Mitigation Implemented | High | Denial Of Service | Does OvSim.Service (LogViewerService) or SQL Log Database take explicit steps to control resource consumption? Resource consumption attacks can be hard to deal with, and there are times that it makes sense to let the OS do the job. Be careful that your resource requests don't deadlock, and that they do timeout. | There are emergency log queue truncation mechanisms and disk log cleanup in place to mitigate cases with extremely high logging. | TC-WRIT-057 | Verify that emergency log queue truncation and disk log cleanup mechanisms prevent excessive resource consumption when writing logs to the database. |  | 1. Configure the Ovation Digital Twin system to generate a very high volume of log data (e.g., by simulating a rapid sequence of events that trigger numerous diagnostic messages) exceeding typical operational logging rates. See USER_GUIDE_CONTEXT pages 14-16 for license and server requirements. 2. Initiate the high-volume log generation and monitor the Model Server, Database Server, and Ovation Digital Twin LogViewer resource utilization (CPU, memory, disk I/O). Refer to USER_GUIDE_CONTEXT page 14 for hardware and performance requirements. 3. Observe the queue size and disk space used by the SQL Log database. 4. Monitor for any errors or warnings related to resource exhaustion or database connection issues. 5. Verify that the Model Server and Database Servers do not experience significant performance degradation or become unresponsive. | The system should continue to operate normally despite the high-volume logging, with log queue truncation and disk log cleanup mechanisms preventing resource exhaustion and database overload. CPU, memory, and disk I/O usage remain within acceptable limits (as defined by Emerson’s recommendations – USER_GUIDE_CONTEXT page 14). The database log file size remains bounded, indicating log cleanup is occurring.
58 | 58. Authorization Bypass | Write Logs to Database | Mitigation Implemented | High | Information Disclosure | Can you access SQL Log Database and bypass the permissions for the object? For example by editing the files directly with a hex editor, or reaching it via filesharing? Ensure that your program is the only one that can access the data, and that all other subjects have to use your interface. | The SQL log database is password protected. | TC-WRIT-058 | Attempting to directly access and modify the SQL log database without proper credentials fails, confirming the database is password protected. |  | 1. Using a hex editor (e.g., HxD), attempt to directly open and modify the SQL log database file located on the Ovation Database Server (referencing USER_GUIDE_CONTEXT - Page 15, "The license registration procedure of the Ovation Digital Twin can be done only on the Ovation Database Server machine."). 2. Attempt to access the SQL log database file via a shared network folder on the Ovation Database Server (referencing USER_GUIDE_CONTEXT - Page 14, "Access to Ovation network."). 3. Attempt to connect to the SQL database server using a generic SQL client (e.g., DBeaver) without providing a username or password. | All attempts to directly access or modify the SQL log database file or connect to the database server without providing valid credentials fail. An error message is displayed indicating that access is denied or authentication is required.
59 | 59. Risks from Logging | Write Logs to Database | Mitigation Implemented | High | Tampering | Log readers can come under attack via log files. Consider ways to canonicalize data in all logs. Implement a single reader for the logs, if possible, in order to reduce attack surface area. Be sure to understand and document log file elements which come from untrusted sources. | There&#39;s a single reader (LogViewer) for the logs. The logs are generated by OvSim service, there&#39;s no known way to inject logs from untrusted sources. | TC-WRIT-059 | Verify that the single LogViewer application prevents unauthorized log injection, confirming the reliance on the OvSim service for log generation. |  | 1. Attempt to create a custom application capable of writing directly to the log files used by the Ovation Digital Twin simulator, bypassing the standard OvSim service. 2. Attempt to inject a malicious log entry into the custom application's log file. 3. Run the injected log file as input to LogViewer, referencing the troubleshooting guide for visibility (USER_GUIDE_CONTEXT, page 9). | LogViewer fails to process the injected log entry and reports an error indicating an invalid format or source, demonstrating the reliance on OvSim as the sole legitimate log source and preventing unauthorized log injection.
60 | 60. Spoofing of Destination Data Store SQL Log Database | Write Logs to Database | Mitigation Implemented | High | Spoofing | SQL Log Database may be spoofed by an attacker and this may lead to data being written to the attacker's target instead of SQL Log Database. Consider using a standard authentication mechanism to identify the destination data store. | The OvSim.Service connects to the SQL database using user and password. | TC-WRIT-060 | Verify that the Ovation Digital Twin service cannot write logs to an attacker-controlled SQL database due to reliance on user and password authentication. |  | 1. Configure a rogue SQL Server instance to mimic the actual SQL Log Database server, ensuring it accepts connections but is under attacker control. 2. Modify the Ovation Digital Twin configuration to point to the rogue SQL Server instance using the valid username and password of a user with *read-only* access to the real SQL Log Database. (Refer to page 10, "What are the Ovation Digital Twin algorithms?") 3. Initiate a process within the Ovation Digital Twin that generates log entries intended for the SQL Log Database. 4. Monitor the rogue SQL Server instance for incoming connections and attempts to write data from the Ovation Digital Twin service. | The rogue SQL Server instance does *not* receive any log data from the Ovation Digital Twin service. The service authentication should prevent the rogue server from accepting the connection despite providing correct username and password, as the user only has read-only access.
61 | 61. Potential SQL Injection Vulnerability for SQL Log Database | Write Logs to Database | Mitigation Implemented | High | Tampering | SQL injection is an attack in which malicious code is inserted into strings that are later passed to an instance of SQL Server for parsing and execution. Any procedure that constructs SQL statements should be reviewed for injection vulnerabilities because SQL Server will execute all syntactically valid queries that it receives. Even parameterized data can be manipulated by a skilled and determined attacker. | The logs are generated by OvSim service, there&#39;s no known way to inject custom text into the logs by the user. | TC-WRIT-061 | Verify that the user cannot inject custom text into the logs generated by the Ovation Digital Twin service. |  | 1. Attempt to inject a SQL injection payload (e.g., `'; DROP TABLE Users;--`) into a data field that is later written to a log file by the Ovation Digital Twin service. This could involve modifying a simulation parameter or entering data into a user interface element that populates a log entry. 2. Following the injection, examine the resulting log file, specifically targeting entries associated with the injected data. Refer to page 15 of the documentation, which states the license registration can be done only on the Ovation Database Server machine and the user must use domain-wide login. 3. Examine the Ovation Digital Twin LogViewer (page 52) and the Ovation Digital Twin Tray App (page 42) to inspect the log entries. Note the license information from both pages. | The injected payload is not executed as SQL code. The log file contains the injected data, but it is treated as literal text, not as a SQL command, and no tables are dropped or modified. The license information obtained from the LogViewer and Tray App remains valid and does not reflect any malicious alterations.
62 | 62. Lower Trusted Subject Updates Logs | Write Logs to Database | Mitigation Implemented | High | Repudiation | If you have trust levels, is anyone other outside of the highest trust level allowed to log? Letting everyone write to your logs can lead to repudiation problems. Only allow trusted code to log. | The SQL log database is password protected. | TC-WRIT-062 | Verify that unauthorized users cannot write to the SQL log database, confirming the password protection is effective. |  | 1. Using a workstation *not* part of the Ovation system and lacking credentials to the SQL log database, attempt to connect to the SQL log database server using standard SQL client tools. 2. Attempt to execute a SQL INSERT statement to add a new log entry to the database using the workstation from Step 1. 3. Examine the Ovation Digital Twin LogViewer to check for any changes to log entries. | The SQL client connection is rejected with an "Authentication Failed" or similar error message, preventing the unauthorized user from writing to the SQL log database and leaving the LogViewer unchanged.
63 | 63. Data Logs from an Unknown Source | Write Logs to Database | Needs Investigation | High | Repudiation | Do you accept logs from unknown or weakly authenticated users or systems? Identify and authenticate the source of the logs before accepting them. | <no mitigation provided>
64 | 64. Insufficient Auditing | Write Logs to Database | Mitigation Implemented | High | Repudiation | Does the log capture enough data to understand what happened in the past? Do your logs capture enough data to understand an incident after the fact? Is such capture lightweight enough to be left on all the time? Do you have enough data to deal with repudiation claims? Make sure you log sufficient and appropriate data to handle a repudiation claims. You might want to talk to an audit expert as well as a privacy expert about your choice of data. | The log should have the necessary data. | TC-WRIT-064 | The log data captured during a simulated operator error includes sufficient information to identify the operator, timestamp, and nature of the error, thus verifying the assertion that the log contains necessary data for repudiation claims. |  | 1. Using the Ovation Digital Twin environment, simulate an operator inadvertently entering a value outside the acceptable range for a critical process variable (e.g., flow rate), mimicking a potential operator error. 2. Access the Ovation Digital Twin LogViewer (page 52) as described in the USER_GUIDE_CONTEXT. 3. Review the entries in the LogViewer, filtering for entries related to the process variable in question. 4. Analyze the log entries to determine if they contain the following information, as directed by the USER_GUIDE_CONTEXT: operator ID, precise timestamp of the event, nature of the alteration (the out-of-range value), and the process variable affected. | The log entries resulting from the simulated operator error contain the operator ID, a precise timestamp, the incorrect value entered, and identify the affected process variable, demonstrating that the log captures sufficient data to understand the event and address potential repudiation claims, thereby proving that the log contains the "necessary data."
65 | 65. Potential Weak Protections for Audit Data | Write Logs to Database | Needs Investigation | High | Repudiation | Consider what happens when the audit mechanism comes under attack, including attempts to destroy the logs, or attack log analysis programs. Ensure access to the log is through a reference monitor, which controls read and write separately. Document what filters, if any, readers can rely on, or writers should expect | The log database should be readonly and only Administrator level users should be able to delete it.