## Ovation 3.5.0
ID | Work Item Type | Title | Assigned To | State | Tags | Acceptance Criteria | Accepted By | Accepted Date | Activated By | Activated Date | Activity | Application Launch Instructions | Application Start Information | Application Type | Area ID | Area Path | Associated Context | Associated Context Code | Associated Context Owner | Associated Context Type | Attached File Count | Authorized As | Authorized Date | Automated Test Id | Automated Test Name | Automated Test Storage | Automated Test Type | Automation status | Backlog Priority | Blocked | Board Column | Board Column Done | Board Lane | Business Value | Changed By | Changed Date | Changeset | ChangeSet Number | Closed By | Closed Date | Closed Status | Closed Status Code | Closing Comment | Created By | Created Date | Created from FINDING | Description | DIR Information | Documentation Requirements | Effort | Emerson Affected Areas | External Link Count | Finish Date | Fix Released Date | Found In | History | Hyperlink Count | Integration Build | INTERNAL AssignedHierarchyPath | Internal Resolution | Issue | Iteration ID | Iteration Path | Legacy System Number | Local Data Source | Node Name | Notify User 1 | Notify User 2 | Notify User 3 | Notify User 4 | Notify User 5 | Notify User 6 | Notify User 7 | Notify User 8 | Parameters | Parent Hierarchy Path | Phase | Planned Release | Planned Release Date | Platform | Priority | Product | Product Category | Product Component | Product Problem Type | Product State | Product Version | Query Text | Rating | Reason | Related Link Count | Released In | Remaining Work | Reported By | Reporting Source | Repro Steps | Resolution | Rev | Reviewed By | Revised Date | Severity | SME Assigned To | Start Date | State Change Date | State Code | Steps | Steps to Reproduce | Submitting Organization | Subrelease | System Info | Target Date | Team Project | Test Suite Audit | Test Suite Type | Test Suite Type Id | TPNF Number | Validation Date | Validator | Watermark
22926 | FINDING | Help button does not function in GBNT:Browse OPC Pts -> OPC Item Browser window. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 03:53 | [8 empty] | FALSE |  |  | USPITTFSService | 2015-06-12 03:53 |  |  |  | 2015-06-12 03:53 |  |  |  | USPITTFSService | 2015-06-12 03:53 |  | When Developer Studio-&gt; Graphics-&gt; Diagrams -&gt; GBNT -&gt; OPC icon on Main toolbar is clicked.<br>GBNT:Browse OPC Pts -&gt; OPC Item Browser window pops up. In this window Help button is non functional. | LC 07/25/2012: Updated the online help file so that information appear when selecting the Help button on the OPC Item Browser dialog. | No Action Required |  | Verify that help comes up for the OPC Item Browser dialog accessed from the GBNT:Browse OPC Pts dialog =&gt; Browse OPC... button. Note that this is NOT the help for the GBNT:Browse OPC Pts dialog. This is the help for the OPC Item Browser dialog. LC 07/25/2012: Select the Help button on the OPC Item Browser dialog. You should get the topic, &quot;To use the OPC Item Browser dialog.&quot; | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Help button will now be implemented. Documentatio group must now support new <br>helpid, IDH_ITEM_BROWSER_DLG [76], in gbnt help doc.<br><br>LC 07/25/2012: Added a topic called &quot;To use the OPC Item Browser dialog.&quot; The help ID is attached to this topic. When the user clicks the help button on the OPC Item Browser window, this topic should display. This fix will be available in the U5 build of the Ovation 3.5 release. (Casteel, Linda Jul 25, 2012)<br><br>PS 23-Aug-12: Found fixed in 3.5.0_U6 build. Hence Closed. (Sachan, Pallavi Aug 23, 2012) <br> |  | 35 | FINDING | 1796 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 60146
22988 | FINDING | For DEVICESEQ Algo, definitions for TARG and FRZ show discrepancies. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:25 | [8 empty] | FALSE |  |  | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:25 | 3.6.0_U1 |  |  | 2017-06-15 04:25 |  |  |  | USPITTFSService | 2015-06-12 03:53 |  | With reference to the Ovation Algorithm reference manual (REF_1100 Jan,06) TARG and FRZ pins for the DEVICESEQ algorithm show following discrepancies:<br><br>TARG (Delay Time Number): <br>CB : Optional Real R2<br>Manual: Required R2 REAL, LA point<br><br>FRZ (Status Update Freezing):<br>Manual: Required<br>CB : Optional | <p>LC 07/24/2012: Updated the TARG and FRZ parameters for the DEVICESEQ algorithm.</p><p>AA 12/01/2015: The particular finding was fixed by Linda. Hence, closing the finding.</p> | No Action Required |  | <p>LC 03/16/10: Check the DEVICESEQ algorithm for the TARG and FRZ parameters. LC 07/24/2012: Check the DEVICESEQ algorithm for the TARG and FRZ parameters.</p><p>AA 12/01/2015: The issue related to the DEVICESEQ algorithm has been resolved by Linda. Please find attached the latest online help screenshot. I will be closing this finding.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>CMM 4/27/06<br><br>These changes are in the online help and will be included in the next hard copy version of Ovation Algorithm Reference Manual (REF_1100) scheduled for publication in May 2006.<br><br>BC 05/08/06 : Modifications are made for TARG only. FRZ still shows discrepancy.<br><br>LC 03/07/07: TARG has been changed to REQUIRED. FRZ is a parameter whether or not the user enters values. A value is sent to the Controller; therefore, it is REQUIRED. This change will be reflected in the next release of the manual (March 2007) <br> LC 03/16/10: Please retest the DEVICESEQ algorithm. This change was made long ago. This is what the manual says:<br>TARG - Selectable Required (with a note that says, &quot;When a parameter type is defined as &quot;Selectable&quot; and marked as &quot;Required,&quot; the Control Builder may default the parameter to a value and mark it as &quot;Optional.&quot; However, for the control function to be executed properly, you must enter a value for the parameter.&quot;<br>FRZ - Data Init Required (Casteel, Linda Mar 16, 2010)<br><br>LC 07/24/2012: This is what the manual says now:<br>TARG - Selectable Required (with a note that says, &quot;When a parameter type is defined as &quot;Selectable&quot; and marked as &quot;Required,&quot; the Control Builder may default the parameter to a value and mark it as &quot;Optional.&quot; However, for the control function to be executed properly, you must enter a value for the parameter.&quot;<br>FRZ - Data Init Optional (Casteel, Linda Jul 24, 2012)<br><br>LC 08/27/2013: Retest in Ovation 3.5.1, build U1. (Casteel, Linda Aug 27, 2013)</p><p><br></p><p>AA 12/01/2015: The issue related to the DEVICESEQ algorithm has been resolved by Linda. Please find attached the latest online help screenshot. I will be closing this finding. The latest updated manual is kept at: Q:\Communication\TechComm\Share\Abhinav_Ovation 3.6.0 manuals\Ovation Algorithms Reference Manual (OW360_R1100). This is visible in 3.6.0_U1 build.</p> |  | 35 | FINDING | 1858 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Bush, Kirt T EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | USPITTFSService | Validation |  |  | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 114322
23048 | FINDING | Help Button missing in some screen snapshots in OW300_90 document. | Casteel, Linda EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [8 empty] | FALSE |  |  | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2015-11-30 15:25 |  |  |  | USPITTFSService | 2015-06-12 03:53 |  | In Graphics Language User Guide for Ovation 3.0(OW300_90 January,2006 Version-1) the following Screen Snapshots do not have HELP button.<br><br>Figure 12 Page-83 Pt Browser Window<br>Figure 13 Page-84 Pt Browser Window (Points Tab)<br>Figure 28 Page-128 Dot Window<br>Figure 29 Page-129 OL Gauge Window<br>Figure 30 Page-130 OL Rectangle Window<br>Figure 31 Page-131 OL cylinder Window<br>Figure 32 Page-132 Bar Window<br>Figure 33 Page-133 Plot Window<br>Figure 35 Page-135 XY Plot Window<br>Figure 36 Page-136 XY Plot Window (Shape select box checked)<br>Figure 37 Page-137 Dynamic Line/Polygon Window<br>Figure 38 Page-139 Trend Window<br>Figure 39 Page-140 Time Window<br>Figure 40 Page-141 Date Window<br>Figure 41 Page-142 Pt Group Text Window<br>Figure 42 Page-143 Process Point Window<br>Figure 43 Page-147 Text Window (Single Text)<br>Figure 44 Page-148 Text Window (Multiple Text)<br>Figure 45 Page-147 Text Window (Text Groups)<br>Figure 47 Page-155 Poke Window showing option types<br>Figure 49 Page-159 Poke Window (Type 23)<br>Figure 51 Page-161 Entry Field Window<br>Figure 52 Page-163 OL Slider Window<br>Figure 53 Page-165 OL Choice Window<br>Figure 55 Page-168 OL Check Box Window<br>Figure 58 Page-171 OL Button Window<br>Figure 62 Page-177 Function key /PKey Window<br>Figure 63 Page-178 Function key /PKey Window- Completed | LC 07/25/2012: Updated the screen captures in the Graphics Builder manual to show Help buttons. | No Action Required |  | LC 07/25/2012: See Description for Affected areas. Windows are found in the sections called, &quot;Working with Background, Foreground, Trigger and Macro Trigger draw items&quot; and Working with Keyboard draw items.&quot; | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 12/29/09: Graphics Builder document belongs to Paul Schaaf. (Casteel, Linda Dec 29, 2009)<br><br>PS 03/15/10: Help added. (Schaaf, Paul G. Mar 15, 2010)<br><br>LC 07/25/2012: Help buttons have been added. These topics are found in the sections called, &quot;Working with Background, Foreground, Trigger and Macro Trigger draw items&quot; and Working with Keyboard draw items.&quot; Fix will be available in U5 build of Ovation 3.5 release. (Casteel, Linda Jul 25, 2012)<br><br>LC 08/27/2013: Retest in Ovation 3.5.1, build U1. (Casteel, Linda Aug 27, 2013) <br> |  | 35 | FINDING | 1918 |  | FINDING | Allwein, John F AUTOSOL PITT | [9 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Not Critical for This Release | 0 |  |  | USPITTFSService | Validation |  | LC 11/30/2015: This was fixed several releases ago. Help buttons are there now.&nbsp; I'm closing this Finding. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 112961
26512 | FINDING | n/a | Gola, Megha EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | 3.6.0_U2 |  |  | 2015-12-10 23:05 |  |  |  | USPITTFSService | 2015-06-12 03:58 |  | From alarm list, right click on a point and select alert details. Alert Details window opens. The help button in following windows are not linked to their help files-<br><br>i&gt;Modify-&gt; Device Suppression<br>ii&gt;View-&gt; Select Font<br>iii&gt;File-&gt; Print and Print Preview.<br><br>The corresponding help pages should be linked. | <p>LC 9-24-09: Context sensitive is now available from Help buttons and information on printing has been added. LC 6/11/10: Context sensitive is now available from Help buttons and information on printing has been added.</p><p>MG 12/11/2015: Added&nbsp;Help IDs in AuthorIT. Help should work now.</p> |  |  | <p>LC 9-24-09: Check context sensitive online help, especially for Device Suppression, Select Font, Print, Print Preview and Print Setup. LC 6/11/10: Check context sensitive online help, especially for Device Suppression, Select Font, Print, Print Preview and Print Setup.</p><p><br></p><p>MG 12/11/2015: Added&nbsp;Help IDs in AuthorIT. Help should work now. Check&nbsp;Plant Web Alerts section of OvPtStudio online help in 3.6.0 U2 build.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>msb - MNR from 3.2.0_U4 to 3.2.0_P0 - 27-May-09<br><br>LC 9-24-09: Added in context IDs that were missing. Now context-sensitive help should appear for<br>Select Font and Device Suppression. Also added in topics that deal with Printing, Print Preview,<br>and Print Setup along with context IDs. Help should now work. ( Casteel, Linda Sep 24, 2009 )<br><br>Can not be tested due to Finding#5783. (Tripathi, Mithilesh Oct 13, 2009)<br><br>LC 6/11/10: Retest the online help in U6 build of 3.3.1. Added in context IDs that were missing. Now context-sensitive help should appear for<br>Select Font and Device Suppression. Also added in topics that deal with Printing, Print Preview,<br>and Print Setup along with context IDs. Help should now work. (Casteel, Linda Jun 11, 2010) </p><p><br></p><p>MG 12/11/2015: Added&nbsp;Help IDs in AuthorIT. Help should work now. Check&nbsp;Plant Web Alerts section of OvPtStudio online help in 3.6.0 U2 build.<br></p> |  | 35 | FINDING | 5378 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8, 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Not Critical for This Release | 0 |  |  | USPITTFSService | Validation |  | MG 12/11/2015: Added&nbsp;Help IDs in AuthorIT. Check&nbsp;3.6.0 U2 build. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 112961
27618 | FINDING | Help button available in Devicenet module configuration P01 window is not opening the related document. | Antony, Leena PROCESS PWS NOIDA | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 03:59 | [11 empty] | USPITTFSService | 2015-06-12 03:59 | [7 empty] | USPITTFSService | 2015-06-12 03:59 |  | If we click on Help button available in the Devicenet module configuration P01 window it opens the document &quot;To access the Profibus module configuration window&quot;. Instead it should open the available document &quot;To access the devicenet module configuration window&quot;. (Basu Saumik May 11, 2010) | LA 08/16/2012: Context id 1267 added to topic &quot;To access the devicenet module configuration window&quot;in the DeviceNet usermanual in Author IT. |  |  | LA 08/16/2012: Context id 1267 added to topic &quot;To access the devicenet module configuration window&quot;in the DeviceNet usermanual in Author IT. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | All I/O, Q-Line and Bus configuration dialogs (past the inital device insertion) are handled through the Controller manuals. I will be reassigning these Findings to Ron Skina. PGS - 18-May-2010 (Schaaf, Paul G. May 18, 2010)<br><br>LC 12/22/11: Developer Studio help is not working. Will fix in Ovation 3.5.0. (Casteel, Linda Dec 22, 2011)<br><br>LC 07/26/2012: Fix belongs in the DeviceNet manual. Re-assigning to Leena Antony. (Casteel, Linda Jul 26, 2012) <br> LA 08/16/2012: Context id 1267 added to topic &quot;To access the devicenet module configuration window&quot;in the DeviceNet usermanual in Author IT. (Antony, Leena Aug 16, 2012) |  | 35 | FINDING | 6485 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Casteel, Linda EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 69479
28634 | FINDING | In Ovation Studio, Cannot load help files [HelpID=1285, HelpID=1286 and HelpID= 1287]. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:01 | [11 empty] | USPITTFSService | 2015-06-12 04:01 |  |  |  | 2015-06-12 04:01 |  |  |  | USPITTFSService | 2015-06-12 04:01 |  | Steps are followed:<br>1.OvStudio &gt; [SISNT1]Network level &gt; Configuration &gt; Alarm Check Remove Reconfirm [Reconfirm Time] &gt; Alarm Check Remove Reconfirm Time. Open available Object &gt; Help button on appeared window gives error &quot; Cannot load help file = C:\Ovation\help\EN\OvPtStudio.chm&quot;, HelpID=1286&quot;.For reference &quot;Studio alarm check remove confirm Time help error.JPG&quot; snapshot is placed on \\168.92.224.52\Val\Tests\3.4.0\From IEC.<br>2.OvStudio &gt; [SISNT1]Network level &gt; Configureation &gt; Alarm Check Remove Reconfirm &gt; [Reconfirm Drops] &gt; Select available option [say drop 135] &gt; Right click and open &gt; Help button on appeared window gives error &quot; Cannot load help file = C:\Ovation\help\EN\OvPtStudio.chm&quot;, HelpID=1287&quot;. For reference &quot;Studio alarm check remove confirm drop help error.JPG&quot; snapshot is placed on \\168.92.224.52\Val\Tests\3.4.0\From IEC.<br>3.OvStudio &gt; [SISNT1]Network level &gt; Configuration &gt; Alarm Check Remove Reconfirm. Right click on [Alarm Check Remove Reconfirm] and select open. Object window gets opened. Help button on object window gives error &quot; Cannot load help file = C:\Ovation\help\EN\OvPtStudio.chm&quot;, HelpID=1285&quot;. (Pandey, Vijay Apr 8, 2011) | SJ 08/13/2012: Topic divided into three sub topics and added the help ids. SJ 09/17/2012: Topic divided into three sub topics and added the help ids. Please check the updated OvPtStudio.chm of 3.5.0_U8 |  |  | SJ 08/13/2012: Topic divided into three sub topics and added the help ids. SJ 09/17/2012: Topic divided into three sub topics and added the help ids. Please check the updated OvPtStudio.chm of 3.5.0_U8 | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 5/18/11: Move to next release 3.5 (Casteel, Linda May 18, 2011)<br><br>LC 07/26/2012: Alarm Check Remove configuration should be documented in the Operator Station Configuration Manual. The help topic will come from there. Re-assigning this to Swati Jain. (Casteel, Linda Jul 26, 2012)<br><br>SJ 08/13/2012: Topic divided into three sub topics and added the help ids. (Jain, Swati Aug 13, 2012)<br>SJ 09/17/2012: Topic divided into three sub topics and added the help ids. Please check the updated OvPtStudio.chm of 3.5.0_U8 (Jain, Swati Sep 17, 2012)<br>VP-09/28- Retested with 3.5.0_U9, found fixed. Hence finding is closed. (Pandey, Vijay Sep 28, 2012) <br> |  | 35 | FINDING | 7504 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 71452
29009 | FINDING | Some math function does not work in VxSim controller, which makes calcblock not working when those are used | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | In VxSim controller there is no round() function, so that it was exchanged with stub function that just prints the message, that it has executed. (Zochowski, Piotr Oct 12, 2011)<br><br>Full list of not working functions:<br>- round()<br>- log2() - log2 function is not documented in Ovation manual, however it is available to the users<br>- trunc() - causes that Truncate and Remain operations are not working in calcblock algorithm (Zochowski, Piotr Nov 16, 2011) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | These functions are not available in math library for vxsim. Stubs for above routines have been updated to function. (Perdeus, Matthew Nov 15, 2012)<br>---<br>msb - Closed: Converted to SDR 19600 (Benzvi, Mati May 10, 2013) <br> |  | 35 | FINDING | 7881 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Souders, Sarah EMR SYSS PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW | [5 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72175
29011 | FINDING | VxSim controller appears in controller diagnostics tool with os version 6.5, which shall be 6.8 | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | VxSim controller appears in controller diagnostics tool with os version 6.5, which shall be 6.8 (Zochowski, Piotr Oct 13, 2011) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK in 3.5.0_U3 @ 02-Jul-12<br> Diagnostices - VC - 142 &gt; OS Version = 6.8 (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 7883 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72179
29012 | FINDING | Download of the vxsim controller copies the vxworks kernel for hardware controller | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Current VxSim controller has different kernel than hardware controller. Right now the user shall not download the kernel from developer studio. However it happens quite often that it is done by mistake and the VxSim controller does not boot up then.<br>The process of download can be changed to download corresponding vxworks kernel on the vxsim controller. (Zochowski, Piotr Oct 13, 2011) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK in 3.5.0_U3 @ 02-Jul-12<br> New VC - 145 - Download. (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 7884 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72181
29015 | FINDING | VxSim console displays "DpuStat : muxTxCookieGet() failed" when connecting from Controller Diagnostics | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Following steps performed :<br>1/Defined Vx Sim Redundant controller in Ovation Studio.<br>2/These Redundant Vx sim are loaded succesfully and working fine.<br>3/ Open the Diagnostic tool to check the Status of Vxsim controllers .<br>4/ On selection of VxSim Drops , This shows error &quot; DpuStat : muxTxCookieGet() failed,&quot; (Gupta, Ankit Oct 13, 2011) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved (Gupta, Ankit Sep 25, 2012) |  | 35 | FINDING | 7887 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72187
29033 | FINDING | VxSim Controllers are rebooting by itself. | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | VxSim Controllers are rebooting by itself several times during the day. It seems, that it does not matter whether they are loaded or not.Reboot also could occur during load. (Kossowski, Grzegorz Oct 26, 2011)<br>Problem was observed on latest version of vxsimMain.out (version of 2011-10-25). (Kossowski, Grzegorz Oct 27, 2011)<br><br>IC 9/26/12 lower to CAT 3 per Matt P email : The current issue with vxsim&quot;s rebooting is in the case of redundant VCs (the missed UDP messages) and there is always one in control. This was originally a cat3, raised to a cat2 by Doug a few weeks ago, not realizing that there was always one in control. (Capani, Nooch Sep 26, 2012) (Perdeus, Matthew Feb 21, 2013) |  |  |  | Verify virtual controllers are not randomly booting. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This problem is being caused by dropped packets from vxsim. WR is working with Matt on this issue. I am raising the category as this is a showstopper issue. (Pingree, Douglas K. Sep 7, 2012) <br> |  | 35 | FINDING | 7905 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | OVA350008 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72223
29034 | FINDING | During VxSim Controller reboot an "Exception at interrupt level" occurs. | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | When VxSim controller is rebooted (no matter if it rebooted manually by operator or rebooted by itself) the error occurs. In the controller console I have found 2 different messages:<br><br>1.<br>workQPanic: Kernel work queue overflow.<br>Exception at interrupt level:<br>Regs at 0x0<br><br>2.<br>Exception at interrupt level:<br>Exception !<br>Vector 13 : Access Violation<br>Program Counter:0x124ab53a<br>Access Address (write):0x00000472<br>Status Register:0x00010216<br>Regs at 0x1123fd60 (Kossowski, Grzegorz Oct 26, 2011)<br><br>Problem was observed on latest version of vxsimMain.out (version of 2011-10-25). (Kossowski, Grzegorz Oct 27, 2011) |  |  |  | Reboot from Stuido of controller with console window displayed should not show an exception as described above. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 7906 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | OVA350005 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72225
29036 | FINDING | VxSim Controller goes to "Failed mode" due to task timeout. | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | Several times during the day has been observed, that VxSim Controllers went to &quot;Failed mode&quot; due to task time. It was &quot;DPU Monitor&quot; task. The problem was observed on Warsaw test system and on Noida test system.<br><br>Sample error log:<br>THU OCT 27 14:21:11 2011 : &lt;134&gt; REDUND_PROC MSG : Switching to Control<br>THU OCT 27 14:21:11 2011 : &lt;132&gt; redundProc : warning: DPU Monitor timed out.<br>THU OCT 27 14:21:11 2011 : &lt;129&gt; Controller Error : Subsystem Error : Watchdog error: task timed out. : 0x13c0efa0 : 0x0 : 0x1f4 : 0x0<br>THU OCT 27 14:21:11 2011 : &lt;134&gt; REDUND_PROC MSG : Switching to Failed mode (Kossowski, Grzegorz Oct 27, 2011)<br><br>Problem was observed on latest version of vxsimMain.out (version of 2011-10-25). (Kossowski, Grzegorz Oct 27, 2011) |  |  |  | Observe VxSim controllers to ensure error message does not appear. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Timeouts were extended for vxsim controllers. (Perdeus, Matthew Sep 10, 2012) <br> |  | 35 | FINDING | 7908 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72229
29122 | FINDING | In Vxsim controller, the usage of FirstOut algorithm will put the simcontroller into failed state. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | When Firstout algorithm is used in Vxsim controller, because of the local memory function, the simcontroller enters into failed state.<br><br>E-mail description of the problem from Piotr Z:<br><br>The problem is with use of local memory function. It was raised about two years ago by Tad, I will try to find his email and forward it to you for reference.<br>Firstout algorithm uses only 4 bytes of local memory. In database and CB templates it has assigned 32 ( which is more than it needs - shall be changed to 16 ). <br>LMEMget ( I don&quot;t remember exact function name ) expects a table of pointers to the blocks of local memory and in this case it expects a table of two pointers ( two 16 bytes blocks ). It fills both pointers that expects to get, which leads to memory overwriting which in case of vxsim controller is a stack corruption. This leads to setting PC to 0 when leaving algorithm function block code and stop of cttask execution. (Gumpu, Ravi Nov 19, 2011) |  |  |  | The problem would cause vxworks 6.8 to page fault. The fix corrects this. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected localmemory pointer to accomodate 2 blocks of data. (Pingree, Douglas K. Apr 5, 2012) <br> Corrected stack corruption issue. The only way to test this is to ensure the firstout algorithm operated correctly. (Pingree, Douglas K. Apr 16, 2012)<br><br>IC 11/6/12 - closed per Piotr Zochowski email: Recently we rechecked the finding and it appears to be corrected in final build (U8). (Capani, Nooch Nov 6, 2012) |  | 35 | FINDING | 7999 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW | [6 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72400
29220 | FINDING | In VxSim Controller,Math-Algorithms gives wrong output values for Invalid input values(nan). | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While execution of Math Algorithms like SUM, MULTIPLY, DIVIDE, SQUREROOT, ANTILOG, LOG, NLOG, SMOOTH on Vx Sim and OCR 400 gives different output values for Invalid input (nan).<br> Testing performed using latest VxsimMain.out file delivered on 7/12/2011.<br><br>SUM :<br>(a)When input values IN1= nan , IN2=1,IN1G=1 ,IN1B= 0,IN2B=0, IN2G=1, IN3G=1 ,IN3B= 0, IN4G=1 ,IN4B= 0, TPSC=100AND BPSC=-100<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;-100&quot; with BAD quality.<br><br>MULTILPY :<br>(a)When input values IN1= nan , IN2=1,IN1G=1 ,IN1B= 0,IN2B=0, IN2G=1, TPSC=100AND BPSC=1<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;1&quot; with BAD quality.<br><br>DIVIDE :<br>(a)When input values IN1= nan , IN2=1,IN1G=1 ,IN1B= 1,IN2B=1, IN2G=2, TPSC=100 AND BPSC=1.<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;1&quot; with BAD quality.<br><br>SQUAREROOT :<br>(a)When input values IN1= nan, IN1G=1,IN1B= 1, TPSC=100AND BPSC=1.<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;0&quot; with GOOD quality.<br><br>ANTILOG :<br>(a)When input values IN1= nan, SCAL=0 and BASE=0<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;1.21E-38&quot; with GOOD quality.<br><br>NLOG :<br>(a)When input values IN1= nan ,BIAS=1<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;-3.4E+38&quot; with GOOD quality.<br><br>LOG :<br>(a)When input values IN1= nan ,BIAS=1<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;-3.4E+38&quot; with GOOD quality.<br><br>SMOOTH :<br>(a)When input values IN1= 0 ,SMTH=nan<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with BAD quality.<br> Observation on Vxsim: OUTPUT = &quot;0&quot; with BAD quality. (Gupta, Ankit Dec 19, 2011) (Gupta, Ankit Dec 19, 2011) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Resolution same as for finding 8125 (for ocr400). (Perdeus, Matthew Dec 18, 2012)<br><br>Closed. Same as Finding 8125 which was converted to SDR 19347. (Perdeus, Matthew Feb 22, 2013) <br> |  | 35 | FINDING | 8097 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [5 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72594
29221 | FINDING | In VxSim Controller,Math-Algorithms gives wrong output values for valid input values(1e+37). | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While execution of Math Algorithms like DIVIDE, SIN, COS, RATECHANGE,TANGENT on Vx Sim and OCR 400 gives different output values at valid input i.e.1e+37. Testing performed using latest VxsimMain.out file delivered on 7/12/2011.<br><br>DIVIDE: <br>(a)When input values IN1= 1e+37 , IN2=1e+37,IN1G=1e+37 ,IN1B= 1,IN2B=1, IN2G=2, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;5e+36&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>(b) When input values IN1= 100 , IN2=10,IN1G=1e+37 ,IN1B= 1,IN2B=1, IN2G=1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;10&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>(c) When input values IN1= 100 , IN2=10,IN1G=IN1B= IN2B=IN2G=1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;9.18&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>(d) When input values IN1= 100 , IN2=10,IN1G=-1e+37 ,IN1B= 1,IN2B=1, IN2G=-1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;10&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>SIN :<br>(a)When input values IN1= 1e+37<br> Observation on OCR400: OUTPUT = &quot;1e+37&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;0.988712&quot; with GOOD quality.<br><br>COSINE :<br>(a)When input values IN1= 1e+37<br> Observation on OCR400: OUTPUT = &quot;1e+37&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;0.14983&quot; with GOOD quality.<br><br>RATECHANGE :<br>(a)When input values IN1= 1e+37<br> Observation on OCR400: OUTPUT = &quot;3.3e+29&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;0&quot; with GOOD quality.<br><br>TANGENT :<br>(a)When input values IN1= 1e+37<br> Observation on OCR400: OUTPUT = &quot;nan&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;6.5989&quot; with GOOD quality. (Gupta, Ankit Dec 19, 2011) (Gupta, Ankit Jan 3, 2012) (Perdeus, Matthew Nov 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected issues with all algs except ratechange. No problems with rate change observed. Note that rate change will output a non zero value for only one cycle for a given change. If the loop time is to fast the user may never see the value of ratechange becoe something else other than 0. (Christy, Benjamin Dec 11, 2012)<br><br>SDR 19346 created (Ritenbaugh, David W. Jan 16, 2013) <br> |  | 35 | FINDING | 8098 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72596
29229 | FINDING | QBAD paremeter not present in CALCBLOCKD algorithm | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | QBAD parameter is not defined in CALCBLOCKD Algorithm. <br><br>But Ref 1100 tell about &quot;The QBAD parameter is initialized by the user to indicate whether the OUT point should be set to bad quality if an invalid number is calculated. The default value is &quot;YES&quot; which sets the output to bad quality if an invalid number is encountered.&quot;<br><br>The above line should be removed from REF1100 manual. (Gupta, Ankit Jan 2, 2012) (Casteel, Linda Jul 25, 2012) | LC 07/25/2012: Removed the information about the QBAD parameter from the CALCBLOCKD algorithm. |  |  | LC 07/25/2012: Check the CALCBLOCKD algorithm. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 07/25/2012: For the CALBLOCKD algorithm, removed the lines, &quot;The QBAD parameter is initialized by the user to indicate whether the OUT point should be set to bad quality if an invalid number is calculated. The default value is &quot;YES&quot; which sets the output to bad quality if an invalid number is encountered.&quot;<br>This will be available in the U8 build of the Ovation 3.5 release. (Casteel, Linda Jul 25, 2012) (Casteel, Linda Sep 11, 2012) <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved (Gupta, Ankit Sep 25, 2012) |  | 35 | FINDING | 8106 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  |  | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72611
29230 | FINDING | In VxSim Controller,Divide-Algorithm gives wrong output values at different valid input values | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While execution of Divide Algorithm on Vx Sim and OCR400 gives different output values at valid input values . Testing performed using latest VxsimMain.out file delivered on 7/12/2011.<br><br>(a) When input values IN1= 100 , IN2=10,IN1G=1e+37 ,IN1B= 1,IN2B=1, IN2G=1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;10&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>(b) When input values IN1= 100 , IN2=10,IN1G=IN1B= IN2B=IN2G=1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br>Observation on OCR400: OUTPUT = &quot;9.18&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>(c) When input values IN1= 100 , IN2=10,IN1G=-1e+37 ,IN1B= 1,IN2B=1, IN2G=-1e+37, TPSC=1e+37 AND BPSC=-1e+37.<br> Observation on OCR400: OUTPUT = &quot;10&quot; with GOOD quality.<br> Observation on Vxsim: OUTPUT = &quot;1e+37&quot; with BAD quality. (Gupta, Ankit Jan 2, 2012) (Gupta, Ankit Jan 3, 2012) |  |  |  | Dulpicate of Finding 8098 | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Dulpicate of Finding 8098 (Gupta, Ankit Jan 3, 2012) <br> |  | 35 | FINDING | 8107 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [5 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72613
29231 | FINDING | In VxSim Controller,HeartBeat Algorithm is giving bad quality for random outputs when no input is connected | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | For the HeartBeat Algorithm when none of the inputs are connected to input pins (IN1,IN2,IN3,IN4 &amp; IN5) the quality of output pins is showing bad randomly. (Jindal, Deepak Jan 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test. (Boehmer, Robert W. Oct 29, 2012)<br>---<br>msb - Closed. Converted to SDR 19601 (Benzvi, Mati May 10, 2013) <br> Checked and verified on Ovation3.5.0 build and found that still in VxSim Controller,HeartBeat Algorithm is giving bad quality for random outputs when no input is connected.Hence the issue has not been resolved. (Jindal, Deepak Nov 2, 2012)<br>Issue resolved. Input point status variable was uninitialized. When no inputs were connected, this uninitialized status was being carried through to the output and caused anomalous output quality. The input status is now properly initialized. (Souders, David Apr 9, 2013) (Souders, David Apr 9, 2013) |  | 35 | FINDING | 8108 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72615
29232 | FINDING | After a reboot of simplex controller, a AAFlipFlop algorithm changes its output value, but there is no 0-&gt1 transition of SRST input. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | External points are connected to all inputs of AAFlipFlop. Inputs are set to the following values and qualities:<br>SRST = 1 GOOD<br>RSET = 0 GOOD<br>INIT = 1 BAD<br><br>After reboot of simplex controller, at first pass of algorithm, the output is set to 0. At second pass, the output is set to 1.<br><br>The VxSim controller was debugged. It looks like the first pass of algorithm run before inputs points are scanned on ddb. On first pass all inputs points have value 0 and are timed out.<br>Before next pass, all inputs are updated. At the next pass SRST is equal to 1 and controller detects a 0-&gt;1 transition, so the output is inverted. In fact, there is no 0-&gt;1 transition. (Kossowski, Grzegorz Jan 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test. (Boehmer, Robert W. Oct 29, 2012)<br>Checked and verified on Ovation3.5.0 build: the issue is resolved. (Kossowski, Grzegorz Nov 5, 2012) <br> |  | 35 | FINDING | 8109 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  |  | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72617
29236 | FINDING | Keyboard algorithm : Controller failed when Keyboard algorithm added in control sheet. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | The OCR400 controller was upgraded from OCR400(Vxworks V5.4) is upgraded to OCR400(Vxworks V 6.8)<br><br>Then ,On defining a keyboard algorithm in controlsheet.The drop/controller is going to failed mode.<br><br>This was excuted on latest build dated 22/12/2011 (Gupta, Ankit Jan 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012) <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved (Gupta, Ankit Sep 25, 2012) |  | 35 | FINDING | 8113 |  | FINDING | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  |  | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Ankit EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72625
29246 | FINDING | No mention of the grouping of alarms using the "Drag a column header here to group by that column" or I believe the sorting of alarms by any of the columns | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | LC 1/13/12: Per Dianne McMaster, this information is missing from the Operator Station book. This functionality is used by customers so it should be in the book. No mention of the grouping of alarms using the &quot;Drag a column header here to group by that column&quot; or I believe the sorting of alarms by any of the columns (Casteel, Linda Jan 13, 2012) (Casteel, Linda Jan 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed; Converted to SDR 19265 (Benzvi, Mati Nov 29, 2012) <br> |  | 35 | FINDING | 8123 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Casteel, Linda EMR SYSS PWS PITT | McMaster, Dianne External Artech | [6 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72645
29247 | FINDING | In OCR468, MATH algorithm gives wrong output values for Valid input values | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While execution of math algorithm (Divide), OCR468 gives different output values for VALID input as mentioned below. Testing performed on build released on 22-12-2011. <br>Divide: <br>1. When input values:<br>NUM = 1e+37,NUMG = 1e+37,NUMB = 1, DEN = 1e+37,DENG = 2,DENB = 1,TPSC = 1e+37,BPSC = -1e+37<br>Observation on OCR454: OUTPUT = &quot;5e+36&quot; with GOOD quality.<br>Observation on OCR468: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>2.When input values<br>NUM = 100,NUMG = 1e+37,NUMB = 1,DEN = 10,DENG = 1e+37,DENB = 1,TPSC = 1e+37,BPSC = -1e+37<br>Observation on OCR454: OUTPUT = &quot;10&quot; with GOOD quality.<br>Observation on OCR468: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>3.When input values<br>NUM = 100,NUMG = 1e+37,NUMB = 1e+37,DEN = 10,DENG = 1e+37,DENB = 1e+37,TPSC = 1e+37,BPSC = -1e+37<br>Observation on OCR454: OUTPUT = &quot;9.1818&quot; with GOOD quality.<br>Observation on OCR468: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>4.When input values<br>NUM = 100,NUMG = -1e+37,NUMB = 1,DEN = 10,DENG = -1e+37,DENB = 1,TPSC = 1e+37,BPSC = -1e+37<br>Observation on OCR454: OUTPUT = &quot;10&quot; with GOOD quality.<br>Observation on OCR468: OUTPUT = &quot;1e+37&quot; with BAD quality.<br><br>The above observations were also observed in VxSim controller(finding no. 8098) (kant, krishna Jan 16, 2012) (kant, krishna Jan 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012) <br> Checked and verified the above Math algorithm (Divide) on Ovation3.5.0_U8 build and issue has not been resolved (kant, krishna Sep 25, 2012)<br><br>Changed type of gained and biased numerator and denominator to avoid overflow (Christy, Benjamin Nov 28, 2012)<br><br>SDR 19348 created (Ritenbaugh, David W. Jan 16, 2013) |  | 35 | FINDING | 8124 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72647
29248 | FINDING | In OCR468, MATH algorithm gives wrong output values for Invalid input values(nan) | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While execution of math algorithm (NLOG,LOG,ANTILOG,DIVIDE,SUM,MULTIPLY,SMOOTH,CALCBLOCK &amp; SQUAREROOT),OCR468 gives different output values for Invalid input as mentioned below. Testing performed on build released on 22-12-2011.<br><br>a.NLOG &amp; LOG <br>When input<br>IN1 = NAN (GOOD)<br>BIAS = 1<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;-3.4e+38&quot; with GOOD quality.<br><br>b.ANTILOG<br>i.When input<br>IN1 = NAN (GOOD)<br>SCAL = 0<br>BASE = BASE_10<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;1.207e-38&quot; with GOOD quality.<br><br>c.DIVIDE<br>When input values<br>NUM = NAN NUMG = 1 NUMB = 1<br>DEN = 1a DENG = 2 DENB = 1<br>TPSC = 100<br>BPSC = 1<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;1&quot; with BAD quality.<br><br>d.SUM<br>i.When input values<br>IN1 = NAN IN1G = 1 IN1B = 0<br>IN2 = 10 IN2G = 1 IN2B = 0<br>TPSC = 100<br>BPSC = -100<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;-100&quot; with BAD quality.<br><br>e.MULTIPLY<br>i.When input values<br>IN1 = NAN IN1G = 1 IN1B = 0<br>IN2 = 10 IN2G = 1 IN2B = 0<br>TPSC = 100<br>BPSC = 1<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;1&quot; with BAD quality.<br><br>f.SMOOTH<br>i.When input<br>IN1 = 0<br>SMTH = NAN<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;0&quot; with BAD quality.<br><br>g.CALCBLOCK<br>i.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = YES<br>EQUATION = (IN1)^(IN2)<br>Observation on OCR454: OUTPUT = &quot;1&quot; with GOOD quality, VALI = TRUE<br>Observation on OCR468: OUTPUT = &quot;0&quot; with GOOD quality, VALI = TRUE<br><br>ii.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = NO<br>EQUATION = (IN1)^(IN2)<br>Observation on OCR454: OUTPUT = &quot;1&quot; with GOOD quality, VALI = TRUE<br>Observation on OCR468: OUTPUT = &quot;0&quot; with GOOD quality, VALI = TRUE<br><br>h.SQUAREROOT<br>i.When input<br>IN1 = NAN (GOOD) IN1G = 1 IN1B = 1<br>TPSC = 100<br>BPSC = 1<br>TRAT = 2.5<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;1&quot; with GOOD quality.<br><br>The above observations were also observed in VxSim controller(finding no. 8097) (dhotre, Ganesh Jan 16, 2012) (dhotre, Ganesh Jan 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012) <br> Checked and verified the above Math algorithm on Ovation3.5.0_U8 build and issue has not been resolved. (dhotre, Ganesh Sep 25, 2012)<br><br>Corrected comparisons to NAN all algs should now being working. (Christy, Benjamin Dec 11, 2012)<br><br>SDR 19347 created (Ritenbaugh, David W. Jan 16, 2013) |  | 35 | FINDING | 8125 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72649
29285 | FINDING | OPP: Observed UDA Alarms instead of low/high alarms after removing UDA limits. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | We have defined UDA limits for analog points and got proper UDA alarms. But, after removing UDA limits, then also we get UDA alarms instead of Low/High alarms. <br><br>Following cases were executed in sequence as mention below:<br><br>Case 1: low/high alarms and dead band/incremental without user defined low/high alarms (UDA) limits.<br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = <br>High alarm limit user =<br><br>After making above changes and loading a controller Drop.<br>We are getting following alarms low1,low2,low3,low4 and high1, high2, high3, high4 in alarm viewer for o/p values of 0,-20,-40,-60 &amp; 150, 170, 190 &amp; 210.<br><br>Case 2: low/high alarms and dead band/incremental with user defined low/high alarms (UDA) limits.<br> <br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = 0<br>High alarm limit user = 150<br>After making above changes and loading a controller Drop.<br><br>We have got L1/LUDA, L2/LUDA, L3/LUDA, L4/LUDA and H1/HUDA, H2/HUDA, H3/HUDA, H4/HUDA alarms properly<br><br>Case 3: low/high alarms and dead band/incremental without user defined low/high alarms (UDA) limits<br><br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = <br>High alarm limit user = <br>After making above changes and loading a controller Drop.<br><br>Expected output on OCR468 : After case3 ,We are getting L1/LUDA, L2/LUDA, L3/LUDA, L4/LUDA and H1/HUDA, H2/HUDA, H3/HUDA, H4/HUDA alarms instead of low1,low2,low3,low4 and high1, high2, high3, high4 .<br><br>Further observation: After rebooting DROP, it works fine and gives proper alarms(low1,low2,low3,low4 and high1, high2, high3, high4) (kant, krishna Feb 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012) <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved (kant, krishna Sep 25, 2012) |  | 35 | FINDING | 8162 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT |  |  | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72722
29286 | FINDING | OPP on VxSim: Observed UDA Alarms instead of low/high alarms after removing UDA limits in VxSim | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | We have defined UDA limits for analog points and got proper UDA alarms. But, after removing UDA limits, then also we get UDA alarms instead of Low/High alarms. <br><br>Following cases were executed in sequence as mention below:<br><br>Case 1: low/high alarms and dead band/incremental without user defined low/high alarms (UDA) limits.<br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = <br>High alarm limit user =<br><br>After making above changes and loading a controller Drop.<br>We are getting following alarms low1,low2,low3,low4 and high1, high2, high3, high4 in alarm viewer for o/p values of 0,-20,-40,-60 &amp; 150, 170, 190 &amp; 210.<br><br>Case 2: low/high alarms and dead band/incremental with user defined low/high alarms (UDA) limits.<br> <br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = 0<br>High alarm limit user = 150<br>After making above changes and loading a controller Drop.<br><br>We have got L1/LUDA, L2/LUDA, L3/LUDA, L4/LUDA and H1/HUDA, H2/HUDA, H3/HUDA, H4/HUDA alarms properly<br><br>Case 3: low/high alarms and dead band/incremental without user defined low/high alarms (UDA) limits<br><br>Various limits defined for output.<br>Low Sensor limit=-400<br>High Sensor limit=400<br>Low engineering limit = -85<br>High engineering limit = 235<br>Low reasonability limit = -110<br>High reasonability limit = 285<br>Low alarm limit 1 = 0<br>Low alarm limit 2 =-2 0<br>Low alarm limit 3 = -40<br>Low alarm limit 4 = -60 <br>Low alarm incremental = 25<br>High alarm limit 1 = 150<br>High alarm limit 2 = 170<br>High alarm limit 3 = 190<br>High alarm limit 4 = 210<br>High alarm incremental=25<br>Low/high alarm dead band = 5<br>Low alarm limit user = <br>High alarm limit user = <br>After making above changes and loading a controller Drop.<br><br>Expected output on VxSim: After case3 ,We are getting L1/LUDA, L2/LUDA, L3/LUDA, L4/LUDA and H1/HUDA, H2/HUDA, H3/HUDA, H4/HUDA alarms instead of low1,low2,low3,low4 and high1, high2, high3, high4 .<br>After rebooting DROP, Still we are getting L1/LUDA, L2/LUDA, L3/LUDA, L4/LUDA and H1/HUDA, H2/HUDA, H3/HUDA, H4/HUDA alarms . <br>Finally, We have to close the &quot;drop batch file and restart again &quot; then it works fine and gives proper alarms(L1-L4 &amp; H1-H4) (kant, krishna Feb 9, 2012) (Boehmer, Robert W. Sep 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012) <br> Checked and verified on Ovation3.5.0_U8 build 32 bit VxSim setup and issue is resolved (kant, krishna Sep 26, 2012) |  | 35 | FINDING | 8163 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT |  |  | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72724
29296 | FINDING | OPP: Observed Negative deadband for low limits donot work. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | OPP: Negative dead band for low limts donot work as per document<br>Low Deadband = -5<br>Low Alarm 1 = -1<br>Low Alarm 2 = -20<br>Low Alarm 3 = -40<br>Low Alarm 4 = -60<br>Low Alarm User= <br>Low Alarm Inc. = 25<br>Low Eng. Limit = -85<br>Low Reas. Limit = -110<br><br>Value Alarm Alarm(expected) Quality<br>0 X X GOOD<br>-1 LOW1 LOW1 GOOD<br>-20 LOW2 LOW2 GOOD<br>-40 LOW3 LOW3 GOOD<br>-39 LOW2 LOW3 GOOD<br><br>According to document Ref 1140, Negative deadband should work as percentage of limt. So for -40 limit, deadband calculated will be 5 % of this value which is equal to 2. (kant, krishna Feb 15, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012)<br>---<br>msb - Closed: Converted to SDR 19270 (Benzvi, Mati Nov 30, 2012) <br> Checked and verified that negative deadband for low limits do not work on Ovation3.5.0_U8 build and issue has not been resolved (kant, krishna Sep 25, 2012)<br><br>This is also a problem in 3.3.1. Deadbands will not work properly when the limit is negative. This is true for high and low limits. SDR will be created and this will be patched. (Boehmer, Robert W. Nov 30, 2012) |  | 35 | FINDING | 8173 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72743
29347 | FINDING | The Locksmith License Generator cannot generate license for 300 Remote Networks | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | The maximum number of Remote Networks that can be selected in the Locksmith Generator -&gt;<br> [Ovation for Windows DROPS License -&gt; Feature: 16 - Num Remote Networks] is 126. <br>With any higher number of remote network the tool displays an error:<br> [Exception caught: Sentinel SetNumKeys failed. Error=4]<br>3.5.0 specs allows 300 Remote Networks. (Benzvi, Mati Mar 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Licensing (LIC)</p> <p><strong>Release Level:</strong> 3.5.0_P0 14-SEP-11</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Swartz, Mark E. Benzvi, Mati Augustine, Lisa</p> <p><strong>Entry Date:</strong> 2012-03-13T07:20:56-04:00</p> <p><strong>Modified Date:</strong> 2012-03-13T09:35:02-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8224 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72843
29385 | FINDING | A controller compact flash disk must be cleared when upgrading to Ovation 3.5.0. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | A controller compact flash disk must be cleared when upgrading to Ovation 3.5.0 to accommodate the new directory structure. (Brown, Sean Mar 28, 2012) | In Ovation 3.5 the controller uses a new operating system and directory structure. This requires the user to delete the existing files off of the flash disk (a format should not be required) or install a new clean flash disk. |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - added to DIR, closed finding. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8265 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72918
29386 | FINDING | Directory data/fieldbus missing from /ata0/wdpf/dpu. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | The directory data/fieldbus is missing from /ata0/wdpf/dpu. This results in an inability to load a redundant controller unless its partner is offline. (Brown, Sean Mar 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected issue by creating directory by default. (Pingree, Douglas K. Apr 5, 2012) <br> |  | 35 | FINDING | 8266 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72920
29387 | FINDING | The [Performing target save and disconnect...] process takes a long time during controller load. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | The [Performing target save and disconnect...] message is present for up to several minutes during a controller load. The message is sometimes still present for a minute or more after the file static.dat file has stopped increasing in size. (Brown, Sean Mar 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Enabled disk caching. (Pingree, Douglas K. Jul 3, 2012)<br><br>Issue appears to have been resolved; closing. (Brown, Sean Sep 28, 2012) <br> |  | 35 | FINDING | 8267 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72922
29388 | FINDING | The file libalg.lib must be modified to allow control with DEVICE algorithms to load. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Loading control sheets with DEVICE algorithms cause the control task to stop. Mark Zaremsky patched the file libalg.lib to allow loading to continue. (Brown, Sean Mar 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected issue with Device algorithm. (Pingree, Douglas K. Apr 5, 2012) <br> |  | 35 | FINDING | 8268 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72924
29389 | FINDING | After 3.5.0 Install or upgrade an Explorer.exe pop-up error is displayed on each drop | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | At the end of the initial load of 3.5.0 or upgrade from a previous 3.5.0 update,<br>a pop-up window is displayd on each workstaion:<br>------------------------------------------<br> (x) Explorer.exe<br> (X)<br> The parameter is incorrect.<br>------------------------------------------ (Benzvi, Mati Mar 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed @ 02-Jul-12.<br> The Error appears on drops where the Explorer Folder non-default options are checked:<br> Remember each folder&quot;s view settings<br> Restore previous folder windows at logon<br>no Ovation action required (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 8269 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72926
29393 | FINDING | 2xSelect algorithm: PBPT PIN value is changing & MRE and XALM pins are showing pulsing output. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | This behaviour has been observed in following two cases:<br>A) When XA=5,XB=99,CNTL=0,ALDB=-100,CNDB=200,RATE=0,DBND=0,HOLD=0, Then OUT=5, PBPT=(value is changing as 0x0400 &amp; 0x0440), XALM=Pulsing(True/false),MRE=Pulsing(True/false).<br><br>B) When XA=5,XB=99,CNTL=0,ALDB=-1.0E+37 , CNDB=200,RATE=0,DBND=0,HOLD=0, Then OUT=5, PBPT=(value is changing as 0x0400 &amp; 0x0440), XALM=Pulsing(True/false),MRE=Pulsing(True/false). (Jindal, Deepak Mar 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected handling of negative deadbands. (Christy, Benjamin Dec 18, 2012)<br><br>SDR 19345 created (Ritenbaugh, David W. Jan 16, 2013) <br> |  | 35 | FINDING | 8273 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72934
29401 | FINDING | In Ovation 3.5, the usage of FirstOut algorithm will put the controller into failed state. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | When Firstout algorithm is used in Ovation3.5, the controller enters into failed state. The problem is with use of local memory function. Firstout algorithm uses only 4 bytes of local memory. In database and CB templates it has assigned 32 ( which is more than it needs - shall be changed to 16 ). LMEMLocalDataGet expects a table of pointers to the blocks of local memory and in this case it expects a table of two pointers ( two 16 bytes blocks ). It fills both pointers that expects to get, which leads to memory overwriting which in case of controller is a stack corruption. This leads to setting PC to 0 when leaving algorithm function block code and stop of cttask execution.<br><br>There was a finding 7999 raised, against that the code for vxsim was corrected and committed to &quot;controller&quot; module in cvs. It shall be copied over to embedded cvs module but still the same problem coming in Ovation 3.5. (Jindal, Deepak Apr 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected issue with first out algorithm. (Pingree, Douglas K. Apr 5, 2012) <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved (Jindal, Deepak Sep 25, 2012) |  | 35 | FINDING | 8281 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 72950
29402 | FINDING | On 64b drops the OHI information is not displayed in the DU record and System Graphics | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | On W7 (64b) &amp; Ws08_R2 (64b) drops the OHI is not showing correctly in the DU record<br>and in the System Status graphs (1800 &amp; 1801):<br>KM - Interface Type = Unknown<br>VE - Interface Vendor = OHI<br>K0 - Channel 0 State = Unknown<br>K1 - Channel 1 State = Unknown<br><br>While on W7 (32b) the record displays:<br>KM - Interface Type = DAS 100 MBit Ethernet<br>VE - Interface Vendor = OHI<br>K0 - Channel 0 State = Available<br>K1 - Channel 1 State = Active (Benzvi, Mati Apr 2, 2012) |  |  |  | There are three different possibilities - Server 2008 32 bit, Windows 7 32 bit, and Windows 7 or 2008 R2 64 bit. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | OHI driver modified to provide this information in a format compatible with both 32 bit and 64 bit systems. (Burgoon, Frank J. Apr 13, 2012)<br>---<br>msb in 3.5.0_u1 -<br> Drop125, 245 - 2008R2-64bit<br> drop126 - WIN7-64bit<br> drop228 - WIN7-32bit (Benzvi, Mati Apr 28, 2012) <br> |  | 35 | FINDING | 8282 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | McMaster, James External Artech | [8 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72952
29406 | FINDING | A controller cannot consistently be drop-loaded. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Incremental drop loads to OCR400 14/64 occasionally fail. Clearing the controller first will usually allow the controller to be loaded (there have been instances where multiple clears were required). PEDIT errors are sometimes reported in the Studio error window. (Brown, Sean Apr 2, 2012)<br><br>Failed in U5. 14 and 64 loaded from cleared state without problems. A security field for all of the points was then touched and an incremental load was performed. 14 (Control) loaded without problems, but the load to 64 (Backup) failed while [Updating target sequence number] was being performed. The Studio error is attached. (Brown, Sean Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | We have changed the dynamics of the drop loads with VxWorks 6.8 relating to disk read/write issues. Please retry with U4. (Pingree, Douglas K. Jul 27, 2012)<br><br>We addressed some issues regarding updating the target sequence number in previous updates. Can you give us some additional information regarding the failure? Is there a pedit message that pops up? Does this happen every incremental load? We are trying to determine if this issue is related to the incremental load problems we have been seeing in general. If you are able to reproduce this at will can you let Ben know? (Pingree, Douglas K. Aug 21, 2012) <br> Multiple tasks using same socket causing issue. Resolved this seems ok (Christy, Benjamin Sep 10, 2012)<br><br>Appears to be resolved in U8. Incremental loads to OCR400 14/64 (EMILY) were successful. Closing. (Brown, Sean Sep 18, 2012) |  | 35 | FINDING | 8286 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Zaremsky, Mark External MZCI | [7 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72960
29423 | FINDING | OvationStationSyncronization.txt fill up the C: drive to capacity on a new 3.5.0 Server | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | On a newly upgraded 3.5.0 Server with only DBS, 2 Eng stations and no Controllers attached, <br>the C: drive fill up to capacity every few days by a 43 Gb text file:<br> C:\Windows\ServiceProfiles\NetworkService\AppData\Local\Temp\<br> OvationStationSyncronization.txt (Benzvi, Mati Apr 4, 2012)<br><br>On the new 3.5.0 Westinghouse network, after creating only OSS, DBS &amp; VCH drops with <br>DU records only, the C: drive on the DBS drop filled to the Max.<br>We found a 55Gb size file:<br>C:\Windows\ServiceProfiles\NetworkService\AppData\Local\Temp\OvationStationSynchronizer<br>On the 2 3.5.0 DBS drops in the Val Lab the size of the same file is 4kb &amp; 5kb respectively. (Benzvi, Mati May 16, 2012)<br><br>Added Description from Duplicate Finding.<br>- (Hutchison, Steven B. May 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - Error log grows quickly without bound.<br> - Gaurded Source Path does not exist exceptions.<br> - Sent Messages to Event Log instead. (Hutchison, Steven B. May 16, 2012)<br>---<br>msb - Was not observed on new system loaded with U3 -&gt; Monitoring (Benzvi, Mati Jun 19, 2012) <br> |  | 35 | FINDING | 8303 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 72994
29426 | FINDING | Reasonabilty range limit is not working as expected in OPP Analog | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | As per the manual REF_1140: &quot;When an Analog value is out of Reasonabilty range , it should change the quality of the Analog point&quot; but it is not working as expected<br><br>For example in following cases:<br>1/ if Reasonabilty limit= 30 than it should change quality above 30 not on 30.<br><br><br>2/ When high reasonability limit is 30 along with high deadband 5, then if value gets decreased to 30 then also quality is not coming back to GOOD while it should become GOOD on 30.<br><br>This behaviour has also been observed on Ovation 3.3.1 (Jindal, Deepak Apr 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19271 (Benzvi, Mati Nov 30, 2012) <br> |  | 35 | FINDING | 8306 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 73000
29431 | FINDING | Cleared drop17/67 fails on startup with "memPartAlloc: block too big" errors | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Cleared drop17/67 (migrated from 3.4.0) fails on restart with following errors:<br>...<br>Init_SHC : Starting SHC daemon - SHC_HWY<br>REDUND_PROC MSG : Switching to Control<br>0x3b89f10 (HSE_Task): memPartAlloc: block too big 3044 bytes (0x4 aligned) in partition 0x4fa7e0<br>0x395ae90 (scada2): memPartAlloc: block too big 5000 bytes (0x4 aligned) in partition 0x4fa7e0<br>0x395ae90 (scada2): ......Message repeated....# times.<br>0xafcb58 (tNet0): memPartAlloc: block too big 32000 bytes (0x4 aligned) in partition 0x4fa7e0<br>0xafcb58 (tNet0): ......Message repeated....# times.<br>Controller Error : Coordinator Subsystem Error : Coordinator Processing Task Error : 0x4 : 0x2 : 0x1c0001 : 0x6<br>REDUND_PROC MSG : Switching to Failed mode (Benzvi, Mati Apr 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | If a memPartAlloc error is seen, please include the following data:<br><br>1. Log into the controller and type memShow, include that in this file with the drop number referenced.<br>2. If possible, duplicate this controller on an older system (3.4 or 3.3.1), load the drop, login and type memShow. Include the output in this file with the drop number referenced.<br><br>We believe that these controllers are exceeding the amount of memory in G01 OCR400 processors. The G01 processor has 64 MB of memory. The G02 processors have 128 MB. It will be necessary to either upgrade the processor card to a G02, or to remove driver(s) from that controller.<br><br>We would like to get as much data as possible on this in order to calculate a recommendation for spare memory when upgrading to Ovation 3.5. (Pingree, Douglas K. Apr 12, 2012)<br>---<br>msb - The drops were upgraded to G02 in U2 but show different failure in U3.<br>Finding #8578 describes the current U3 failure. (Benzvi, Mati Jun 18, 2012) <br> |  | 35 | FINDING | 8311 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73009
29436 | FINDING | A Drop Clear of an OCR400 returns a PEDIT error. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Clearing an OCR eventually returns a PEDIT message in Studio after a few minutes (perhaps due to a timeout). The clear appears to be successful (the OCR reboots then enters Control or Backup). (Brown, Sean Apr 11, 2012)<br><br>The second statement above is inaccurate. The OCR must be rebooted again before a load can be attempted (Studio errors indicate the OCR cannot be found). (Brown, Sean Apr 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | We have changed the dynamics of drop clears and loads by changing how the disk reads/writes occur with vxworks 6.8. Please try again with U4. (Pingree, Douglas K. Jul 27, 2012)<br><br>Appears to be resolved in U8. Multiple clear and load operations of OCR400 14/64 (EMILY) were successful. Closing. (Brown, Sean Sep 18, 2012) <br> |  | 35 | FINDING | 8316 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73019
29437 | FINDING | Two OCR400s with Fieldbus cannot be loaded. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Drop loads to two OCR400s on the WALT system fail (17/67 and 16/66). These OCRs are configured for Fieldbus. Both OCRs return similar errors in Studio (attached). (Brown, Sean Apr 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | These devices need to be added via the device update tool. (Pingree, Douglas K. Apr 11, 2012)<br><br>IC 8/7/12 Val+Dev+Doc mtg - may already be in U5, change owner to be Steve H. (Capani, Nooch Aug 7, 2012) <br> |  | 35 | FINDING | 8317 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [7 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73021
29441 | FINDING | Ovation PowerTools service (OvPtSvr) stops when searching events in Audit Viewer | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Ovation PowerTools service stops when searching events in Audit Viewer. Following steps were performed:<br>a. Initially, Drop176 (DBS+PDC) is working fine. All applications &amp; engineering tools including developer studio was working properly.<br>b. Opened Audit Viewer tool on EWS drop245. Searched for the events by changing time stamp.<br>c. The tool displayed all the events properly lying within the time band. Till now OvPtSvr service is running normally.<br>d. When again did event search in the audit viewer tool, the OvPtSvr service stopped on drop176 as seen in Services.msc window. Also, the EventViewer window gave error message &quot;The OvPtSvr service terminated unexpectedly. It has done this 1 time(s). The Event ID appeared is 7034.<br>e. Due to this, we could not open Developer Studio on any EWS drops. Attempting to do so the OvPtSvr service starts for a second on drop176 &amp; then again stops. And Eventviewer shows that many number of Event ID messages.<br>f. It has also been observed that when we reboot DBS drop176 to start the OvPtSvr service, its Distributed Database Update Percentage does not distribute (shows value 65535 as seen in Ovation Session Manager). We have to manually STOP &amp; RESTART OracleServicePTDB service in the Services.msc window. (Gupta, Chandresh Apr 12, 2012) |  |  |  | The affected area is in the software associated with the retrieval of Engineering Tool audit entries. Previously, an implicit clean-up was performed prior to the initiation of a query into the Engineering Tool audit database. Since the OvPtSvr service (which supports the Audit Viewer on non-database server machines) automatically disconnects and reconnects to the database as necessary, this implicit clean-up may take place with an already disconnected session, and cause the OvPtSvr application to abort. The software has been changed to explicitly clean-up its internal connection to the database after each Engineering Tools audit entry retrieval. The applicable binary is the Audit View application. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please also reference cat 3 SDR 17589 which describes the same issue.<br><br>Please also note that item (f) in the description (i.e., the fact that OracleServicePTDB service had to be manually restarted following reboot) is not related to the earlier OvPtSvr crash. Ensure that the database server does not have any network interfaces which are simply disconnected. If so, disable those other interfaces until network connnectivity has been restored. If necessary, the OracleServicePTDB service issue should be tracked separately. (Swartz, Mark E. Apr 12, 2012)<br><br>During investigation, a problem was discovered which may be related to the issue reported in this Finding and in the referenced SDR 17589. Specifically, the operation of the Audit Viewer on a non-database server machine can cause the crash of the OvPtSvr service via the following:<br>1. Perform an Audit Retrieval of some specified time period -- resulting in the retrieval of one or more entries.<br>2. Let the Audit View application remain idle for 15 minutes or more (i.e., perform no user actions on this application during this time).<br>3. Perform an additional Audit Retrieval with the same (or different) time period.<br><br>The second retrieval will likely crash the OvPtSvr service.<br><br>Please confirm if this behavior exists. (Swartz, Mark E. Apr 23, 2012)<br><br>cg (05/24/12) - Finding retested in Ov3.5.0_U2. As outlined in the Resolution field, performed Audit Retrievel as mentioned below:<br>1. 1st time with 2 minute time period &quot; OvPtSvr service did not stop<br>2. After 20 min, 2nd time with 5 minute time period &quot; OvPtSvr service did not stop<br>3. Left the Audit Viewer window in open state. Then after ~4 hrs., 3rd time with ~1 hour period - OvPtSvr service stopped &amp; retrievel window showed nothing. Please see the attached snapshot file F#8321_recreate.jpg.<br>Based on these observations this finding is marked as Open (Failed Retest) &amp; Action field is changed to DRR. (Gupta, Chandresh May 24, 2012) (Swartz, Mark E. May 30, 2012) <br> We cannot recreate this issue, so more information requested. When did the OvPtSvr service stop -- during the actual Audit result retrieval attempt, during some other system-wide operation, or by some unknown issue? Does the time of the OvPtSvr crash (as would be found in Ovation Event Log) correspond with the attempted Audit retrieval? (Swartz, Mark E. May 30, 2012)<br><br>cg (06/13/12) - I tried to recreate the issue in Ov3.5.0_U3 but unable to recreate. However, during U0 (when this finding was posted), the OvPtSvr service stopped during the actual Audit result retrieval attempt. And both the timings almost matched (OvPtSvr crash &amp; Audit retrieval). Please advice if I should keep this finding open with Monitoring action or shall I close the issue? Thanks! (Gupta, Chandresh Jun 13, 2012)<br><br>cg (06/25/12) - The OvPtSvr service stopped today also on Net#8 DBS drop176 upon doing the same steps as mentioned in the Description field above. Timings of OvPtSvr crash &amp; Audit retrieval were also same. Hence State of this finding is changed to DRR. (Gupta, Chandresh Jun 25, 2012)<br><br>Please retest. Other changes related to Engineering Tools Audit (reference 8575) may have also affected this issue in a positive way. (Swartz, Mark E. Jul 13, 2012)<br><br>cg (07/30/12) - Finding retested in U4 build. The OvPtSvr service did not stop anytime out of 4 attempts from Audit Viewer. Hence finding is kept in Monitoring state. (Gupta, Chandresh Jul 30, 2012)<br><br>cg (09/27/12) - Finding retested in 3.5.0_U9. The OvPtSvr service is not stopping any time while attempting actions in Audit Viewer application. Hence finding is closed now. (Gupta, Chandresh Sep 27, 2012) |  | 35 | FINDING | 8321 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73029
29442 | FINDING | Few discrepancies observed in Controller Diagnostics window | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | There are few discrepancies observed in the Controller Diagnostics window. They are:<br>1. In [Controller Overview] subheading, &quot;Ethernet Address&quot; details are appearing as TOP aligned. The same needs to appear at the center.<br>2. &quot;Controller Type&quot; &amp; &quot;Processor&quot; details are appearing as &quot;Unknown&quot;. It should contain the selected drop details.<br>3. &quot;Comm Services&quot; details with option Enable/Disable is missing from this window. The same was available in Ov3.4.0 &amp; prior release Diagnostics window.<br>Please refer the attached snapshot file controller_diagnostics_041112.jpg. (Gupta, Chandresh Apr 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Issue one and two are resolved in U8. Issue is not an issue. Comm services was removed with the transition away from telnet and ftp. (Christy, Benjamin Sep 10, 2012)<br><br>cg (09/19/12) - Finding retested in Ov3.5.0_U8. All ok as per developers comments. Hence finding closed. (Gupta, Chandresh Sep 19, 2012) <br> |  | 35 | FINDING | 8322 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73031
29445 | FINDING | The initial load of a new OCR400 fails. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Controllers loaded for the first time on the WALT system display a message stating that the loadable contents have changed (message is attached). (Brown, Sean Apr 12, 2012) |  |  |  | The order in which various operations are performed during a load has changed. Specifically, the retrieval of the maximum modified sequence from the database is now performed after interrogating the target (and the database) for the set of applicable received points. The applicable binary is OvPtSysApi.dll. Also reference Finding 8527 Affected Areas and Test Recommendations. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Sometime during the preparation for the load, the drop object itself (where the target IP addresses are) gets updated. This in turn effects the &quot;max sequence number&quot; used during the load. In previous releases, this did not matter. However, in Ovation 3.5.0, this value is now double-checked right before sending load commands to the target. <br><br>The reason the &quot;max sequence&quot; value is double-checked in this release is because of load preview. We don&quot;t know how long the user is staring at the load preview window -- and while they were doing that, someone else may have edited one of the points in the drop.<br><br>This issue may only happen once following an import of that target&quot;s contents. A subsequent load attempt should be successful. (Swartz, Mark E. Apr 12, 2012) (Swartz, Mark E. Apr 30, 2012)<br><br>One of the reasons this issue can occur is due to the creation of children objects of the drop database object itself during the initial portion of the load operation. For example, the creation of a DDB object will update the parent drop object&quot;s modified sequence number. <br><br>The initial load of a newly imported redundant Ovation drop can cause this issue. During the preliminary portions of the load operation (before the preview window is shown), the target partner&quot;s DU DDB is created. Currently, this is performed AFTER the database modified sequence number is captured. Therefore, by the time the modified sequence number comparison is performed at the conclusion of the preview window, it will have been changed and the load is subsequently aborted.<br><br>The load software will be changed to capture the database modified sequence number AFTER any received point DDBs are created. (Swartz, Mark E. May 8, 2012)<br><br>The issue is still observed (a new redundant OCR is imported; the load aborts with a [loadable contents have changed] message). (Brown, Sean Jun 12, 2012) <br> The issue is also related to the creation of DDB objects to support the Control Sheet interrogation of the controller during the load. The changes made to address Finding 8527 will also address this Finding. (Swartz, Mark E. Aug 24, 2012)<br><br>Resolved in U7; closing. (Brown, Sean Sep 13, 2012) |  | 35 | FINDING | 8325 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73037
29446 | FINDING | OCR400 controller drop7 FAIL upon clearing | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | OCR400 controller drop7/57 is configured on IEC 3.5.0 Net#8. When we cleared drop7 it came up but in FAILED mode with Coordinator Subsystem Error. Please note that the controller has G01 Processor Module. Attached are the error log file with the error messages &amp; telnet--&gt;memShow details of this failed drop7. (Gupta, Chandresh Apr 13, 2012)<br><br>cg (04/18/12) - On drop7/57, after changing the configuration of Maximum Point Limit from 32000 to 16000, the drop was deltreed &amp; brought up (download, reboot &amp; load). The drop came up ok &amp; till now is working fine. Attached are memShow files drop7_telnet_041812.txt &amp; drop57_telnet_041812.txt after the above changes were done. (Gupta, Chandresh Apr 18, 2012)<br><br>cg (05/07/12) - After upgrading the network to Ov3.5.0_U2, controller drop7 was Downloaded, Cleared. Upon Loading drop7 failed with error &quot;Controller Error : Coordinator Subsystem Error : Coordinator Point Edit Error : 0x3 : 0x23 : 0x4 : 0x0&quot;. Please refer attached text file drop7_load_fail_U2_050712.txt. (Gupta, Chandresh May 7, 2012)<br><br>Logged into system and cleared and loaded both drop7/57 without any controller errors. There were some sheet move errors from studio. Please investigate these sheets so that controller load may complete properly and we can investigate again. (Perdeus, Matthew May 15, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Attempted to recreate this issue on both 5/15 and 5/16 by logging into system. Both attempts were unsuccessful. Believe this was an anomaly. If you have no more issues with this drop, please close finding. (Perdeus, Matthew May 16, 2012)<br>cg (06/07/12) - Finding retested in Ov3.5.0_U3. Drop7/57 both came up properly after Download--&gt;Clear--&gt;Load operation. Hence, attempt to recreate the issue was not successful. As mentioned by the developer, this issue may be anamoly. So closing this finding as CND. (Gupta, Chandresh Jun 7, 2012) <br> |  | 35 | FINDING | 8326 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73039
29449 | FINDING | 3.5.0 Compile window of control sheet displaying different option to choose a data directory | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Step to reproduce:<br>1.Open Devp.studio-&gt;Goto control task-&gt; select control sheet-&gt;Tools-&gt;Operations-&gt;Compile operation.<br>observe the data directory window it is providing the option to select the folder.<br>if user select the &quot;Library&quot; folder(showing by default) it throws the error says &quot;No control Builder files found in:Z:\IVALSYS3....&quot;<br><br>By default it should select the&quot;ControlFunctions&quot; folder.<br><br>If the user is click the &quot;selectFolder button&quot; without selecting any folder user can able to do compile operations.<br>and compile operation is working fine.<br>If the user select any other folder other then &quot;ControlFunctions&quot; folder.It throws the error.<br><br>Please find the attached snop shot.<br><br>For your information:<br>In 3.4.0 system(win7 &amp; XP) by default it&quot;s selecting the&quot;ControlFunctions&quot; folder and compile get successful. (K, SendhilKumar Apr 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works as designed. The select directory dialog box is platform dependent. When the library directory is selected, it is processed and found empty.<br>- (Hutchison, Steven B. Apr 18, 2012)<br><br>SKK:<br>Our intension to raise this issue is, there are some possibility user can able to select other then &quot;ControlFunctions&quot; folder.It may be conflict with new users. <br>&quot;selectFolder&quot; option need to be removed and it should be dispplayed as 3.4.0 compile window which is only displaying &quot; OK &quot; option.<br>Please refer the attachements,3.4.0 &amp; 3.5.0 complie window (both are Win7 OS machine). (K, SendhilKumar May 30, 2012)<br><br>Works As Designed. The select directory dialog is platform dependent and therefore managed by the QT framework. - (Hutchison, Steven B. Jun 6, 2012) <br> |  | 35 | FINDING | 8329 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73045
29450 | FINDING | Apply button disabled in "New control sheet" window | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Step to reproduce:<br>Open Devp.studio-&gt;Goto control task-&gt;Insert new sheet-&gt;<br>observe the new sheet window Apply button disabled always even after all the entries(Sheet name etc..) are filled.<br><br>Please find the attached snop shot. (K, SendhilKumar Apr 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This works as designed. <br>Note that when an existing Control Sheet is edited (i.e., opened) via the Ovation Developer Studio, the Control Builder is launched instead of a simple dialog window of the Ovation Developer Studio. When Inserting a new Control Sheet, the user must first enter a few attributes (e.g., Sheet name, etc.) after which the Control Builder is launched so that the rest of the control sheet can be built. It would be improper and misleading behavior for the user to press Apply, have entries saved to the database and not have the Control Builder launched. (Swartz, Mark E. Apr 13, 2012) <br> |  | 35 | FINDING | 8330 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73047
29451 | FINDING | Loading an OCR400 with GE Mark V points causes the controller to fail. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | A controller configured with GE Mark V points fails after being loaded. Error buffer messages:<br><br>&lt;131&gt; coord: GE Mark 5/6 IO Driver : error 0x380003 opening /ata0/data/gett.dat.<br>&lt;131&gt; coord: GE Mark 5/6 IO Driver : edit session end error: file copy failed.<br>&lt;131&gt; coord: IO Library : io edit session: ioctl failed. io fd: 0x37. iod: 2. device #: 3.<br>&lt;129&gt; Controller Error : Coordinator Subsystem Error : Coordinator Point Edit Error : 0x3 : 0x27 : 0xffffffff : 0x0<br>&lt;134&gt; REDUND_PROC MSG : Switching to Failed mode<br>&lt;131&gt; Point Editor : Received NACK message : 25 from client #1 (Brown, Sean Apr 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The path for the gett.dat file was incorrect. Path has been corrected. (Pingree, Douglas K. Apr 17, 2012) <br> |  | 35 | FINDING | 8331 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73049
29452 | FINDING | Studio dropload aborts when VC is loaded with more than 29K pts. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Configured 29K pts on Virtual contoller by loading 99 Traffic sheets.<br>The last 6 sheets loaded are fast points in Task Area 1. 4 loaded OK.<br>When the last 2 sheets were added and the controller was Droploaded, all the sheets were<br>loaded and seem to be active on the VC 141. No error is shown in the Overrlog.<br>The dropload, however aborts with error:<br><br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br>[External]: (Unable to update target sequence number)<br>[External]: (error (11) from PEDITSimpleModify, OpStat = (0), ErrNum = (0))<br>[External]: (error modifying drop point for target &quot;DROP141&quot;, SID (0x8000008d)) <br>- (Benzvi, Mati Apr 13, 2012)<br>=================================================================================<br>msb - 7/06 in U3 - Added more Traffic sheets, one at a time, to get 31896 points.<br>The last sheet that was loaded OK was 518 in Task Area 5.<br>When sheet 519 was added the load fail. A clear got studio stuck for 30 minutes.<br>After a forced reboot of VC drop141 and a new dropload, studio got stuck again for 20 minutes<br>and than displayed error:<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br> [External]: (Unable to update target sequence number)<br> [External]: (error (11) from PEDITSimpleModify, OpStat = (0), ErrNum = (0))<br> [External]: (error modifying drop point for target &quot;DROP141&quot;, SID (0x8000008d))<br><br>Now Diagnostics shows all 108 sheets in the [Sheet Info] tab, including 519,<br>but Signal Diagram doesn&quot;t see sheet 519, while 518 is running.<br>- (Benzvi, Mati Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Was able to successfully load this drop. Please add more points and see if problem arises again. (Perdeus, Matthew Jul 6, 2012)<br>---<br>msb - 8/10 - In U5:<br> Still cannot see sheet 519 in Siganl Diagram.<br> a. Touched sheet 519 and reload. 16:58<br> b. The dropload loaded area 2 sheets and stopped. @ 17:30 there is no error.<br> b. waited 30 minutes and killed Studio. (Benzvi, Mati Aug 10, 2012)<br><br>Please retest in U8. The load issue is most likely related to a timing issue corrected in U8. The sheet that is titled as sheet 519 is actually numbered as 119. sheet 119 is loaded and running in task 5 in this drop. (Perdeus, Matthew Sep 14, 2012)<br>---<br>msb - 9/19 - in U8: 141 with 108 Sheets &amp; 31898 pts.<br> a. Incremental Load<br> b. Clear and load<br> c. All sheets including 519 appears in Signal Diagrams (Benzvi, Mati Sep 19, 2012) <br> |  | 35 | FINDING | 8332 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73051
29453 | FINDING | Messages regarding loading of Control sheet in a Controller is not logged on the configured EWS | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Created a new control sheet and loaded it successfully in the controller Drop29/Drop79.Error messages for Drop29/Drop79 are configured to be displayed on EWS Drop174. It was observed that following messages are displayed on Database Server Drop176 instead of EWS Drop174:<br> &quot;Drop176 Load Control LOADING DROP29 TASK 2 [101 MASTATION CONTROL SHEET]<br> Drop176 Load operation to &quot;DROP29&quot; completed&quot;<br>However, other messages e.g. &quot;Drop29 Clear in Progess, Drop79 switching to Control,Drop29 switching to Fail mode, Drop29 swiching to Backup&quot; are displayed correctly on EWS drop174. (Lal, Ramesh Apr 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Controller does not report these messages. (Pingree, Douglas K. Apr 16, 2012)<br><br>Drop loading message are displayed on the datababase server<br>- (Hutchison, Steven B. Apr 18, 2012)<br><br>5/16/2012: RL - Finding closed based on Dev&quot;s comment. (Lal, Ramesh May 16, 2012) <br> |  | 35 | FINDING | 8333 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73053
29454 | FINDING | Controller Dignostics need correction in Software Version tab | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Open Controller Diagnostics and navigate to Controller List&gt;DROP29/DROP79&gt;Software Versions&gt;Library Module Versions.For Algorithm the version shown is 3.4/Rev6.0. Here 3.4 may be changed to 3.5 (Lal, Ramesh Apr 16, 2012)<br><br>6/6/2012:RL - O.K. in 3.5_U3. Finding closed. (Lal, Ramesh Jun 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8334 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73055
29455 | FINDING | System Viewer is not a part of Ovation Application Menus. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | System Viewer is not a part of Ovation Application Menus. Application System Viewer can only be opened from Right Click -&gt;Point Menu.<br>An icon needs to be included in Ovation Application Menus. (Sachan, Pallavi Apr 16, 2012) |  |  |  | start the program from start menu and from the ovation applications folder on the desktop. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This has been fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Now we have an icon for OSV in Ovation Application Menus.Finding Fixed hence Closed. (Sachan, Pallavi Aug 29, 2012) <br> |  | 35 | FINDING | 8335 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73057
29456 | FINDING | While logged in as user other than administrator, Point Menu is not functional. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | While logged in as user other than administrator that is Valengr/ Valoper, the Right Click Point Menu does not open Trend and Point Information applications. Only Signal Diagram could be opened by Right Click. (Sachan, Pallavi Apr 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I was able to start Point Information and Trend from the point menu when I was logged in as a user that is a member of the Operator Role and the Group Policy was Operator (locked down).<br><br>What Operating System does this happen on? Is there any messages in the Ovation error Log? Is OvArb running for your session? What permission does the user Valengr/Valoper have? What role is it a member of? (Augustine, Lisa Apr 16, 2012)<br><br>(1)This is observed on OS Win7SP1 for both 64bit and 32bit workstations.<br>(2)Error Log says: <br>Priority 3: UI PDS Arbitrator : ProcessDiagram/diagram_group_init: Error-&gt; unable to open diagram group file.<br>Priority 3: UI PDS Arbitrator : ProcessDiagram/group_init: Error-&gt; unable to open point group initialization file.<br>(3)From Point Menu right click to open System Viewer, message appears OvArb program has stopped responding. (this is another bug which kills OvArb)<br>(4)Permissions and Roles are default for Global.Engineer / Global.Operator. (Sachan, Pallavi Apr 17, 2012)<br><br>It looks like the selection of the System Viewer kills OvArb. Once this happens, the point info and trend options will not open from the point menu. Logout and login again to restart OvArb (verify it is running). Once OvArb is running, check the point information and trend options on the point menu. If this works, the issue is with the System Viewer selection on the point menu. (Augustine, Lisa Apr 18, 2012)<br><br>I checked the above mentioned steps and found the same observations. <br>Kindly suggest that the issue with the System Viewer selection on the point menu, will be handled by same F#, or this one is to be closed and a new F# against System Viewer should be entered. (Sachan, Pallavi Apr 20, 2012)<br><br>We will use this finding. We do not need to open another one. I assume you mean that the point info and trend worked for Valengr/Valoper when this was tested without selecting the system viewer. What type of point were you selecting the system viewer option for? What hardware was it configured for? (Augustine, Lisa Apr 20, 2012)<br><br>Is there an OvSystemViewer.exe file in the OvationBase directory? (Augustine, Lisa Apr 20, 2012)<br><br>Yes, OvSystemViewer.exe is present in the C:\Ovation\OvationBase directory.<br>Any point LA\LD\LP, right clicked from AlarmWindow/ Point Review Window/ Trend Window/ Graphics/ etc, gives option to open System Viewer Application. Points may may not be configured for any hardware.<br>[While logged in as administrator, when hardware is configured for a point, it opens system viewer to that tab and if hardware is not configured, system viewer opens showing error window &quot;an error occured loading the specified point.] (Sachan, Pallavi Apr 23, 2012)<br><br>Log in as Valengr/Valoper. Select the System Viwer from the point menu. After it terminates start a command tool and go to the Ovationbase directory. Run the OvArb.exe program. After this select the System Viewer option on the point menu and see what messages are writtent to the command window where the OvArb.exe was started by hand. Let me know what the results of this test is. (Augustine, Lisa Apr 23, 2012)<br><br>Permissions and Roles are default for Global.Engineer / Global.Operator, hence there is no permission to go to the OvationBase folder or start any service or run command prompt window. Am I supposed to grant permissions of all these tasks to user Valengr/Valoper from Ovation Security, and perform the desired action?? (Sachan, Pallavi Apr 24, 2012) <br> The issue is with the Group Policies assigned to the locked down user. When the OvSystemViewer.exe is not listed under System, Run Only Allowed Windows Applications, the selection of the System Viewer on the point menu results in an exception being raised to teh OvArb application when it tries to start the process. Since the execption is not handled, the process terminates. The OvArb application will be updated to handle the exeption and the group policies will have to be updated to add the OvSystemViewer.exe to the list of allowed applciations. You can test this on one of your 3.5 networks by manually adding the OvSystemViewer.exe to the Group Policies, System, Run only Allowed Windows applications foe the locked down user. (Augustine, Lisa Apr 24, 2012)<br><br>I added OvSystemViewer.exe to the Group Policies, System, Run only Allowed Windows applications for both the Engineer and Operator locked down user. And found the application to be working fine. My querry would be why this needs to be done manually? (Sachan, Pallavi Apr 25, 2012)<br><br>You should not have to do this manually. I need to update the security policy xml so you will not need to do it manually. I just wanted you to do this on one network to verify that was the only issue. The security policy xml and the OvArb process will be updated to accommodate this issue. (Augustine, Lisa Apr 25, 2012)<br><br>Found Fixed. Hence Closed. (Sachan, Pallavi Jun 7, 2012) |  | 35 | FINDING | 8336 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73059
29457 | FINDING | Ovation GBNT Application crashes, when point is browsed in Poke. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | In Ovation GBNT, when we call Application POKE(Control 23),Chose a program, Application Program Parameter List window is opened. Now click on option Browse PTS, Application Program: Point Browser Window opens. Select a point click OK, this crashes GBNT.<br>Kindly find GBNT - PT BRWSR CRASH.jpg attached. (Sachan, Pallavi Apr 16, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Graphic Builder (OW-GB)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U0 28-MAR-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Johnson, Kathy Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-04-16T05:43:58-04:00</p> <p><strong>Modified Date:</strong> 2012-04-16T10:12:16-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8337 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73060
29458 | FINDING | New points created in controllers show bad quality even if initial values are defined in the Developer Studio | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Created new LA/DA/LD/DD type points in the Controller and droploaded the controller. It was observed that these point show BAD quality in the Point Info.If we define some initial value even then quality is BAD. However, if we scan off the point, force some values and scan on the point then quality will become GOOD. (Lal, Ramesh Apr 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | If you create a new point without an initial value and load the controller with that configuration and then you add an initial value to the point and re-load the controller the point&quot;s value on the controller will not be set to the initial value and the point quality will remain BAD. If the controller is re-booted then the initial value will be used and the quality will be set to GOOD. If the controller is cleared before being loaded after the initial value is set then the quality will also be set to GOOD. This same behavior has been verified in 3.2 and 3.3.1 and 3.5. This is the way it works. (Boehmer, Robert W. Dec 4, 2012)<br><br>12/10/12: Finding closed based on Dev&quot;s explanation (Lal, Ramesh Dec 10, 2012) <br> |  | 35 | FINDING | 8338 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73062
29460 | FINDING | Adding Multiple points into trend application, it gets hanged. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | 1.Open Trend application.<br>2.Try to add multiple points at a time(more than 20).<br>3.Trend application gets hanged.User can not be moved from one tab to another tab (e.g. Graph to Table view etc.)<br>4.Wait for some time.Open task Manager.<br>5.Task manager shows the status that Trend is not responding.<br>6.Trend application needs to be killed from task manager.<br>7.Occasionaly error comes for Graph and Radar view.Both tabs can not be opened.<br>8.The same behaviour is for loged in by Administrator,Engineer,Operator.Test is done on Drop205.<br>9.Please find the attched snapshots. (Athavale, Samiradixit Apr 16, 2012) (Athavale, Samiradixit Apr 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Code has been added to Trend Application to detect invalid floating point value and treat it as NULL (missing) value. So if the BAD floating point values originated on highway and went into TrendCollect and then into Trend, new code is supposed to fix the issue. Retesting required.<br><br>Please retest in 3.5.0_U1 (Bargaje Prashant Apr 20, 2012)<br><br>As the new Code is added in to Trend Application,then I think Finding status should be LIB.Previously With multiple points Trend application gets hanged.Now in 3.5.0_U2 Trend is working fine even after adding multiple points. (Athavale, Samiradixit May 30, 2012)<br><br>I am changing the status of this finding to LIB. (Bargaje Prashant May 30, 2012) <br> Adding Multiple points into trend application,working fine.Hence finding is closed. (Athavale, Samiradixit Jun 1, 2012) |  | 35 | FINDING | 8340 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73066
29462 | FINDING | Explore tab in Trend application is showing error for each topic under Explore tab. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | 1.Open Trend Application.Click on Explore tab.It shows Choose topic window.<br>2.Topics are Current Preferences,Application Base style,User Default style,Current Trend Defination,Trend Files,Trend Style Files.<br>3.Click on each of the topic gives error.Could not find the file.Please find the attached snapshot of the error.<br>4.If click on quit,Trend application gets closed. (Athavale, Samiradixit Apr 17, 2012) (Athavale, Samiradixit Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The XSL files in directory Ovation\mmi\trend\xslfiles were missing.<br><br>In 3.5.0_U1, they should be in place after install.<br><br>Please retest. (Bargaje Prashant Apr 20, 2012)<br><br>Below observations found after retesting in 3.5.0_u1:<br>1.After click on Explore tab Current Preferences,Application Base style,User Default style,Current Trend Defination,Trend Files can be opened.<br>2.If click on &quot;Trend Style &quot;,it will open trend style window.If I select any trend style (which is created in trends earlier) and click on open, then respective trend style window will be opened,but it is in blank format.It does not give any information.<br>3.Please find the attached snapshots for the reference. (Athavale, Samiradixit May 2, 2012) <br> Because of a design change (name of a field changed in TS file) that was made in 3.5 U1 code, the older file will show as blank in 3.5 U1.<br><br>Older TREND STYLE files should be replaced by saving them again. (Bargaje Prashant May 3, 2012)<br><br>Found fixed in U2.Hence Finding is closed. (Athavale, Samiradixit May 11, 2012) |  | 35 | FINDING | 8342 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | [8 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73070
29463 | FINDING | Log File of Error Log is not in readable format. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | 1.Open Error Log.Click on Save as option.<br>2.Log file will be generated in Text document format.It will open in Notepad.<br>3.This saved Log file is not in readable format.It is not showing proper columns,column names.<br>4.Where as If Alarm file will be exported,it will also save in Text document format which appears with column and column names.<br>5.Please find the attached Files for reference. (Athavale, Samiradixit Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | As per the email communication with Mati &amp; Nooch(dated on 8/13/2012) there is no plan to chnage the Error Log Format.Hence finding is closed. (Athavale, Samiradixit Aug 29, 2012) <br> |  | 35 | FINDING | 8343 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73072
29464 | FINDING | In Graphics application, if the Main Toolbar gets closed,it never gets opened again. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | 1.Open Graphics application.Close the Main toolbar by click on the cross mark on it.<br>2.Try to open the Main Toolbar from View tab.<br>3.Main Toolbar does not get open again.<br>4.User Need to close the Graphics Application then only it will display the Main Toolbar. (Athavale, Samiradixit Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Update to allow the &quot;Main Toolbar&quot; option to redisplay the toolbar when it has been closed. (Spillane, Donal A. Aug 24, 2012)<br><br>1.Open Graphics application.Close the Main toolbar by click on the cross mark on it.<br>2.Try to open the Main Toolbar from View tab.It shows that Main Toolbar is already selected with checked mark.(Which should be unchecked because Main Toolbar is closed.)<br>3.Again click on Main Toolbar (under view tab).Checked mark gets removed.<br>4.Now select Main Toolbar from view tab.It gets selected with checked mark.<br>5.Main Toolbar gets restored again.No Need to close the Graphics Application.<br>Hence finding is closed. (Athavale, Samiradixit Aug 30, 2012) <br> |  | 35 | FINDING | 8344 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73074
29465 | FINDING | PI window is showing unpredictable behaviour on "Limit" tab. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | Steps to reproduce:<br>1.Create an analog point (LA, DA) on any type of ovation drop (Controller/ EWS).<br>2.Keep all the limit setting of the point by default (All the limit setting remains blank by default)<br>3.Load the corresponding drop and see the point limits on PI window from &quot;Limit&quot; tab.<br>Observation: It is observed that the point fields ZM (Low incremental alarm limit) and DJ (Low alarm dead band) can be editable from PI.<br><br>Conventionally if the limit setting are kept blank from developer studio then should not be able to edit the corresponding field value from PI , but for above two fields it is not working as convention. (Joshi, Parmesh Apr 17, 2012) (Augustine, Lisa Apr 18, 2012)<br><br>PJ:2nd May 2012 : Checked on build 3.5.0_U1 and found ok i.e. can not edit fields (ZM, DJ) if nothing configured (kept blank) in developer studio. hence closed. (Joshi, Parmesh May 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The logic in the function that determines whether the field is can be edited has been fixed for the ZM and DJ fields. (Augustine, Lisa Apr 18, 2012) <br> |  | 35 | FINDING | 8345 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73076
29466 | FINDING | User has to manually add cbEditor.exe program in Security Builder in order to access Control Sheets from DS | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 |  |  |  | 2015-06-12 04:02 |  |  |  | USPITTFSService | 2015-06-12 04:02 |  | In Manage Ovation Security--&gt;Manage Group Policies window, for Valengr user [Group Policy -Engineer (locked down), Roles - Global.Engineer] user has to manually add [cbEditor.exe] Windows application program in order to access Control Sheets from Developer Studio when logged in with Valengr user. Please refer the attached snapshot file cbEditor_group_policy.jpg. Please note that by default the Engineer Role has Engineering Rule [Allow full access to Ovation control sheets - Enabled] for Local as well as Remote Console. So if the user is unable to open the control sheets from the Developer Studio then this rule is not useful.<br>I feel that the cbEditor.exe program should by default appear in the group policy list for Engineer. (Gupta, Chandresh Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Even though Valengr user is assigned a &quot;Global Engineer&quot; Role which has full access to Ovation control sheets, this doesn&quot;t give automatic access to the cbEditor.exe application. This engineering rule is meant to only restrict access to editing control sheets from inside Ovation Developer Studio - specifically whether the menu item to open control sheet should be enabled or not.<br><br>Permission to launch an application itself, by a specific user, is governed by Windows Group policy (Not Ovation Roles) setting. In this case, Valengr is assigned to &quot;Engineer (Locked Down) which doesn&quot;t allow CbEditor.exe to be launched, or for that matter any external engineering tool applications.<br><br>In this case although the Ovation Role says that Valengr is allowed to edit control sheets, it is overruled by the Group Policy setting (Engineer lockdown) which doesn&quot;t have permission to launch cbeditor.exe. It&quot;s not a bug and is the way it is supposed to work.<br><br>In the real world, this configuration doesn&quot;t make much sense. Why a user is configured to be &quot;Global Engineer&quot; for Ovation Roles (which by default has all engineering permission), but be &quot;Engineer - locked down&quot; (which restricts all lauching capabilities of engineering tools external application, such as cbeditor) for Group policy. This does not seem to be a valid configuration in the real world. (Swartz, Mark E. Apr 17, 2012) <br> cg (05/02/12) - Per developers comments above this finding is closed. (Gupta, Chandresh May 2, 2012) |  | 35 | FINDING | 8346 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73078
29467 | FINDING | Window Size Configuration can not be saved for Graphics Application window. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:02 | [11 empty] | USPITTFSService | 2015-06-12 04:02 | [7 empty] | USPITTFSService | 2015-06-12 04:02 |  | 1.Open Graphics Application.Open File tab.Click on Configuration.It will open Configure Graphic window.<br>2.Try to open Window tab.Windows Size:Height error will occur.Click on Ok.Windows Size:Width error will occur.Click on Ok.Then only Windows tab will open.<br>3.Now to remove above errors,in Window size Selected Custom tab and selected Height(e.g.1200) and width (e.g.450) for Window-1 (in Select Window) Click apply and ok.<br>4.The Opened Graphics application window will be dispalyed in above customized size.<br>5.Close Graphics application and open it again.This time Graphics application will not open in customized size which is given for window-1.<br>6.Open Configuration from File tab.Open window tab.Again it will display the same error for Windows Size:Height and Windows Size:Width.<br>7.Window size settings can not be saved for Graphics application.Where as in Ovation3.1.3 and 3.2.0 Customized window size get saved.Testing is done on Drop203 (Screen Resolution for Drop203 is 1440*900)Please find the attached snapshots for reference. (Athavale, Samiradixit Apr 17, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Graphics (GR)</p> <p><strong>Release Level:</strong> 3.5.0_U0 28-MAR-12</p> <p><strong>Originator:</strong> Athavale, Samiradixit</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Athavale, Samiradixit</p> <p><strong>Entry Date:</strong> 2012-04-17T07:42:17-04:00</p> <p><strong>Modified Date:</strong> 2012-04-17T07:42:17-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8347 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73079
29468 | FINDING | The ab_test tool cannot be executed. | Ritchie, Mark AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Loading ab_test in an OCR400 returns the following message:<br>ld(): module contains undefined symbol(s) and may be unusable.<br><br>Running the tool returns errors (Telnet session attached). (Brown, Sean Apr 17, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> Allen Bradley (AB)</p> <p><strong>Release Level:</strong> 3.5.0_U0 28-MAR-12</p> <p><strong>Originator:</strong> Brown, Sean</p> <p><strong>Responsible:</strong> Ritchie Mark A.</p> <p><strong>Notify List:</strong> Pingree, Douglas K. Brown, Sean Zaremsky, Mark</p> <p><strong>Entry Date:</strong> 2012-04-17T12:51:42-04:00</p> <p><strong>Modified Date:</strong> 2012-08-07T15:31:58-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8348 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Zaremsky, Mark External MZCI | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73080
29469 | FINDING | The Default Router configuration is not used by an OCR400. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Default Router configuration is present in the /ata0/etc/routes file, but is not used (netstat -r does not show an entry for 0.0.0.0/0).<br><br>This prevents testing with third-party devices that reside on other networks. A routec command can be used to manually define the default route, but it is lost after a reboot. (Brown, Sean Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Development Completed. (Pingree, Douglas K. May 15, 2012) <br> |  | 35 | FINDING | 8349 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73082
29470 | FINDING | Modbus Master in OCR400 cannot connect to its device. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | An OCR400 configured with a Modbus Master device reports the following messages:<br>Modbus Device 3 : could not ping 172.16.42.244<br>Modbus Device 3 : could not connect to 172.16.42.244:502<br><br>The IP address above can be pinged from a Telnet session with the controller (including from mod_test) and a Telnet session to the IP address and port from a workstation can be opened as well. In this case the device is a simulator program running on a workstation connected to the same network. (Brown, Sean Apr 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Several changes were made to the kernel (added support for routec command) and device drivers as part of the migration. Additional changes will be added for U6. Retest. (Ciccozzi, Anthony Aug 7, 2012) <br> |  | 35 | FINDING | 8350 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritchie, Mark AUTOSOL PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [7 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73084
29471 | FINDING | Column Sorting is non-functional for Ovation Alarm System. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Ovation Alarm System(Alarm Application window).<br>2.Click on column e.g.Name. The column remains as it is.It does not get sorted in alphabetical manner.<br>3.The behaviour is same for all columns.e.g.Date,Alarm type,Code,Name,Description,AP,AY,Value,Q,Units,Incr,PM,Net Alias,Net ID (Athavale, Samiradixit Apr 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: In Studio is Alarm Widow Style configured as Legacy/Classic Style. If it is then sorting will not work. Also make sure Modify Alarm Widow Properties is Enabled. (Matreja Shyam Apr 18, 2012)<br><br>In studio Alarm Window Style configured as Enhanced Grid Mode style at system level configuration.Could not find Modify Alarm Widow Properties at system level Alarm Configuration. (Athavale, Samiradixit Jun 1, 2012)<br><br>smatreja: Please send me the screen shot of the alarm window application. You will need to use the Ovation Security tool to configure the security for Modify Alarm Window properties. (Matreja Shyam Jun 1, 2012) <br> After configuring Alarm style as &quot;Enhanced Grid Mode Style&quot;in Studio and downloading respective drop Column sorting is functional.Hence finding is closed. (Athavale, Samiradixit Aug 30, 2012) |  | 35 | FINDING | 8351 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73086
29472 | FINDING | control sheets found in signal diagram and in compile operation window even after its control task is deleted directly | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1. If a control task , which is having some control sheets, is deleted directly without deleting its control sheets first, then after clearing &amp; loading the controller, the deleted control task (and its control sheets as well) is still appearing on &quot;Compile operation window&quot; and &quot;Signal diagram&quot;<br><br>2.If the deletion is done one by one (i.e. 1st delete the control sheets then delete the control task), then the task and its sheets not appearing in &quot;Compile operation window&quot; and &quot;Signal diagram&quot; after clearing&amp;loading the controller.<br><br>Checked on ov 3.4.0 , found the same behavior (Joshi, Parmesh Apr 18, 2012) (Swartz, Mark E. Apr 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a duplicate of SDR 17013. Deleting an object above the control sheet does not delete all the files for descendent control sheets. (Hutchison, Steven B. Apr 18, 2012)<br><br>Since it is found as duplicate of SDR 17013. Hence closed. (Joshi, Parmesh Jun 15, 2012) <br> |  | 35 | FINDING | 8352 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73088
29473 | FINDING | Controller does not come up after definining Numa logic device. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On Ov3.5.0 ,tried to configure Numalogic in OCR400 controller(drop29/79).<br>Following steps were done:<br><br>1)Configured N3 Port of controller for Ethernet Remote Interface.<br>2)Added new Ethernet Remote Device for Device 2.<br>3)Added New I/O device (i.e. I/O device 5) with selection as Ethernet Remote.<br>4)Added New Ethernet Remote Node(Node1) with I/O selection as Numalogic.<br>5)Assigned Node point to this device.<br>6)Downloaded drop29.<br>7)Cleared drop29.<br><br>After step 7 controller drop29 does not come up online on highway.<br><br>We can telnet this drop29 and error log from this drop is attached.<br>We cannot bring this controller up unless and until Numalogic device is removed from controller&quot;s configuration. (Kumar, Shailendra Apr 18, 2012)<br><br>SK:Checked in U3, controller does not goes off highway. (Kumar, Shailendra Jun 11, 2012)<br> 12/6/12: Problem still exists in U3, hence reopening. (Kumar, Shailendra Jun 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected several NL issues in U6. (Pingree, Douglas K. Aug 21, 2012)<br><br>SK:Now controller does not goes offhighway but comes in failed state (66,1,04,1), NL HW is not connected to this controller and Node was defined not to fail the controller(attached is the error log-Drop29_latest). (Kumar, Shailendra Oct 23, 2012) <br> Try this again. When downloading DO NOT select the reboot option. When download completes clear the drop and load. (Boehmer, Robert W. Oct 29, 2012)<br><br>As adviced tried downloading/clear load and it was sucessfull.<br>But if reboot option is used after Download controller fails and even clearing/load does not resolves this. (Kumar, Shailendra Oct 30, 2012)<br><br>This behavioir exists in pre 3.5 versions of Ovation. In general after adding a new driver to a controll the controller MUST be cleared and loaded. This was verified on a 3.3.1 Ovation system. (Christy, Benjamin Nov 26, 2012) |  | 35 | FINDING | 8353 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73090
29474 | FINDING | Column Chooser customization is not functional in Ovation Point Review. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Ovation Point Review Application.<br>2.Right click on any coumn Header e.g.Alarm Status. Column Chooser option will be displayed.<br>3.Click on &quot;Column Chooser&quot; Customization window will be opened.It gives message &quot;Drag &amp; Drop columns here to customize layout&quot;<br>4.After try to drag and drop any coulmn in Customization window,Drag and drop action will never occur.<br>5.The same behaviour is observed for all coulmns.e.g.Point name,Drop,Description,Characteristic,Alarm Status,Value,Quality,Point status etc.<br>6.Where as same functionality of Coulmn Chooser is working for Ovation Alarm System. (Athavale, Samiradixit Apr 18, 2012) (Athavale, Samiradixit Apr 18, 2012) | none |  |  | Right click on column header and ensure column chooser functionality operates properly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Change properties on main grid to enable column chooser functionality. (Burgoon, Frank J. Apr 27, 2012)<br><br>Column Chooser customization is working fine.Found Fixed in Ov 3.5.0 U2.Hence Finding is closed. (Athavale, Samiradixit May 10, 2012) <br> |  | 35 | FINDING | 8354 |  | FINDING | [10 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73092
29475 | FINDING | In marker lines & Stripes dilog box of trend application,first coloum is not expanding through cursor. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br><br>1. In Trend application windows click Display settings from Menu bar--&gt;Configure Settings window open.<br><br>2. click on master scale tab &amp; select &quot;Lines&quot; row----&gt;Marker Lines window opens<br><br>3. Expand the Number coloum(First Column)--&gt; not able to expand <br><br>Effects: if the number count increases beyond 2 digit (99), it is not visible on default width.<br><br>Same behaviour is observed on Stripes&quot; window as well (Configure setting--&gt; Master Scale --&gt; Stripes) (Prasad, Parmatma Apr 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed in 3.5.0_U2.<br><br>The width of the column will change automatically based on the sequence number displayed in that column. (Bargaje Prashant May 3, 2012)<br>Retested in Ov3.5.0_U2 release,the issue has been resolved. (Prasad, Parmatma May 7, 2012) <br> |  | 35 | FINDING | 8355 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Contento, James AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73094
29476 | FINDING | OvationOnLineSynchronizer is slowing down the DBS. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OvationOnLineSynchronizer consistently uses 80% or more of the CPU on DBS 245 (WALT system). (Brown, Sean Apr 18, 2012) |  |  |  | Get me prior to next installation to reset the registry to initial settings. After next update problems should not exhibit itself. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Installation did not set-up registry. The timers were zero, to the process tried to continuous resynch or generate catalog. Set default times to more reasonable values.<br><br>- (Hutchison, Steven B. Apr 20, 2012)<br><br>OK in U2; closing. (Brown, Sean May 7, 2012) <br> |  | 35 | FINDING | 8356 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73096
29477 | FINDING | OracleServicePTDB service failed to start upon configuration change and drop reboot | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | After making a DDB size change in Studio, Downloading and rebooting the Database Server<br>the OracleServicePTDB service failed to start with the following error in <br>C:\Oracle\Ora11g\diagnostics\diag\rdbms\ptdb\ptdb\trace\alert_ptdb.log:<br><br>Wed Apr 18 16:01:51 2012<br>***********************************************************************<br>Fatal NI connect error 12638, connecting to:<br> (DESCRIPTION=(LOCAL=YES)(ADDRESS=(PROTOCOL=beq)))<br><br> VERSION INFORMATION:<br>TNS for 64-bit Windows: Version 11.2.0.3.0 - Production<br>Oracle Bequeath NT Protocol Adapter for 64-bit Windows: Version 11.2.0.3.0 - Production<br> Time: 18-APR-2012 16:01:51<br> Tracing not turned on.<br> Tns error struct:<br> ns main err code: 12638<br> <br>TNS-12638: Credential retrieval failed<br> ns secondary err code: 0<br> nt main err code: 0<br> nt secondary err code: 0<br> nt OS err code: 0 (Benzvi, Mati Apr 18, 2012) (Benzvi, Mati Apr 25, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The modification of this Ovation configuration item (DDB size change) should have no effect on the operation of the Oracle database. In fact, there are no downloadable configurations which effect the configuration or startup of the Oracle database.<br><br>There have been very isolated occurrences in other Ovation systems where OracleServicePTDB failed to start following reboot (even though the Services UI indicates &quot;Started&quot;). In some cases, it appears to be related to additional network interfaces which were disconnected at the time of reboot. Proper ordering of the interfaces and/or disabling any interfaces which are disconnected can sometimes restore proper &quot;reboot behavior&quot;. There has also been speculation that there is a timing issue.<br><br>When this situation occurs, the simple work-around is to manually restart OracleServicePTDB service via the Services UI (e.g., Server Manager).<br><br>Due to the nature of this inconsistently occurring issue and the fact that there is a simple one-time work-around following reboot, the category of this Finding will be changed from 2 to 3.<br><br>Please verify whether or not this issue occurs every time this particular Database Server is rebooted. (Swartz, Mark E. Apr 19, 2012)<br><br>Verbal feedback indicated that this issue did occur every time this particular Database Server was rebooted. Please confirm whether or not this Database Server is also the Domain Controller. (Swartz, Mark E. May 11, 2012)<br>---<br>msb - Closing as CND - earliest log on file is Apr-27. (Benzvi, Mati Aug 10, 2012) <br> |  | 35 | FINDING | 8357 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73098
29478 | FINDING | The points appears on Ovation point browser window without selecting any drops. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br>1:- Open the Trend Window.<br>2:- Click on the &quot;Add point&quot; option from menu bar. Specify Point Information window is open.<br>3:- click on point browser, open the Ovation Point Browser window.<br>4:- Select the &quot;Network/Unit&quot; button, Press on Refresh tab &amp; Press Ok.<br>5:- Select the Drops button, dselect all the drops &amp; Press Ok.<br>6:- Press the Start button.<br> As shown in screen shots &quot;point appears on point browser window.jpg&quot;, Even after deselecting the ALL Drops, Points names are appearing in lower window.<br>Same observation is found while Ovation point browsing through Ovation Point Information. (Prasad, Parmatma Apr 19, 2012) | none |  |  | In point search window deselect all drops. Search should return zero points. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Point search window changed to return no points if no drops are selected. (Burgoon, Frank J. Apr 27, 2012)<br>Retested in Ov3.5.0_U2 release,the issue has been resolved. (Prasad, Parmatma May 7, 2012) <br> |  | 35 | FINDING | 8358 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73100
29479 | FINDING | Background, Foreground & Grid colors of trend application window are not changing. | Contento, James AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br>1:-Open &quot;Ovation developer Studio&quot; window.<br>2:-Change the Trend Background color from ¿white to yellow¿ at Drop level.<br>(e.g.: Go to Drop182--&gt;Configuration--&gt;Trend--Press Trend Window Tab).<br>3:-Press Apply button &amp; then press OK button.<br>4:-Download Drop182 &amp; then reboot the system.<br>5:-Open trend window application then the trend application open its default background white color.<br>Same behavior is observed of Foreground &amp; Grid.(Drop182--&gt;configuration--&gt;Trend--&gt;Trend Window Tab). (Prasad, Parmatma Apr 19, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Trend (TR)</p> <p><strong>Release Level:</strong> 3.5.0_U0 28-MAR-12</p> <p><strong>Originator:</strong> Prasad, Parmatma</p> <p><strong>Responsible:</strong> Contento, James L.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Prasad, Parmatma</p> <p><strong>Entry Date:</strong> 2012-04-19T03:06:57-04:00</p> <p><strong>Modified Date:</strong> 2012-04-19T03:06:57-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8359 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73101
29480 | FINDING | Print Preview window of Ovation Alarm System gets crashed inconsistently. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Ovation Alarm System.Click on print tab.It will open print and preview window.<br>2.Click on Print Preview tab.It will open Print preview of Alram window.<br>Case 1: While scrolling mouse button up &amp; down of Print preview window,it gets crashed sometimes.<br>Case 2: After giving print command,Print preview window gets crashed sometimes.<br>Case 3: After changing Page setup&gt;Paper&gt;Size&gt;A4,Print preview window gets crashed sometimes.<br>Case 4: After selecting Header &amp; Footer tab and changing Font&gt;Arial,adding Page number,Date,User name to Footer Print preview window gets crashed sometimes.<br>Case 5: It has observed that sometimes Print Preview window appears in proper manner.<br>Testing is done on DrOP205.<br>Please find the attached snapshot for reference. (Athavale, Samiradixit Apr 19, 2012) (Athavale, Samiradixit Apr 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest in next build i.e U2. (Matreja Shyam Apr 30, 2012)<br><br>Found Fixed in Ov 3.5.0 U2.Hence finding is closed. (Athavale, Samiradixit May 11, 2012) <br> |  | 35 | FINDING | 8360 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73103
29485 | FINDING | When Copying or Importing a sheet in cbOperation the first sheet"s title is set to EC_ORDER. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step1: Create a control sheet.<br>Step2: Now right click on sheet through dev. studio and select Control options-&gt;Copy Operation.<br>Step3: Choose another drop/Task/Sheet number for new sheet. Complete Copy operation successfully.<br>It is observed that the new sheet is copied as desired in the proper drop/Task/Sheetnumber but with sheet title as &quot;EC_ORDER&quot; and also the existing sheet title changes to &quot;EC_ORDER&quot;. This happens inconsistently. Later the Drop Load operation gives error loading sheet for the existing sheet and load operation could not be completed. <br>It is also observed that this EC_ORDER sheet is created generally if this is the first and only sheet in the control task. (Sachan, Pallavi Apr 20, 2012)<br><br>Drop Load Error is unrelated to setting the first sheet in a copy, import from cbOperations, and new control function in the cbEditor.<br>- (Hutchison, Steven B. Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The first sheet created during the import or copy looses the sheet title.<br><br>Fixed. - (Hutchison, Steven B. May 10, 2012)<br><br>The problem was monitored for long duration and EC_ORDER named sheet is not observed during any operation. Hence Finding is Closed. (Sachan, Pallavi Jun 19, 2012) <br> |  | 35 | FINDING | 8365 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73113
29486 | FINDING | Sheet title having special characters, shows changed Sheet Title at compile operation window. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Insert a sheet in controller drop, through Dev.Studio. <br>Sheet Title can be given special Characters. Save the sheet and perform compile operation.<br>At Compile operation -&gt; Completed Window, the Title consists of &quot;-&quot; instead of given special characters, like &quot;!,#,$,%,&amp;,*,(,),+,=,-,~,`,¦,\{,},:,&quot;,&quot;,&lt;,&gt;,?,/&quot;<br>eg. if the sheet Title is &quot;OV$350#D7&amp;T2&quot;, it looks as &quot;OV-350-D7-T2&quot;. (Sachan, Pallavi Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it works - no plans to fix.<br>- (Hutchison, Steven B. Apr 20, 2012)<br><br>In this case we should document that the above mentioned special characters are seen as &quot;-&quot; in the compile operation completed window. (Sachan, Pallavi May 31, 2012)<br><br>No Plans to Fix or Document. There is no reason to highlight what most users would never notice.<br>- (Hutchison, Steven B. Jun 8, 2012)<br><br>Closed as per above comments. (Sachan, Pallavi Jun 10, 2012) <br> |  | 35 | FINDING | 8366 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73115
29488 | FINDING | XPID algorithm, does not have options to Raise/Lower Setpoint. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Raise/Lower Setpoint tabs are not available for XPID Algorithm.<br>This option is available till Ovation 3.1.3 Release. (Sachan, Pallavi Apr 20, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U0 28-MAR-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-04-20T02:15:42-04:00</p> <p><strong>Modified Date:</strong> 2012-05-25T04:54:59-04:00</p> | 0 |  | Ovation for Windows/General/Software | See Finding 2637 - Works as Designed. (Hutchison, Steven B. Apr 24, 2012) <br> As per developer&quot;s comments I understand that the &quot;Raise/Lower Setpoint tabs have been removed from XPID Algorithm. <br>Kindly modify Test Case 5.4.1 of 3.5_ST_BASIC_FUNCTIONS_SVTP_rev1.M_PS.doc for XPID algorithm. Raise/Lower Setpoint Tab testing needs to be removed. (Sachan, Pallavi May 25, 2012) |  | 35 | FINDING | 8368 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [10 empty] | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73118
29490 | FINDING | Deleting LA/LD/DA points of workstation (EWS) drop & subsequent loading it FAILS the drop | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps performed are:<br>1. Created LA, LD, DA points in workstation (EWS) drop245. Only point limits were defined.<br>2. Loaded drop245. The drop loaded successfully without any error.<br>3. Deleted the created points &amp; again loaded drop245.<br>4. This time drop245 FAILED with DPU ERROR OPP Subsystem Error.<br>Please refer the attached snapshot file drop245_fail.jpg.<br>Similar behavior is observed on drop203 also.<br>Please note that the mentioned behavior happens inconsistently. (Gupta, Chandresh Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Tried unsuccessfully to recreate this on our system. How many points are being added/deleted? Can this be retried on U3? If it still happens, please send the database export for one of these drops. (Perdeus, Matthew Jun 6, 2012)<br><br>cg (06/12/12) - I have used around 10 points of different Record types. I tried adding points--&gt;Loading controller drop--&gt;deleting points--&gt;loading controller drop several times in Ov3.5.0_U3 also. However, I was also not able to recreate the scenario of EWS drop fail. Please suggest if I should keep the finding as Open-Monitoring or shall I close the issue. (Gupta, Chandresh Jun 12, 2012) <br> Please close. Can not duplicate. (Pingree, Douglas K. Jun 26, 2012)<br><br>cg (06/26/12) - Closing this finding as the issue could not be duplicated on 3.5.0_U3. (Gupta, Chandresh Jun 26, 2012) |  | 35 | FINDING | 8370 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73122
29492 | FINDING | Silence Audio button in Alarm window is not working for Ovation Alarm System | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I have configured Audio Alarm settings in studio:<br><br>Audio type as continuous-&gt; Audio<br>Silence Audio with Alarm Acknowledgement -&gt; Enable.<br><br>When Audio Alarm comes then Silence Audio in Alarm window is not working for Ovation Alarm System even it shows enable. (Singh, Ghanshyam Apr 20, 2012) |  |  |  | The silence audio function of the alarm window has been affected. The sending of the silence audio message to the continuous audio was failing. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | What is the configuration for the contiunous audio? The silence audio will be sending a message to the continuous audio process running on the drop where the Silence Audio with Alarm Acknowlege function is configured. (Augustine, Lisa Apr 20, 2012)<br><br>GS: I have done all configuration on local drop and Silence Audio with Alarm Acknowlege enable for the drop.Even I have observed memebrane key board Audio silence working fine on the drop.Same Expriment has been performed on 3.4.0 release and found desire result. (Singh, Ghanshyam Apr 20, 2012)<br><br>what is the operating system? (Augustine, Lisa Apr 20, 2012)<br><br>GS:My os is win-7 sp-1. (Singh, Ghanshyam Apr 25, 2012) <br> GS:tested in U3 and found fixed, hence closed. (Singh, Ghanshyam Jun 12, 2012) |  | 35 | FINDING | 8372 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73126
29493 | FINDING | Other than first priority alarms are not working for Audio alarm. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I have configured individualy all priorities in Audio files one at time.<br>e.g. alarm with priority 2 is set in audio then and no any other priorities alarms are configured .<br>Observation:All priority alarms are not working for Audio alarm Other than priority 1. (Singh, Ghanshyam Apr 20, 2012) |  |  |  | The changing of the filtering for the audio has been affected. The issue was a result of the increase in the number of networks, which is used in the filtering message that is sent when the filter is updated. This was failing, so the system was always annunciating priority 1 alarms. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | When the priority 1 alarm is sounding no other priorities will be annunciated. The continuous audio only annunciates the highest priority alarm. A lower one will not be heard. When you say you cannot hear the priority 2, did you silence the priority 1 audio and then trigger the priority 2 alarm without any priority 1 alarms being triggered? Is there a valid audio file configured for both prioriyt 1 and 2 alarms? I am not sure if you completely understand how the continuous audio is suppose to work. If you are not sure, you should discuss this with validation personnel that are more familiar with the continuous audio system. (Augustine, Lisa Apr 20, 2012)<br><br>GS(04/12/2012):When I configured alram priority 2 that time no other alarm was configured in audio.Audio files is good becasue for the priority 1 also the same files are used.<br>I have performed same test to 3.4.0 release, it gave me desire result. (Singh, Ghanshyam Apr 20, 2012)<br><br>What operating system does the drop have? When you do not hear the priority 2 alarms, did the priotity 1 alarm silence actually silence the audio? (Augustine, Lisa Apr 20, 2012)<br><br>GS(04/25/2012):My OS is win7 sp-1.Once I am configuring Alarm Priority 2 no other priorites are configured even priorty 1, so there is no issue with pririty 1 silence becaue it is not configured. (Singh, Ghanshyam Apr 25, 2012) (Singh, Ghanshyam Apr 25, 2012)<br><br>When you say it is not configured, what do you mean? Did you simply leave the audio file blank? If so, did you filter out priority 1 alarms? If the priority 1 alarm are not filtered out, the contiunous audio will be notified to sound the priority 1 audio file. If none is configured, then nothing will be sounded. The audio only receives the highest priority alarm that passes the filter each second. (Augustine, Lisa Apr 25, 2012)<br>GS:your statement is a bit confusing for me , please eleborate the test. (Singh, Ghanshyam May 3, 2012)<br><br>I mean what are the audio files you have configured for each priority? When you say &quot;priority 1 is not configured.&quot; What did you do to accomplish this? Did you filter out the priority 1 alarms on the alarm list? What did you configure in the audio for the priority one file? (Augustine, Lisa May 4, 2012) <br> GS:tested in U3 and found fixed, hence closed. (Singh, Ghanshyam Jun 12, 2012) |  | 35 | FINDING | 8373 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73128
29494 | FINDING | Default "High & Low" Scale of trend application window for Digital & Packed points are not changing. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br>1:-Open &quot;Ovation developer Studio&quot; window.<br>2:-Change the Trend Default High &amp; Low Scales at Drop level.<br>Default High Scale =-3<br>Default Low Scale = 3<br>(e.g.: Go to Drop182--&gt;Configuration--&gt;Trend--Press Trend Window Tab).<br>3:-Press Apply button &amp; then press OK button.<br>4:-Download Drop182 &amp; then reboot the system.<br>5:-Open trend window application.<br>6:-Add digital point then the Scale range is not taking Default High &amp; Low Values.<br><br>Same behavior is observed of Packed Point (Drop182--&gt;configuration--&gt;Trend--&gt;Trend Window Tab). (Prasad, Parmatma Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The new Trend application allows the default scales to be set as a user preference. The Dev Studio settings are no longer used. (Contento, James L. Sep 10, 2012)<br>Closed as per developer&quot;s comments above. (Prasad, Parmatma Sep 11, 2012) <br> |  | 35 | FINDING | 8374 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73130
29495 | FINDING | Highest & lowest define limit values are not showing in the trend application window for Digital & Packed points. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br>1:-Open Trend application window &amp; add a digital point (PP_350_D13_F_LD01.UNIT0@FE350).<br>1:-Open &quot;Trend Options&quot; window from Trend Application window.<br>2:-Select &quot;Scales&quot; Tab from Trend Options Window.<br>3:- Select Low &amp; High Values (Low=-1.5 &amp; High=1.5) on &quot;digital/packed point Scale Limits&quot;.<br>4:-Press OK Button.<br>5:-As shown in screen shot &quot;highest &amp; lowest scale limit missing.jpg&quot; ,Highest &amp; lowest limit are missing.<br>Same behavior are observed for DD,LP &amp; DP points as well. (Prasad, Parmatma Apr 20, 2012) (Contento, James L. Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This finding seems to be duplicate of 8378. (Bargaje Prashant Sep 10, 2012)<br>Closed as per developer&quot;s comments in Resolution of finding#8374. (Prasad, Parmatma Sep 11, 2012) <br> |  | 35 | FINDING | 8375 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73132
29496 | FINDING | Baseline Comparison shows wrong status for newly created baselines. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Right click on controller drop / Operating station drop.Add new baseline (e.g.Sa_1)<br>2.Create new Analog point e.g. SA_350_D203_LA_5 etc.and load the drop.<br>3.Now create new Baseline. e.g SA_2<br>3.Right click on controller drop / Operating station drop,click on compare baselines.Select two baselines. (e.g.SA_1 &amp; SA_2)<br>4. It shows Baseline Comparision window in which it shows status of SA_350_D203_LA_5 &quot;Deleted&quot;<br> actually this point is added.<br>5.Now if existing Digital points have been deleted e.g.SA_LD_1/SA_LD_2/SA_LD_3 Load the drop.<br>6.Right click on controller drop / Operating station drop.Add new baseline e.g. SA_3<br>7.Compare baselines SA_2 &amp; SA_3 it shows digital points SA_LD_1/SA_LD_2/SA_LD_3 status &quot;Added&quot;,where as in actual these points are deleted. <br>8.It has been observed that if copmarison is done with existing baseline i.e.Current Baseline then only status for added points shows &quot;Added&quot; and for deleted points status is &quot;Deleted&quot;.<br>But if comparision is done between two newly added baselines then it shows wrong status.<br>Please find the attached snapshots for reference.Testing is done on Drop13,Drop205,Drop203. (Athavale, Samiradixit Apr 20, 2012) |  |  |  | The comparison has been changed such that the results will always be presented based on a &quot;time&quot; comparison. In other words, the results will show the changes made to the &quot;earlier&quot; baseline selection. In addition, the order in which the baselines are presented to the user will be shown from the &quot;most recent to the oldest&quot;. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please note that the Status indication (e.g., Deleted versus Added) is dependent on the order in which you select the two baselines. If you first select SA_1 followed by SA_2, you see one set of results. If you perform a second comparison, this time selecting SA_2 first followed by SA_1, you should see a different set of results. The Add/Delete status, therefore is relative. <br>Please confirm this. (Swartz, Mark E. Apr 20, 2012)<br><br>If I select first SA_1 followed by SA_2 and perform Baseline Comaprision, then it shows status &quot; Deleted&quot; for the points which are added actually.Now If I change the order and select SA_2 first followed by SA_1and perform Baseline Comaprision then again it shows the same status &quot; Deleted&quot; for the points which are added actually.It is observed that status indication is not dependent on order selection of baseline.Please refer the attached snapshots.The baseline is created on 20APR12 and other is on 24APRIL.Meanwhile points are added,modified.Now while comparing baselines (Tested by both orders)it shows the status &quot;Deleted&quot; always for added points irrespective of order selection of baselines. (Athavale, Samiradixit Apr 24, 2012) <br> The comparison will be changed such that the results will always be presented based on a &quot;time&quot; comparison. In other words, the results will show the changes made to the &quot;earlier&quot; baseline selection. (Swartz, Mark E. Apr 24, 2012)<br><br>Baseline comparision is working based on &quot;time&quot;.Found fixed in 3.5.0 U2.Hence Finding is closed. (Athavale, Samiradixit May 10, 2012) |  | 35 | FINDING | 8376 |  | FINDING | [10 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73134
29497 | FINDING | Details Panel in Trend for LD & LP points does not show the actual high and low scale values | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Details Panel in Trend application, for Digital and Packed points does not show <br>the actual high and low scale values, in LOW SCALE and HIGH SCALE columns, <br>when the scale criteria is LIMITS or CUSTOM.<br><br>Steps to reproduce:<br>1. Add a digital or packed point to trend.<br>2. Change the scale to MyScale and set the criteria to LIMITS or CUSTOM.<br><br>The Details Panel shows the SET and RESET description instead of actual limits <br>or custom scale limits. (Benzvi, Mati Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed in 3.5.0_U2<br><br>For scale criteria of LIMITS, the low scale and high scale values in Details Panel should show a background with gradient colors.<br><br>For scale criteria of CUSTOM, the low scale and high scale values in Details Panel should show a background with solid color. (Bargaje Prashant May 3, 2012)<br>---<br>msb - 02-Jul-2012:<br>1. Trend - Digital - Trace Properties = MyScale<br> Scale Criteria = Costume, -1.5 to 1.5 <br> Panel = -1.5 to 1.5 (White on Red SOLID Background) <br>2. Trend - Digital - Trace Properties = MyScale<br> Scale Criteria = Limits, Trend Option Scale = -2.5 to 4.0 <br> Panel = -2.5 to 4.0 (White on Red GRADIANT Background) <br>3. Repeast with LP<br> Closed - OK in 3.5.0_U3 (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 8377 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | [7 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73136
29498 | FINDING | Trend of LP points does not take the Digital/Packed point default limits as set via Trend Options dialog | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Trend application, for Packed points does not take into consideration the Digital/Packed <br>point default limits set via Trend Options dialog.<br><br>Steps to reproduce:<br><br>1. Add a packed point to trend.<br>2. Change the scale to MyScale and set the criteria to LIMITS. (Benzvi, Mati Apr 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed in 3.5.0_U2.<br><br>For DIGITAL and PACKED points, scale criteria of LIMITS should result in graph with low scale and high scale specified via TREND OPTIONS dialog. (Bargaje Prashant May 3, 2012)<br>---<br>msb - 02-Jun-2012:<br> 1. Display: LP Point - Trend: Scale Limit = -1.5 to 1.5<br> 2. Trace Properties - Scale: MyScale<br> Trace Criteria: Limits [OK] -&gt; Display Scale = -1.5 to 1.5<br> 3. Trend Options - Scale - Digital/Packed Point Scal Limits &gt; low = -4, High = 3 [OK]<br> Tren display scale = -4 to 3<br> 4. Repeat for digital<br> OK - Finding Closed - (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 8378 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | [7 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73138
29499 | FINDING | CLN gives an error and crashes. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step 1)Opened CLN through Ovation utility.<br>Step 2)Enter Point to be searched. <br>Step 3)On searching point with (general/all), CLN correctly displays drop name and instances details of point used in sheet.<br>Step 4)But on clicking on any of the instances, CLN does not perform any task, and later gives an error. Kindly see attached CLN_error.jpg<br>Same steps performed on DBS crashes CLN. Kindly find CLN_crash on DBS.jpg (Sachan, Pallavi Apr 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. May 7, 2012)<br><br>Found Fixed. Hence Closed. (Sachan, Pallavi Jun 7, 2012) <br> |  | 35 | FINDING | 8379 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73140
29500 | FINDING | Consistency check doesnot flag inconsistent External Alarm configuration on all drops. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Consistency check doesnot flag inconsistent External Alarm configuration on all drops.<br>On 3.5.0 - EMILY network (DBS - 125), the Alarm Configuration is only configured on <br>the System Level with 2 Alarm collectors drop126 (OpSt) &amp; drop127 (Opst+VCH). <br>On the Network level, in the [External Alarm Collector Networks], drop126 is configured with 1 external network (FE221) while drop127 is configured with 2 networks (FE221,WALT).<br>If a Consistency check is run on the System or Network Levels, 3 errors are given:<br> [Alarm Collectors Scan Different Remote Networks], One for each drop (125, 126, 127).<br>Consistency check on drop126 show the same error for drop126.<br>However, Consistency check on both drop125 or 127 shows no errors.<br>If both 126 &amp; 127 were configured initially to scan 1 network (FE221) and the 2nd network (WALT) was added later only on drop 127, download of the inconsistent configuration is <br>allowed to drop 127 with no errors. <br>As a result, 126 &amp; 127 show only 1 remote network when 126 is Active, Remote alarms is timeout on drop127 when drop126 is rebooted or shout down (ie. 127 doesnot take control).<br>Drop127 see 2 networks only when drop126 is down while the the alarm is started on drop127. (Benzvi, Mati Apr 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The consistency check did not always flag inconsistent alarm collectors. The return value was inadvertently reset during the next consistency check. The operator stations that displayed the error had additional findings that were reported. The ones that did not report the error, had no other consisteny findings to report. (Augustine, Lisa Apr 23, 2012)<br>---<br>msb - Deleted (WALT) on drop127. Download was not allowed:<br> Error: Alarm Collectors Scan Fifferent Remote Networks. - OK (Benzvi, Mati Aug 19, 2012) <br> |  | 35 | FINDING | 8380 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73142
29501 | FINDING | OCR400s show Channel 1 as Unavailable when configured for Single Highway Connection. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400s 17/67 and 18/68 (WALT) are configured as Ovation Network Connection = Single. KM = 0x6 and K1 = 0x3 for both redundant OCRs. (Brown, Sean Apr 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed by Mark Zaremsky. (Pingree, Douglas K. Aug 7, 2012) <br> |  | 35 | FINDING | 8381 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73144
29504 | FINDING | Error occurs while selecting "Aharoni" font style in Ovation Point Review application. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Ovation Point Review application.<br>2.In Home tab select &quot;Aharoni&quot; (very first font style)font style.<br>3.Error occurs : Font &quot;&quot;Aharoni&quot; does not support style &quot;Regular&quot;<br>4.If click on Quit option Ovation Point Review application gets closed.<br>5.Please find the attached snapshot for reference. (Athavale, Samiradixit Apr 24, 2012) | none |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Some font combinations are invalid. Message box will be shown for invalid font selections. (Burgoon, Frank J. May 7, 2012)<br><br>As per resolution after selecting Aharoni font style in Ovation Point Review window, error message comes: &quot;Font Aharoni does not support style &quot;Regular&quot;&quot;Please find the attached snapshot for reference.Hence finding is closed. (Athavale, Samiradixit Jul 12, 2012) <br> |  | 35 | FINDING | 8384 |  | FINDING | [10 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73150
29505 | FINDING | Error occurs while selecting "Aharoni" font style in Trend application. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Trend application.<br>2.In Home tab select &quot;Aharoni&quot; (very first font style)font style.<br>3.Error occurs : Font &quot;&quot;Aharoni&quot; does not support style &quot;Regular&quot;<br>4.If click on Quit option Trend application gets closed.<br>5.Please find the attached snapshot for reference. (Athavale, Samiradixit Apr 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed in 3.5.0_U3<br><br>1) A message box will appear describing the error<br>2) The UI will still say &quot;Aharoni&quot; font (or any other font with limitations) so that User can make other valid selections (Bargaje Prashant May 7, 2012)<br><br>As per resolution after selecting Aharoni font style in Trend window, error message comes: &quot;Font Aharoni does not support style &quot;Regular&quot;&quot;Please find the attached snapshot for reference.Hence finding is closed. (Athavale, Samiradixit Jul 12, 2012) <br> |  | 35 | FINDING | 8385 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73152
29506 | FINDING | GBNT hangs while a Macro is called for 64bit-OS systems. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When a Macro is called in Graphic builder, the GBNT appplication gets hanged in 64bit-OS, Ovation stations.<br>Step1: Insert new GBNT.<br>Step2: Select Macro, opens GBNT:Macro Window.<br>Step3: Select Browse, opens GBNT: Macro Explorer Window.<br>This shows list of Macros existing in the system. <br>Step4: Click on any Macro to select, nothing happens, click again, hangs the application. <br>Above mentioned problem is seen for Win7 SP1 and WinServer2008 R2, both having 64bit-OS. While same operation is observed to be working fine for other 32bit-OS stations. <br>Kindly find attached files, GBNT_crash_Macro.jpg and GBNT_crash_Macro_ DBS.jpg. (Sachan, Pallavi Apr 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Need more info. We cannot duplicate this on our 64-bit systems(WinServer2008 R2 or Win7 SP1). Plus, we remote logged into your drop176 and cannot duplicate this .... Can you reproduce this ALL of the time, or just sometimes? (Johnson, Kathy Apr 25, 2012) <br> On further investigation of your system, there seems to be a file I/O or network issue on your drop231. We could only duplicate this problem on that drop. GBNT works fine on your WinServer2008 R2 drop and on drop232 (Windows 7, SP1). GBNT was not hanging, it was just taking a long time to update the MACRO dialogs after selecting a new macro (and we only got the &quot;GBNT not responding dialog&quot; if/when we attempted to close the macro dialogs while the update operation was still in progress). We also noticed that it took a long time to update the GBNT:BMP_IMAGE dialog after selecting bmps from the list. Bmp files tend to be very large. We noticed that if we attempted to open one of the macro bmp files on the data base server outside of GBNT (from a Windows explorer) dialog, it also took a long time. It also took a long time to open a large .txt file on the data base server in Notepad. Accessing large files on the database server from drop231 seems to take a very long time - hence we think you have a network problem... (Johnson, Kathy Apr 25, 2012)<br><br>PS: With reference to the steps followed in the mail chain (IEC &quot;Not Responding&quot; Issue - finding 8386), I conclude that the Finding reported was due to networking issue and not due to Macro use in GBNT. Hence Finding is Closed. (Sachan, Pallavi May 1, 2012) |  | 35 | FINDING | 8386 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73154
29507 | FINDING | Quality of Simulated point does not follow quality of Simulation point for LD/DD type points | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If the qualty of Simulation point is FAIR, the Simulated point will show it as GOOD.Other quality type e.g. BAD,GOOD are reported correctly. This behaviour is observed only for LD/DD points. (Lal, Ramesh Apr 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest. Tried this with both point types and was not able to recreate. (Perdeus, Matthew Dec 17, 2012)<br><br>12/19/2012: Retested by creating new LD/DD points. The problem could not be recreated, hence finding is closed. (Lal, Ramesh Dec 19, 2012) <br> |  | 35 | FINDING | 8387 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73156
29510 | FINDING | Online alarm printer doesn"t print Alarm type column | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I have configured online dot matrix printer on com1 port but it doesn&quot;t print Alarm alarm column. (Singh, Ghanshyam Apr 25, 2012) |  |  |  | The MMILibrary was not being properly initialized so the string resources could not be extracted. The call to retrieve the strings was failing so a blank was returned. This affects the AlarmPrinter.exe and the Historical Alarm Review. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The MMILibrary was not being properly initialized so the string resources could not be extracted. The call to retrieve the strings was failing so a blank was returned. (Augustine, Lisa Jun 8, 2012)<br><br>GS(7/18/2012)-tested in U4 and found fixed, hence closed. (Singh, Ghanshyam Jul 19, 2012) <br> |  | 35 | FINDING | 8390 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73162
29514 | FINDING | The "Details" window of trend display is not behaving correctly. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Some columns name of &quot;details&quot; window is not showing e.g. SV &amp; LV columns while the same can be seen on its print preview window. As shown in screen shot &quot;SV &amp; LV columns are not showing .jpg&quot;. As shown in screen shot &quot;SV &amp; LV columns are showing on print preview.jpg&quot; <br>2.The width of the details column is not changing.<br>3.The columns headings (e.g. point name, historian&quot;.etc) are not showing with the default view of details window.<br>As shown in screen shot &quot;Columns heading are not showing.jpg&quot;. (Prasad, Parmatma Apr 26, 2012) (Contento, James L. May 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Details Panel behaviour has been revised.<br><br>1) Double click on details panel grid will toggle the header bar.<br>2) When header bar is visible, the columns can be resized by the user.<br>3) By default when the application comes up, by design the header bar will be invisible.<br>4) The header bar will display icons for GRAPH visible column and SCALE visible column. Print preview will show abbreviations G and S respectively for the same.<br>5) When Trace value explore and compare explorer is activated/deactivated, the grid columns will be resized automatically for best fit.<br>6) When a new TGD file is opened and when points are added/deleted, the grid columns will be resized automatically for best fit.<br>7) A menu will appear upon right clicking the header bar. It has 4 options for best fit. These are same options as in Table view and summary view grid.<br>8) ELLIPSIS characters (...) should not appear for Details panel Grid header bar. (Bargaje Prashant May 3, 2012)<br>Retested in Ov3.5.0_U2 release,the issue has been resolved. (Prasad, Parmatma May 8, 2012) <br> |  | 35 | FINDING | 8394 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73170
29515 | FINDING | Error occurs while selecting "Aharoni" font style in Point Information application. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Point Information application.<br>2.In Home tab select &quot;Aharoni&quot; (very first font style)font style.<br>3.Error occurs : Font &quot;&quot;Aharoni&quot; does not support style &quot;Regular&quot;<br>4.If click on Quit option Point Information application gets closed.<br>5.Please find the attached snapshot for reference. (Athavale, Samiradixit Apr 27, 2012) | none |  |  | Attempt to set the font to Aharoni with a regular type face. A message box will be displayed with an error message. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Attempting to create the Aharoni font with regular type face generates a program exception. Application will now catch the exception and display an error message. Similar behavior by other fonts will also be handled. (Burgoon, Frank J. Apr 27, 2012)<br><br><br>As per resolution after selecting Aharoni font style in Point Information window, error message comes: &quot;Font Aharoni does not support style &quot;Regular&quot;&quot;Please find the attached snapshot for reference.Hence finding is closed. (Athavale, Samiradixit Jul 12, 2012) <br> |  | 35 | FINDING | 8395 |  | FINDING | [10 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73172
29516 | FINDING | Studio only saves files under Ovation\OvationBase when Save As is selected. | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If a user saves a file from within Studio (such as Search Results) by selecting Save As, the file will always be saved under Ovation\OvationBase. The window for selecting a drive and folder appears as expected, but the target location is not used. (Brown, Sean Apr 30, 2012)<br><br>Archived Engineering Audit data is also saved to Ovation\OvationBase. (Brown, Sean Jul 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8396 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73174
29517 | FINDING | An OCR400 does not communicate with a GE Mark V device. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The GE Mark V device can be pinged from the controller, but no other diagnostics can be performed (executing ge_tools causes a page fault). (Brown, Sean Apr 30, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Removed programatic pings from code thus resolving the issue. (Christy, Benjamin Nov 20, 2012)<br><br>SDR 19349 created (Ritenbaugh, David W. Jan 16, 2013) <br> |  | 35 | FINDING | 8397 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Zaremsky, Mark External MZCI | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73176
29518 | FINDING | Studio giving "OvPtApi: Key not found" error during controller configuration change and controller drop load | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | We have observed that whenever any configuration change is made in a controller drop (7/57 or 29/79) such as changing Sheet Set Size it consistently gives error &quot;OvPtApi: Key not found&quot;. Please refer the attached snapshot file OvPtApi-error.jpeg. This behavior is also observed during drop load operation but is not consistent. (Gupta, Chandresh May 1, 2012) |  |  |  | The remaining references to the Controller Services configuration object type have been removed from the Engineering Tools software. The affected area is in the software which generates controller configuration files (OvPtSysApi.dll and OvPtApi.dll). Testing should include modification of controller configurations (including the drop object itself). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This error does not originate from the controller. (Pingree, Douglas K. May 1, 2012)<br>This error is the result of the removal of the Controller Services configuration object from the Ovation 3.5.0 release. Unfortunately, this particular validation system probably already contains this configuration object in the database (though it is not shown in the hierarchy for Ovation 3.5.0). This issue was previously identified by persons in the controller group. The additional references to this type of configuration object have been removed from the Engineering Tools software and will be available in the next update. (Swartz, Mark E. May 1, 2012)<br><br>cg (05/24/12) - Finding retested in Ov3.5.0_U2. Now, the OvPtApi error is not appearing. Hence this finding is closed. (Gupta, Chandresh May 24, 2012) <br> |  | 35 | FINDING | 8398 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73178
29519 | FINDING | Virtual Controllers fails | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Virtual Controllers configuration is changed in 3.5.0.<br>1. Need a new procedure to configure Virtual Controllers (vxsim)<br>2. Virtual controllers fail shortly after startup with no error in Errlog. (Benzvi, Mati May 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1.) The issue with the missing directories will be corrected in the next update. These are to be created during the Ovation installation.<br>2.) A resource issue is being investigated on the virtual controller host. (Perdeus, Matthew May 2, 2012) <br> These VCs were moved to another machine and they functioned properly. It is our belief that the MMI had a problem unrelated to the VCs. Please close. (Pingree, Douglas K. Jun 26, 2012)<br>---<br>msb - OK in 3.5.0_U3 @ 02-Jul-12 (Benzvi, Mati Jul 2, 2012) |  | 35 | FINDING | 8399 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73180
29520 | FINDING | Accessing the Node Point IO Module field in Search can cause Studio to crash. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When using Search with Node Points, displaying the IO Module field or using the IO Module as a search parameter sometimes crashes Studio on the DBS (or crashes OvPtSvr from a non-DBS workstation).<br><br>The crashing was observed multiple times as follows:<br><br>EMILY: Does not crash, only 14/64 has RN points, some are Fieldbus<br>WALT: Searching only 14/64 does not crash, should be identical to 14/64 on EMILY<br>WALT: Searching RN points in all drops causes crash <br>WALT: Seaching RN points in 16/66 causes crash, some points are Fieldbus<br>WALT: Seaching RN points in 17/67 causes crash, some points are Fieldbus<br>WALT: Seaching RN points in 19/69 causes crash, some points are Fieldbus<br><br>IO Task and IO Access fields could be searched/displayed with RN points. The IO Module field could be searched/displayed with RM points. (Brown, Sean May 1, 2012)<br><br>Failed in U2 (problem occurs in the same manner). (Brown, Sean May 7, 2012) |  |  |  | The affected area is in the software responsible for creating/updating the text shown in the update window during search operations (or during the update of search results) and in the software which generates the displayed I/O Location field of Node points. The applicable binary is OvPtApi.dll. There are no other specific test recommendations other than to repeat the operations which led to initial detection of the problem (as described in this Finding). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This problem is not specific to the I/O Module of Node points, but could in fact occur in other search instances as well. The software which generates the text strings shown in the progress window was not utilizing static memory. This will be corrected in the next update. (Swartz, Mark E. May 1, 2012)<br>Another problem was found in the population of the I/O Module field of Node records assigned to Fieldbus Devices (or any other object whose name becomes part of the x.y.z io_location string). This error should also occur if those particular node records are Opened (as well as included in a Search). (Swartz, Mark E. May 7, 2012)<br><br>OK in U3; closing. (Brown, Sean Jun 8, 2012) <br> |  | 35 | FINDING | 8400 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73182
29521 | FINDING | OSR reports DLL errors (lsapiw32.dll) | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | The following error message is reported multiple times in OSR:<br><br>ErrorA exception was caught while retrieving license information: Message: Unable to load DLL lsapiw32.dll: The specified module could not be found. (Exception from HRESULT: 0x8007007E) (Brown, Sean May 1, 2012)<br><br>Failed; the same errors appear in U3. (Brown, Sean Jun 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Encountered due to transition in 64bit platform. Changed Platform setting in VS to x86 since license DLL is still using 32 bit version. For re-test on next release. (Quintos, Ronaldo M. May 11, 2012) <br> |  | 35 | FINDING | 8401 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Quintos, Ronaldo PROCESS PWS MNL | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73185
29523 | FINDING | While configuring VxSim Controller,download operation is not getting files from proper directory. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were performed:<br><br>1. As per procedure While configuring VxSim Controller, download operation is performed.<br><br>2.Observed that the download operation is not getting &quot;vxsimCtlr_Unlinked.o&quot; file from proper directory.<br><br>3.After copying the &quot;vxsimCtlr_Unlinked.o&quot; file from the following location C:\Ovation\Embedded\Controller\vxsim\controller to C:\Ovation\OvationVirtual\vdrop77\ata0\controller,VxSim starts working fine. (Jindal, Deepak May 2, 2012)<br><br><br>While configuring VxSim Controller in developer studio , Controller type can be selected as &quot;Controller&quot; or &quot;Virtual controller&quot;<br>1.When Controller type is selected as &quot;Controller &quot; then download operation is sending &quot;OCR400ctlr_unlinked.o&quot; file in place of &quot;vxsimCtlr_Unlinked.o&quot; file due to which at the time of clear operation ,&quot; VxSim controller drop is not available&quot; error message is coming.<br>2.When Controller type is selected as &quot;Virtual controller&quot;, then download operation is sending appropriate file and is working fine.<br>Earlier finding has been raised for first scenario,So It would be better to have some checking so that VxSim controller will be configured as &quot;Virtual controller&quot; only. (Jindal, Deepak May 11, 2012) (Pingree, Douglas K. May 15, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot recreate. Download function sent file to and from proper location and virtual controller started properly without any manual intervention. (Perdeus, Matthew May 2, 2012) <br> This was user configuration error. Way it works. (Boehmer, Robert W. Oct 29, 2012)<br><br>Checked and verified on Ovation3.5.0 build and issue is resolved. (Jindal, Deepak Nov 1, 2012) |  | 35 | FINDING | 8403 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW |  |  | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 73189
29524 | FINDING | When configuring the VxSim controller, registery settings are not getting updated. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While configuring the VxSim controller, the registry settings at the following location &quot;HKEY_LOCAL_MACHINE\SOFTWARE\Wind River Systems\Wind River VxWorks Simulator Network Daemon&quot; are not getting updated. These values should get updated automatically on running &quot;WR-VxSim.reg&quot; file located in &quot;C:\Ovation\OvationVirtual&quot; directory.<br><br>If manualy update the following two fields<br>1. &quot;CONFIG_FILE&quot; field from &quot; &quot; TO &quot;C:\\Ovation\\OvationVirtual\\vxsimnetd.conf&quot; 2. &quot;SHELL_SERVER_PORT&quot; field from &quot;dword:0000ffff &quot; TO &quot;dword:00001e61&quot; , <br>the VxSim starts working fine. (Jindal, Deepak May 2, 2012) |  |  |  | Remove config file name from the registry entry &quot;HKEY_LOCAL_MACHINE\SOFTWARE\Wind River Systems\Wind River VxWorks Simulator Network Daemon&quot; , install registry as in instructions and verify that the entry is returned. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected file that installs registry entry. (Perdeus, Matthew May 2, 2012) <br> Checked and verified on Ovation3.5.0_U8 build and issue is resolved. (Jindal, Deepak Sep 25, 2012) |  | 35 | FINDING | 8404 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW |  |  | Implementation | 3.5.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 73191
29525 | FINDING | Signal Diagram Viewer window crashes in a particular scenario after Invalid value Entry | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were performed:<br>1. Created a Control Sheet containing SETPOINT, PID, MASTATION &amp; LEADLAG algorithms.<br>2. Saved, Compiled &amp; Loaded the control sheet in drop13.<br>3. When we open Signal Diagram Viewer window, by default the &quot;Algorithm Control&quot; window appears at the right pane alongwith &quot;Properties Summary&quot; window. <br>4. Opened the created control sheet in Signal Diagram &amp; made changes from this &quot;Algorithm Control&quot; window for MASTATION/SETPOINT algorithms. This works fine.<br>5. Now Drag the &quot;Algorithm Control&quot; window from right pane &amp; drop it to the bottom of Signal Diagram. So this window will align with &quot;Event Log, Algorithm summary &amp; Function Summary&quot; windows.<br>6. Select MASTATION algorithm. In &quot;Algorithm Control&quot; window click on &quot;Enter&quot; or &quot;Slew&quot; button without entering any values in the entry field. Upon doing so an error message generates in the Event Log &quot;Invalid Entry: Enter valid numerical value&quot;.<br>7. At this stage select SETPOINT algorithm. In &quot;Algorithm Control&quot; window click on either &quot;Increment, Decrement, Enter or Slew&quot; button. <br>Doing so the Signal Diagram Viewer window crashes.<br>Please refer the attached snapshot file Signal_Diagram_crash.jpeg. (Gupta, Chandresh May 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. May 7, 2012)<br><br>cg (06/07/12) - Finding retested in Ov3.5.0_U3. Still Signal Diagram is crashing when above mentioned steps are done. Hence marking this finding as Open (Failed Retest) with Action field changing to DRR. (Gupta, Chandresh Jun 7, 2012)<br><br>Fixed - (Hutchison, Steven B. Jun 7, 2012)<br><br>cg (07/20/12) - Finding retested in U4. Now, Signal Diagram is not crashing if above mentioned steps are followed. Hence this finding is closed.<br><br>However, the INC/DEC buttons for Setpoint, MAStation are not working properly. Writing seperate finding for it. (Gupta, Chandresh Jul 20, 2012) <br> |  | 35 | FINDING | 8405 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73193
29526 | FINDING | SIS functionality is not working on the controller |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When SIS is configured on the controller, SIS functionality is not working. One of the SIS tasks (sisio) is using all of CPU time and other tasks with priorities below sisio stop working. <br>Some of preprocesor defines required to properly build sisio module were not imported from makefile to project file. (Czak, Jakub May 2, 2012) |  |  |  | Adding SIS I/O device shouldn&quot;t fail controller. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Preprocesor defines were added to project properties. (Czak, Jakub May 28, 2012) <br> |  | 35 | FINDING | 8406 |  | FINDING | [10 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73195
29527 | FINDING | Advanced Edit is not available for SIS algorithms. | Hutchison, Steven EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | It is not possible to open Advanced Edit window for SIS algorithms from Control Builder. Option is not visible in popup menu that is displayed after right click on the algorithm. (Czak, Jakub May 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. May 8, 2012) <br> |  | 35 | FINDING | 8407 |  | FINDING | [10 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73197
29528 | FINDING | Error occurs while selecting "Aharoni" font style in System Viewer application. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open System Viewer application.<br>2.In Home tab select &quot;Aharoni&quot; (very first font style)font style.<br>3.Error occurs : Font &quot;&quot;Aharoni&quot; does not support style &quot;Regular&quot;<br>4.If click on Quit option Trend application gets closed.<br>5.Please find the attached snapshot for reference. (Athavale, Samiradixit May 2, 2012) |  |  |  | If this font is selected, an information message box will be displayed. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A message box will be displayed when the font is selected.<br>It will state that the fond is not supported. (Wozniak, Diane M. Aug 27, 2012)<br><br>As per resolution after selecting Aharoni font style in System Viewer window, error message comes: &quot;Font Aharoni does not support style &quot;Regular&quot;.However it accepts &quot;Aharoni&quot; bold and italic style.Hence Finding is closed. (Athavale, Samiradixit Aug 28, 2012) <br> |  | 35 | FINDING | 8408 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73199
29531 | FINDING | cbViewer crashes inconsistently on 64-bit OS drop232. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | As per 3.5_ST_BASIC_FUNCTIONS_SVTP_rev1.M_PS, 5.4.3 Test: Using Dual Opcons : open 4 Signal Diagrams on each monitor. Display 4 different Ladder Sheets on one monitor and 4 different Control Sheets on the other monitor. <br>It is observed that while performing the above tests, cbViewer crashes inconsistently on 64-bit OS drop232. <br>Scenario 1: when 4th Control sheet is opened, when already 4 ladder sheets and 3 control sheets are opened.<br>Scenario 2: When 4 control sheets are opened and editing one of the 4 ladder sheets.<br>Scenario 3: When 4 control sheets are opened and editing one of the 4 ladder sheets.<br>Kindly find the attached cbViewer_crash_03may.jpeg (Sachan, Pallavi May 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a duplicate of SDR 17864.<br>- (Hutchison, Steven B. Sep 4, 2012)<br><br>Finding Closed as per &quot;NAR&quot; by developer. (Sachan, Pallavi Sep 14, 2012) <br> |  | 35 | FINDING | 8411 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73205
29532 | FINDING | Change of font size for [Aharoni]font, does not take effect | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps are performed:<br>1.Open Ovation Historical review - Select [Operator event] tab - Select [Aharoni] font - Set the filter - Click start button. Events appeared in the list. <br>2.Change the font size, it it does not take effect. Same behaviour is observed for other tabs(Point/SOE/Common/Ascii/Alarm). (Pandey, Vijay May 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. Next build should have the fix. (Matreja Shyam May 7, 2012)<br>VP- Retested in U2, found not fixed. Finding state change to failed retest. (Pandey, Vijay May 29, 2012)<br>smatreja: Check in U3 because U2 was build on May 4, 2012 and the fix was done on May 7. So it should be in U3. (Matreja Shyam May 29, 2012)<br>VP: Retested with U3. Found not fixed. Upon selecting [Ahroni] font, error appeared. For reference screenshot &quot;hist rev_u3_error.jpg&quot; is attached.Hence state is still in Open (Failed Retest). (Pandey, Vijay Jun 7, 2012)<br>smatreja: This dialog box was added to inform the user that this is not a valid selection. This font should be used with Bold (button) selected. Please compare it with other application such as Point Info and Point Review and check if it behaves same or not. (Matreja Shyam Jun 7, 2012)<br>VP- As per devloper explanation, finding retested and found fixed. Hence, finding is closed. (Pandey, Vijay Jun 11, 2012) <br> |  | 35 | FINDING | 8412 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73207
29533 | FINDING | [Services] option is not available in Developer Studio Controller Configuration hierarchy | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Developer Studio for Controller drops, under Configuration the [Services] option is not available. So we are unable to ENABLE/DISABLE the Communication Services of Controller drops. (Gupta, Chandresh May 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works as designed for Ovation 3.5. Communications Services has been removed from the Ovation database. Please reference SRF 1379. (Swartz, Mark E. May 4, 2012)<br><br>cg (05/09/12) - Based on developers comments this finding is closed. (Gupta, Chandresh May 8, 2012) <br> |  | 35 | FINDING | 8413 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73209
29534 | FINDING | Multiple customization window appear on a single tab window. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Historical review application<br>2.Right click on coloumn ribbon - select coloumn chooser - Customization window gets appeared - Remove some coloumn from window, removed coloumns appeared in customization window. <br>3.Switch to [Operator event] tab, customization window that appeared on [Point]tab still available. Right click on coloumn ribbon - select coloumn chooser - another Customization window gets appeared.<br>If we perform above steps on all tabs, six customization window appeared on a single tab window. For reference [OHR-CUSTOMIZATION.jpg] screenshot is attached. It makes confusion for user. (Pandey, Vijay May 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | VP- As per devloper comments, finding is closed. (Pandey, Vijay May 29, 2012) <br> |  | 35 | FINDING | 8414 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73211
29535 | FINDING | Network failover is not occurring on an OCR400. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400 Controller 35/85 is configured on the WALT network. Failover between the FEI ports on 35 is not taking place, which affects communication with 35. (Brown, Sean May 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The switch port was faulty. Moving the cable to another port corrected the problem. (Pingree, Douglas K. May 7, 2012) <br> |  | 35 | FINDING | 8415 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Zaremsky, Mark External MZCI | [7 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73213
29536 | FINDING | Ovation Historical Review button icon is not clearly visible on 32-bit machine. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Ovation Historical Review button icon is not clearly visible on 32-bit machine. It is clearly visible on 64 bit machine. (Pandey, Vijay May 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Please retest in next release. (Matreja Shyam May 17, 2012)<br>VP: Retested with U3. Found fixed, hence finding is closed. (Pandey, Vijay Jun 7, 2012) <br> |  | 35 | FINDING | 8416 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73215
29537 | FINDING | Ancillary value (Data) can not be modified from Point Information Window.(Ref of SRF1523) | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Ancillary labels (BOILER 1,BOILER 2,BOILER 3)are present in analog points.e.g. SA_350_D13_LA_1<br>2.Open PI Window.Open Ancillary tab.<br>3.Ancillary labels are present on left side as Parameters.If user click on edit button in value tab infront of parameter(BOILER 1),user can write any value in new value window.<br>4.Now if user want to modify the value,click on edit button,again blank new value window will be opened.so that already present value can not be modified.<br>Value can not be added,can not be chnaged.No back space option.Value only get overwritten.<br>5.e.g. &quot;Analog point&quot; is given in value, now user wants to add info LA_1 ahead of &quot;Analog point&quot;,then user has to write &quot;Analog point_LA_1&quot; whole thing again.<br>If user wants to delete &quot;Point&quot; from &quot;Analog Point&quot; then again user has to write only &quot;Analog&quot; so it will get overwrite.<br>6.Please find the attached snapshot. (Athavale, Samiradixit May 7, 2012) | none |  |  | Edit ancillary data and see that edit field is pre-populated with current value | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The window comes to edit Ancillary field, allows max.80bytes (characters in actual).If user writes up to 70 characters in ancillary field and afterwards user wants to edit last/first 20 characters, then he has to type all 70 characters again and then he can do required edition. It is tedious job to type all 70 characters, only for edition/ modification. From user point of view it is easier if click to edit then window should come with ancillary field data which is typed by user, and it is in editable form, so that whenever user wants to edit/modify the ancillary data he can edit, as mentioned in SRF 1523 that Ancillary field is editable from PI window in runtime. As of now window comes blank. (Athavale, Samiradixit Jun 1, 2012)<br><br>Editing ancillary values will now populate the edit field. (Burgoon, Frank J. Jun 1, 2012)<br><br>Ancillary field data which is typed by user is in editable form and pre-populating in PI window Editing of ancillary values is possible from PI window.Hence Finding is closed. (Athavale, Samiradixit Jul 18, 2012) <br> |  | 35 | FINDING | 8417 |  | FINDING | [10 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73217
29538 | FINDING | GE Mark files and Holding Registers are modified in controller before Load Preview occurs. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | (MES) Load Preview entries are displayed after the loading of GE Mark files and Holding Registers has already been performed. These changes will also appear in the next Load Preview if the current Load is Aborted (since the MS field of the target OCR will not have been updated). (Brown, Sean May 7, 2012) |  |  |  | The affected area is in the software responsible for performing the Load operation. Tests should include the verification that an load operation aborted during the viewing of the Load Preview window will NOT result in any modified holding registers in the target controller or in the inadvertant download of a GE Mark V/VI data file. The applicable binary is OvPtSysApi.dll. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Load operation software will be reorganized so that data files are implicitly downloaded after the display of the Load Preview window. Note that this applies to data files which are implicitly downloaded prior to the loading of Ovation points (e.g., GE Mark V/VI data files).<br>In addition, the Load operation software will also be reorganized so that the actual loading of modified Holding Registers will also be performed after the display of the Load Preview window.<br>Note that since this issue is applicable to the Load Preview functionality, this is not applicable to earlier releases. (Swartz, Mark E. May 7, 2012)<br><br>OK in U3; closing.<br>Used HREGInfo to very Holding Register value.<br>Viewed /ata0/wdpf/dpu/data to verify GETT.DAT timestamp.<br>Verified Abort/Continue behavior using Holding Register, GE Mark V point, GE Mark VI/Ve point, Control Sheets and multiple point types.<br>Verified behavior for incremental and full (cleared controller) drop loads. (Brown, Sean Jun 8, 2012) <br> |  | 35 | FINDING | 8418 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73219
29540 | FINDING | On Ovation 3.5.0, .epm files could not be generated by OSR. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | At Save Collected Data Window, the OSR doesnot generate SysRegData.epm files and gives error.<br>Kindly find the SaveCollectedData_error.jpeg (Sachan, Pallavi May 8, 2012)<br><br>I need access to Ovation DB server. Kindly send the remote desktop details. (Quintos, Ronaldo M. May 9, 2012)<br><br>Hi Ron, For Ovation 3.5.0 DB server is drop176 (DBS+PDC &quot; Net#8). <br>Kindly find the remote login details in &quot;Primary_gateway_new_drop163_login_steps.doc&quot; file under : \\10.209.228.177\Ohara\ProductDevelopment\ValidationTechnicalSupport\IEC\IEC Val Drops remote login procedures\ (Sachan, Pallavi May 11, 2012)<br><br>May I know if this is still an open issue? (Quintos, Ronaldo M. Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | No, this issue was reported and fixed long back. You can just change the Action field to LIB, so that I can close the finding as issue FIXED. (Sachan, Pallavi Nov 1, 2012)<br><br>Found fixed. Hence Closed. (Sachan, Pallavi Nov 15, 2012) <br> |  | 35 | FINDING | 8420 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73223
29541 | FINDING | On Ovation 3.5.0, Ovation System Preferences shows Ethernet Netwrok as NO. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | While the network (NET#8 on Ovation 3.5.0, Validation Lab) is connected on FE, the OSR report shows Ethernet Network as NO under Ovation System Preferences. (Sachan, Pallavi May 8, 2012)<br><br>I need access to the remote machine. Kindly send the login details. (Quintos, Ronaldo M. May 11, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation System Registration (OSR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Benig, Ronaldo B.</p> <p><strong>Notify List:</strong> Quintos, Ronaldo M. Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-05-08T01:26:47-04:00</p> <p><strong>Modified Date:</strong> 2012-05-11T07:51:41-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8421 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73224
29542 | FINDING | OSR Report doesnot identify the Ovation Software revision for 64-bit OS machines. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | OSR Report doesnot identify the Ovation Software revision for (Win7 &amp; WS2008 R2)64-bit OS machines. <br>For 32-bits machines, Software Revision is shown as 3.5.0, while for 64-bit machines, Software Revision is shown as (blank). (Sachan, Pallavi May 8, 2012)<br><br>Dependent on Finding 8401 issue. (Quintos, Ronaldo M. May 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | See resolution for Finding 8401. For testing on next release. (Quintos, Ronaldo M. May 11, 2012)<br><br>Problem is still observed to be same in U3. Hence Failed Retest. (Sachan, Pallavi Jun 7, 2012) <br> |  | 35 | FINDING | 8422 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73227
29543 | FINDING | OSR Reports error for all the working controllers. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | OSR Report shows same error for all the controllers on the network. The error on the report appears as follows:<br>&quot;Errors: A problem was encountered retrieving information from DROP7 <br> A problem was encountered retrieving information from DROP57&quot; <br>Logs observed in SysRegLog.txt file is as follows: <br>&quot;Failed to retrieve Ovation version information from the local machine.<br>Error fetching information from controller: DROP7/57 (Sachan, Pallavi May 8, 2012)<br><br>Dependent on Finding 8401 issue. (Quintos, Ronaldo M. May 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | See resolution for Finding 8401. For testing on next release. (Quintos, Ronaldo M. May 11, 2012)<br><br>Problem is still observed to be same in U3. Hence Failed Retest. (Sachan, Pallavi Jun 7, 2012) <br> |  | 35 | FINDING | 8423 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73230
29544 | FINDING | The LP (packed point) & DP (Deluxe packed point) point"s value did not change on Historian Trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:<br> 1. Open Trend application window.<br> 2. Add LP &amp; DP points on Trend window.<br> 3. Change the LP point value. (E.g. 0 to 1 &amp; 1 to 0)<br> 4. In Live Trend, the value becomes change from 0 to 1, but in Historian Trend LP point value does not change. As shown on attached Screen shots of Live (PP_Live.jpg) &amp; Historian (PP_Historian.jpg) Trend.<br> Same behavior is also observed on DP point. (Prasad, Parmatma May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1) Looks like the OPH scanner was down and therefore historian drop245 did not have data for part of duration specified for Historical Trend. Therefore that part of TREND shows as missing. This was verified using OvhConsole application on drop245. Historical Reviews (Point and SOE) also may be used to verify absense of data. SOE review will indicate TIME GAP START and END.<br><br>2) When the upper-most (BIT-15, first bit being BIT-0) invalidity bit was set for packed point, there was a bug that caused incorrect value being displayed for a packed point in Historical Trend. This problem is fixed. (Bargaje Prashant May 11, 2012) (Bargaje Prashant May 13, 2012)<br>Retested in Ov3.5.0_U3 release,the issue has been resolved. (Prasad, Parmatma Jun 8, 2012) <br> |  | 35 | FINDING | 8424 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73232
29545 | FINDING | SDR#18497:"Locked Down" policies do not permit certain OPH applications from running as expected is failed. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | According to resolution of this SDR:<br>The items &quot;ovhdiag.exe&quot; and &quot;start_ovh_ui.bat&quot; will be added to the list of standard items/exceptions which are permitted to run for the &quot;Operator (locked down)&quot; and &quot;Engineer (locked down)&quot; policies.<br>But it is found that instead of ovhdiag.exe it is ophdiag.exe and instead of start_ovh_ui.bat it is start_oph_ui.bat.(refer snapshot) (Kumar, Shailendra May 8, 2012) |  |  |  | The affected area is in the template files utilized by the Ovation Security Manager and updated during the installation or update of the Ovation software. Re-released to library 7/11/2012. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The original specification of ophDiag.exe and start_oph_ui.bat was incorrect. This typographical error will be corrected in the template used by the Ovation Security Manager. (Swartz, Mark E. May 8, 2012)<br><br>Checked in U3,it is solved for &quot;Operator (locked down)&quot; but for &quot;Engineer (locked down)&quot; policies it is still not solved, hence Open(Failed Retest). (Kumar, Shailendra Jun 12, 2012)<br><br>As noticed, there were other typographical errors which still remained in the template. These additional entries have also now been corrected. (Swartz, Mark E. Jul 11, 2012)<br><br>SK:checked in U4, hence passed. (Kumar, Shailendra Jul 27, 2012) <br> |  | 35 | FINDING | 8425 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73234
29546 | FINDING | Transfer Algorithm doesnt have option to select and delete the pin individually. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In transfer Algorithm, there is no option of the selection or deletion of pins whereas this was working till Ov 3.4.0.<br>At the time of selection of pin, it is selecting the whole Transfer Algorithm.<br>But the option of pin selection and deletion is possible with other Algorithm in Ov 3.5.0. (Katiyar, Akanksha May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it works. The transfer algorithm&quot;s selector pin falls within the bounding rectangle of the symbol. Selection within the bounding rectangle select the entire algorithm. To delete this pin use the object browser. (Hutchison, Steven B. May 8, 2012) <br> AKKK_06/01/2012<br><br>Thanks for the guidence.I am closing this finding as it is working in the same manners as described by you in the Resolution. (Katiyar, Akanksha Jun 1, 2012) |  | 35 | FINDING | 8426 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73236
29548 | FINDING | Failed to launch "Help" error message displayed on W7 64 bit OS | Long, Edward M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In the &quot;Help&quot; menu, select &quot;Help Topics&quot; option, an error message is displayed &quot;failed to launch help.<br>On other OS levels the menu button is working fine.<br>This probelm has been encountered on W7 SP1 64 bit OS. (Khanna, Anant May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8428 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73240
29549 | FINDING | In Ovation Point Browser filter file for record types is not getting saved | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation Point Browser filter file for record types is not getting saved.If again load filter with record type, it selects all record type irrespective of selection of record type.<br>(if ovation point browser initatied from the PI:close both ovation point browser and PI then again open the both and load filter ).PFA for clarity (Singh, Ghanshyam May 8, 2012) | none |  |  | Saving and loading record type filters. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected a bug in saving and loading record type filters. (Burgoon, Frank J. May 10, 2012)<br><br>GS:tested in U3 and found fixed, hence closed. (Singh, Ghanshyam Jun 12, 2012) <br> |  | 35 | FINDING | 8429 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73242
29550 | FINDING | points matching search criteria is getting blank untill strech it horizontally | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation Point Browser if drops details are very long ,then points matching search criteria is getting blank untill strech it horizontally.<br>If retain the less drop details then still it shows blank.(Good way to recreating select other multinetwork having one short drop details and one having long drop details).<br>PFA for clarity. (Singh, Ghanshyam May 8, 2012) | none |  |  | Put enough information in filter display area to exceed the minimum window width. The information will still be visible but the end will be cut off. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The first picture attached shows a browser window that is still generating the list of points. At this point the details are not shown. It is not until the entire list of points is generated that the browser windows fills in the details. Could you give further details of the complaint? (Burgoon, Frank J. May 11, 2012)<br>GS(6/6/2012):In the 2nd picture all points are generated but points matching search criteria still bank.It will remain blank utill we strech the window horizonatlly. (Singh, Ghanshyam Jun 6, 2012) <br> Changes made to correct this problem. (Burgoon, Frank J. Jun 12, 2012)<br><br>GS(7/18/2012)-Tested in U4 and found fixed, hence closed. (Singh, Ghanshyam Jul 19, 2012) |  | 35 | FINDING | 8430 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73244
29551 | FINDING | Once filtered file is loaded in ovation point browser then filter name should on the top window | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Once filtered file is loaded in ovation point browser then filter name should on the top window .It will help to idetify the fillter file and it will reduse the confusion to the user . (Singh, Ghanshyam May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Current filters are displayed in the UI. (Burgoon, Frank J. May 10, 2012)<br><br>GS(6/1/2011):My concern on the saved filter as name then use in future but after selecting a filter we don&quot;t have any display for current filter.e.g. if you saved filter in alarm,it comes with filter name on the top the browser. (Singh, Ghanshyam Jun 1, 2012) (Singh, Ghanshyam Jun 1, 2012)<br><br>GS(18/7/2012)-As developer and Nooch&quot;s comment, finding closed. (Singh, Ghanshyam Jul 18, 2012) <br> |  | 35 | FINDING | 8431 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73246
29552 | FINDING | OHI discrption is incomplet. | McMaster, James External Artech | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | There is &quot;OHI help&quot; is present as discrption which is incomplet.As discrption is present for other driver/services.PFA for clarity. (Singh, Ghanshyam May 8, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Data Highway Controller (DHC)</p> <p><strong>Subproduct:</strong> Ovation Highway Interface (OHI)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> McMaster, James</p> <p><strong>Notify List:</strong> McMaster, James Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2012-05-08T07:16:25-04:00</p> <p><strong>Modified Date:</strong> 2012-06-06T00:28:23-04:00</p> | 0 |  | Ovation for Windows/General/Software | No plans to update OHI driver for this. If OHI changes are required for other reasons<br>we may revist this finding (McMaster, James May 18, 2012)<br><br>GS(6/1/2011):If you feel , you may revist the issue so it could be better to make this issue as SDR or MNR. (Singh, Ghanshyam Jun 1, 2012) <br> |  | 35 | FINDING | 8432 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [10 empty] | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73247
29553 | FINDING | Signal diagram and summary diagram are disable in point menu once going through trends | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Signal diagram and summary diagram are disable in point menu once going through trends.Point is configured for signal diagram and summary diagram which verifed with point menu through the PI.PFA for clarity. (Singh, Ghanshyam May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Should appear fixed in 3.5.0_U3 (Bargaje Prashant May 16, 2012)<br><br>GS:tested in U3 and found fixed, hence closed. (Singh, Ghanshyam Jun 12, 2012) <br> |  | 35 | FINDING | 8433 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73249
29554 | FINDING | signal diagram menu opens graphics window with error once initiated thought point menu of annuntiation. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | signal diagram menu opens graphics window with error once initiated thought point menu of annuntiation.PFA for clarity (Singh, Ghanshyam May 8, 2012) |  |  |  | The Alarm Annunciation Window has been updated to initiate the cbViewer (rather than the graphics window) when the signal diagram point menu option is selected. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The software will be updated to initiate the cbViewer. (Augustine, Lisa May 8, 2012)<br><br>GS:tested in U3 and found fixed, hence closed. (Singh, Ghanshyam Jun 12, 2012) <br> |  | 35 | FINDING | 8434 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73251
29555 | FINDING | Ancillary data can not be edited from PI for newly created Global Role.(Ref SRF 1523) | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | (with Ref of SRF 1523 tEST5.2.4 case 2)<br>1.New Global role is created in Ovation Security Manager.e.g.Validator<br>2.Right click on Role Validator.role properties&gt; Operator&gt; Allow Modification of Ancillary Data is enabaled for Local &amp; Remote.<br>3.Assigned Validator Role to User:Val_V (Policy is Unrestricted User)<br>4.Log in by User Val_V.Open Ovation Session Manager.It shows Modify Ancillary Data is enabled.<br>5.Open PI window.Open analog point.Click on Ancillay tab.Value edit button is not appearing.<br>New value window to edit ancillary field is also not appearing.Hence Ancillary data can not be edited from PI for newly created Global Role Validator.<br>6.Please find the attached snapshot. (Athavale, Samiradixit May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please check to see if point security groups are enabled on the role and the point. Point security groups are not enabled on the roles by default. (Burgoon, Frank J. May 9, 2012)<br><br>1.For any newly created Global role, open Point Security Groups.Under this admin tab is enabled for Local &amp; Remote console.<br>2.After this Ancillary data can be edited from PI for any newly created Global role. <br>3.To edit Ancillary data,point security group of role must be enabled,this point is not mentioned in SRF1523.This point needs to be added in SRF1523. (Athavale, Samiradixit May 10, 2012) <br> |  | 35 | FINDING | 8435 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73253
29558 | FINDING | drop13 controller FAILING consistently with Coordinator Subsystem Error : Coordinator PCL Error. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Action Performed:<br><br>1. Some control sheets are made in controller drop13 (including distibutor algo) and loaded the controller. drop13 went to fail mode showing the error &quot;Algorithm Library: Local memory size error&quot;.<br>2. Suspecting that Distributor algo might be the culprit, removed the control sheets created and cleared the controller. After that controller came to control mode &amp; got loaded successfully.<br>3. To confirm distributor algo issue, control sheet with this algo was created &amp; controller loaded. Again this time Controller failed with the same error message. Now changed the shared memory size from 5 MB to 6 MB. Downloaded the controller and reboot. However, the controller came up in failed mode with error message Coordinator Subsystem Error : Coordinator PCL Error.<br><br>4. Return back the Shared Memory size from 6 to 5 and downloaded the controller, reboot, still controller got failed.<br><br>5. Controller flash is cleared, then also controller is in failed mode after download and clear.<br><br>In brief, now drop13 is not in working condition &amp; is lying in failed mode.<br><br>Please find the text file drop13_FAIL.txt containing printErrorBuffer details, memShow details &amp; max points details. (Joshi, Parmesh May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | We cannot reproduce this here. We have tried using the same configuration files and database export, but cannot reproduce. Validation has temporarily switched the configuration to 6000 points and this allows the controller to come up. (Pingree, Douglas K. May 15, 2012) <br> In this case the iodata file appears to be corrupt. The final two numbers indicate the version and subversion in the iodata file. They should be very small (example: 5, 0). Perform a clear to get rid of the corrupt iodata file. If problems persist then I recommend replacing the flash disk.<br>We have also applied a Vxworks patch that corrects issues with file corruption. Please retry this with the latest update. (Pingree, Douglas K. May 31, 2012)<br><br>PJ, 12th June 2012: changed drop13 point limit setting from 16000 to 32000. Observed controller behaviour for 3 days by performing functions in the controller like Load, Clear, Download, Creating points, Control sheets, harware IO module assignment etc.. Controller is working fine now with no faliure. hence closed. (Joshi, Parmesh Jun 12, 2012)<br><br>PJ,19July-12: Observed the same problem reoccur with 3.5.0_U4 for controller drop13.<br>When the point limit is changed to 32000 ,the controller drop13 is going to failed mode permanently after download &amp; Clear. However, When switching back to 16000 point capacity and download &amp; Clear, the controller is coming back to normal mode.<br>Please find attached the error log details named &quot;drop13_01_FAIL_071812.txt&quot;.<br>Please find the remote login details of drop 176. (Joshi, Parmesh Jul 19, 2012)<br><br>PJ:26th July 2012: As per developer comments on mail sent on July 24 2012, The controller has run out of memory. this is because using 128 mb RAM for OCR400 G01 controller. The controller (drop13)need to decrease capacity or upgrade to a G02 OCR400. <br>Since this has different problem, not linked with the finding (8438) issue, hence closed. (Joshi, Parmesh Jul 26, 2012) |  | 35 | FINDING | 8438 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73259
29559 | FINDING | Ancillary data can not be edited from PI for Supervisor,Engineer(DB,Graphics)Global Roles.(Ref SRF1523 Case1) | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.New user Val_E is created in Ovation Security Manager.Policy assigned is Unrestricted User.Role is assigned as &quot;Supervisior&quot;,which is bydefault Global Role as per SRF 1523.<br><br>2.For &quot;Supervisior&quot; role properties&gt; Operator&gt; Allow Modification of Ancillary Data isenabaled.<br><br>3. Loged in by user Val_E Open PI window.Open Ancillary tab.Edit button does not Appear.NewValue window does not appear.Ancillary data can not be edited for user:Val_E Role:SupervisiorOvation session Manager is showing Modify Ancillary Data is enabaled.<br><br>4.The same problem is with user:Val_Engg, Role:&quot;Engineer(DB,Graphics)&quot; which is bydefault roleas per SRF1523.7.Please find the attached snapshots. (Athavale, Samiradixit May 8, 2012) (Ritenbaugh, David W. May 8, 2012) (Ritenbaugh, David W. May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please check to see if point security groups are enabled on the role and the point. Point security groups are not enabled on the roles by default. (Burgoon, Frank J. May 9, 2012)<br><br>1.For any Global role, open Point Security Groups.Under this admin tab is enabled for Local &amp; Remote console.<br>2.After this Ancillary data can be edited from PI for Engineer(DB,Graphics).The same procedure is done for other Global roles.e.g Supervisor etc.<br>3.To edit Ancillary data,point security group of role must be enabled,this point is not mentioned in SRF1523.This point needs to be added in SRF1523. (Athavale, Samiradixit May 10, 2012) (Athavale, Samiradixit May 10, 2012) <br> |  | 35 | FINDING | 8439 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73261
29560 | FINDING | Ancillary data cannot be edited from PI for other than bydefault Global Roles.(Ref SRF 1523) | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Open Ovation security Manager.In Global Roles,bydefault Global Roles as per SRF1523 are Admin,Supervisor,Engineer,Engineer(DB,Graphics).Open other than these bydefault Global Roles.e.g.Engineer(Graphics)Right click on it.<br>2.Properties&gt;Operator&gt;Allow Modification of Ancillary Data is enabled for Local &amp; Remote.<br>3.Log in by User:Val_V (Policy:Unrestricted Uesr) Role:Engineer(Graphics)Open Ovation Session Manager.It shows Modify Ancillary Data is enabled.<br>4.Open PI window. Open analog point. Click on Ancillary tab. Value edit button is not appearing.New value window to edit ancillary field is also not appearing.Hence Ancillary data cannot be edited from PI for Engineer(Graphics) Global Role.<br>5.The same problem is for other Global Roles:Operator,IT,Technician etc.Even after enabling Modification of Ancillary Data property of Role,it is not allowing to edit Ancillary data cannot be edited from PI,which is actual requirement as per SRF 1523 Test5.2.4 Case3. (Athavale, Samiradixit May 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please check to see if point security groups are enabled on the role and the point. Point security groups are not enabled on the roles by default. (Burgoon, Frank J. May 9, 2012)<br><br>1.For Engineer(Graphics) role, open Point Security Groups.Under this admin tab is enabled for Local &amp; Remote console.<br>2.After this Ancillary data can be edited from PI for Engineer(Graphics).The same procedure is done for other roles.e.g. IT,Operator etc.<br>3.To edit Ancillary data,point security group of role must be enabled,this point is not mentioned in SRF1523.This point needs to be added in SRF1523. (Athavale, Samiradixit May 10, 2012) <br> |  | 35 | FINDING | 8440 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73263
29563 | FINDING | Saved filter file does not opened by typing "review /settings system:&ltfile name&gt.rvt" on command prompt. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to reproduce:-<br>1. open ovation point review window.<br>2. save a filtered file as a name of say &quot;abc&quot; in User,Role &amp; System level.<br>3. when type &quot;review /settings System:abc.rvt&quot; on command prompt then the filtered file(abc) did not opened.(the command is not working)<br><br>Note: when the same is done for opening user and role level file by giving corresponding commands(&quot;review /settings User:Administrator:abc.rvt&quot; for user level &amp; &quot;review /settings Role:Admin:abc.rvt&quot; for role level) then filtered file(abc) is opened. <br><br>same behaviour is also observed for alarm. (Prasad, Parmatma May 9, 2012) | none |  |  | save/load system filter files | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | System files will now behave properly. (Burgoon, Frank J. May 11, 2012)<br>Retested in Ov3.5.0_U3 release,the issue has been resolved. (Prasad, Parmatma Jun 8, 2012) <br> |  | 35 | FINDING | 8443 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73269
29565 | FINDING | Hierarchy Search is not working properly in Ovation System Viewer window. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ov 3.5.0_U2 --&gt; Hierarchy Search is not working properly in Ovation System Viewer.<br>If i am selected only two Drop for serching but after serching show all drop details.<br>Please see the attechments for your reference . (Kumar, Sudheer May 10, 2012) |  |  |  | retest the search section. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This should be fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Hierarchy Search is not working in Ov 3.5.0_U7. (Kumar, Sudheer Sep 7, 2012)<br><br>The commissioned and alert searches were not working properly. (Wozniak, Diane M. Sep 11, 2012)<br><br>This should be fixed in the Nov 1 patch. (Wozniak, Diane M. Oct 29, 2012) (Wozniak, Diane M. Oct 29, 2012) <br> |  | 35 | FINDING | 8445 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73273
29567 | FINDING | SDR 18518: G03 Speed Detector Interrupt Rate error message has incorrect limit. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | SDR 18518: For 1C31189G03/1C31192G01 Speed Detector Interface (Enhanced), the parameter [Interrupt Rate at Mechanical Trip Speed (Hz)] is to be limited to a maximum value of 1000 Hz. This limit is enforced, but the error message states that the value must be less than 1000 Hz (rather than having a maximum of 1000 Hz). (Brown, Sean May 10, 2012) |  |  |  | The affected area is in the software which performs object-level validation -- in this case, for the Enhanced Speed Detector I/O Module. The validation check is the same -- only the text shown to the user has changed. The applicable binary is OvPtApi.dll | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The validation message will be modified to indicate that the attribute &quot;...cannot be greater than 1000 Hz&quot;. (Swartz, Mark E. May 10, 2012)<br><br>OK in U3; closing. (Brown, Sean Jun 8, 2012) <br> |  | 35 | FINDING | 8447 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73277
29568 | FINDING | Hardware-related changes causes Virtual Controller to fail during incremental load. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Performing an incremental load of a Virtual Controller after hardware points have been added will cause the controller to fail (I/O scan table entry errors). (Brown, Sean May 10, 2012) |  |  |  | Load a virtual controller. Add a hardware point (or a few). Load the virtual controller to perform an incremental load. This should not result in controller errors. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | problem existed in I/O driver configuration for vxsim (Perdeus, Matthew May 15, 2012)<br><br>OK in U3; closing. (Brown, Sean Jun 8, 2012) <br> |  | 35 | FINDING | 8448 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73279
29569 | FINDING | COMPARE Algorithm is not working properly for invalid inputs. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Whenever we give an invalid value to its any input, all outputs should set to FALSE.<br>Steps to recreate the issue-<br>(1) Use COMPARE algorithm in a control sheet.<br>(2) Open it in signal diagram.<br>(3) Give invalid value to any input/inputs i.e. &quot;NAN&quot; and observe output values. (Singh, Rajan May 11, 2012) (Hutchison, Steven B. May 16, 2012)<br><br>RS: Give &quot;NAN&quot; as input (or any other Invalid value) to one input-pin or both input-pins of COMPARE algorithm. Here all outputs should set to false.<br><br>(Can use attached &quot;svg&quot; file and give &quot;NAN&quot; as input to input-pin IN2 through AVALGEN.) (Singh, Rajan May 22, 2012) (Hutchison, Steven B. May 23, 2012)<br><br>Re-assigning to Ben. (Boehmer, Robert W. Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot Duplicate - (Hutchison, Steven B. May 16, 2012)<br><br>This appears to be how a specific algorithms sets its outputs.<br>- (Hutchison, Steven B. May 23, 2012)<br><br>Issue was wtih comparisons against NaN not returning correct value in VxWorks 6.8. Put in explicit check for NaN. (Christy, Benjamin Jan 29, 2013)<br><br><br>Tracked as SDR 19377 (Ritenbaugh, David W. Jan 29, 2013) <br> |  | 35 | FINDING | 8449 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73281
29570 | FINDING | GBNT crashes while configuring button tabs. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I did the following steps.<br>OPened the GBNT. Selected button. Went to stste/tag field. In the Disabled Button configuration, selected the options as 0 , selected one colour &amp; saved. Again I went for option 1, &amp; while selecting for another colour, GBNT crashes. This happens everytime while I tried to configure the above steps. (N, Thamaraiselvi May 11, 2012) | This bug could cause GBNT to crash when: a) user presses the &quot;save disabled display settings&quot; button in the DisabledButtonConfiguration groupbox on the GBNT:Button dialog(state/tag tab), AND THEN b) user attempts to select a new disabled button color from the color scrolling list. GBNT could also crash if/when user presses the &quot;save appearance settings&quot; button on the GBNT:Button dialog(appearance tab), AND THEN attempts to select a new color from any of the scrolling lists on the appearance page. There was a bug in the routine that saves the settings to the WindowsRegistry that was using uninitialized memory. If the uninitialized memory happened to be 0, GBNT would not crash. That is why this bug is only found on certain computers and GBNT works fine on others. |  |  | Repeatedly change settings on the GBNT:Button dialog and then press the buttons on the GBNT:Button dialog that save the settings to the Windows Registry, and then verify that you can still select new colors from all of the color lists on the GNBT:Button dialog. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I cannot duplicate this. Are you editing/changing the properties of an existing button on the graphic when this happens, or are you creating a new button, or are you saving the disabled display settings in the Windows Registry? Do you have conditionals specified for the disabled configuration params when this happens? Are you changing the default disabled configuration params or are you changing conditional disabled display param settings? Does this happen on all of your systems, or just on one computer? What do you mean by &quot;selected one color &amp; saved&quot;? Do you mean that you pressed OK/Apply and created a new button on the graphic, or did you press the &quot;Apply configuration to selected buttons&quot; button to apply the new display option and color to 1 or more selected buttons, or did you press the &quot;save disabled display settings&quot; button? When you say that GBNT crashed &quot;while selecting for another color&quot;, do you mean that GBNT crashed as soon as you selected a new color from the scrolling list (before you press the OK/Apply button to actually apply the new color to something), or does GBNT crash after pressing the OK/Apply button AFTER selecting a new color? Please send the graphic .src file you are using and specific details of what you do to recreate this problem. (Johnson, Kathy May 11, 2012) <br> This GBNT crashing happening in an existing button on the graphic as well when I am creating a new button. I am not saving the disabled setting in the Window Registry.I don&quot;t specify any conditionals parameter for the disabled parameter. Step 1) In the default disabled button configuration only, in the display options,I select any options say &quot;0&quot; from the scroll tab, then select colour in the 2nd tab showing colours with scroll tab &amp; saved. Step 2) Then again I am selecting in the display options as &quot;1&quot;, then When I gor selecting the 2nd tab for any other colour, while clicking the scroll tab itself, the GBNT start crashing.I observed this on all 32 bit systems. Not happening in 64 bit systems. I need not press the apply configuration. Crashing happening before I press OK/Apply in the step 2 of my above procedure. In the step 1, after selctiong display options &amp; the colour (both from the sccroll tab options), I press the save symbol button.Please refer the attached snapshot file. (N, Thamaraiselvi May 14, 2012).<br><br>Tested the finding in U_3.Observed the issue is resolved. Thus closing the finding. (N, Thamaraiselvi Jun 12, 2012) |  | 35 | FINDING | 8450 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73283
29571 | FINDING | Control Logic Navigation Application is not working properly. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ov 3.5.0_U2 Control Logic Navigation Application is not working properly.<br>Step to reproduce:<br>1.Serch a loaded point in control logic navigator <br>2.Observe the point Originated showing properly<br>3.After serching only it&quot;s showing orginated drop number.But it does not show the point where it&quot;s used. (Kumar, Sudheer May 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can not duplicate. The application works as expected. It finds multiple sheets within the originating controller and receiving controllers.<br><br>The interface is cumbersome. To effect a change in the selected drop, the user must click in the point name field and hit enter. This is the way it works.<br><br>- (Hutchison, Steven B. May 16, 2012) <br> |  | 35 | FINDING | 8451 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73285
29572 | FINDING | Slow Propagation Of Network Highway Status For DU RECORD | Souders, Sarah EMR SYSS PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | After the reboot of the controller, The Network status word (HC field from DU record) is set to 0230H value having 4th bit (Static Point Data Needs Saved) and 5th bit (DDT File Data Needs Saved) set. After 7-10 minutes it is getting updated to 0200H value on OCR400 ( Vxworks Version6.8) controller.<br> <br>Similar test case was executed on Ovation 3.3.1 with OCR400 (vxworks Version5.4) and observe that Network Status Word value is updated in 2-3 seconds.<br> <br>The problem is also appearing on VxSim controller. (Jindal, Deepak May 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please re-test. (Boehmer, Robert W. Oct 29, 2012) <br> Checked and verified on Ovation3.5.0 build and found that there is still Slow Propagation Of Network Highway Status For DU RECORD.Hence the issue has not been resolved. (Jindal, Deepak Nov 1, 2012) |  | 35 | FINDING | 8452 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 73287
29573 | FINDING | In case of VxSim controller,the toolserver stop error message is coming while running the diagnostic application. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In diagnostic application if we select the VxSim controller drop then tool server task is getting stopped as mentioned in below error log on VxSim drop console-<br><br>Exception !<br>Vector 13 : Access Violation<br>Program Counter:0x1015bc4f<br>Access Address (read):0x83e58a19<br>Status Register:0x00010a93<br>Task: 0x1402dc48 &quot;toolsrvr&quot;<br>0x1402dc48 (toolsrvr): task 0x1402dc48 has had a failure and has been stopped.<br>0x1402dc48 (toolsrvr): fatal kernel task-level exception!<br><br>[vxsim] drop76&gt; tt toolsrvr<br>0x12b102ed dpustat +0x11d: svc_run ([0, 0, 0x1003bc01, 0, 0])<br>0x10146fb8 svc_run +0x68 : 0x10146d33 (0x141cfebc, 0x1302b978, 0x100, 0)<br>0x10146f28 svc_getreqset+0x298: 0x12b1040d (0x141cfe78, 0x12facd98, 0x141cfd54, 0x10073263)<br>0x12b10602 dpustat +0x432: dropdiaggetdropinfo_1 (0x141ce520, 0x141cfe78)<br>0x12b147f6 dropdiaggetdropinfo_1+0x16 : DROPDIAGserverGetDropInfo (&amp;glo)<br>0x12b11b15 DROPDIAGserverGetDropInfo+0x115: muxIoctl (&amp;dro, 0x4010e507, 0x141ce4f0)<br>value = 0 = 0x0<br><br>and diagnostic in not showing any status for the VxSim Drop. (Jindal, Deepak May 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK in 3.5.0_U3 @ 02-Jul-12 (Benzvi, Mati Jul 2, 2012) <br> |  | 35 | FINDING | 8453 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW |  |  | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM India Engineering Center |  |  |  | FINDING | [6 empty] | 73289
29574 | FINDING | (Drop) Download Preview window could not be opened from System Database Object. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Right click on System Database object(IVALSYS3).Click on Download option.<br>2.Try to open Download Preview window. It could not be opened.<br>3.Error occurs.&quot;Unable to complete the requested operation.&quot; Attached by name Drop_Download_Preview_1<br>4.If click on Ok. Sometimes one more error occurs. Attached by name Drop_Download_Preview_2 (Athavale, Samiradixit May 14, 2012)<br>Download Preview window can be opened from System Database Object.Found Fixed in 3.5.0_U3.Hence Finding is closed. (Athavale, Samiradixit Jun 7, 2012) |  |  |  | The Ovation Developer Studio download function has been affected. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8454 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73291
29578 | FINDING | point "COPY" option is not available for DU point. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If a drop point (DU) is selected and Right Click the context menu is not showing &quot;COPY&quot; option. <br><br>Applicability: If we have one redundant drop (E.g drop 29/79) then after creating one drop point (drop29), the second drop point (drop79) can be created using &quot;COPY&quot; functionality.<br><br>Please find attached the remote login details of drop 245. (Joshi, Parmesh May 16, 2012) |  |  |  | The affected area is in the software which contains the operations applicable to object types. Specifically, the Copy operation will be supported for Drop Points. The applicable binary is OvPtApi.dll | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | By design, this function was omitted for Drop points, as it was recognized to have limited utility/value. However, this function can be added. The user should note, however, that care must be taken to ensure that the Drop Number and Partner Drop pull-down attributes are properly specified in the copied point. (Swartz, Mark E. May 16, 2012)<br><br>PJ, 07th June 2012: Checked in ov 3.5.0_U3, Found ok. Hence closed. (Joshi, Parmesh Jun 7, 2012) <br> |  | 35 | FINDING | 8458 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73298
29579 | FINDING | Opening Control sheet view window through &ltopen item in control sheet&gt after reconcile gives error. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Opening Control sheet view window through &lt;open item in control sheet&gt; after reconcile gives error.<br>In Studio, on reconciling controller shows tuning changes ,right clicked &lt;open item in control sheet&gt; it gives error (refer reconcile.jpg) (Kumar, Shailendra May 16, 2012)<br>Remote login steps for drop where this was performed is attached(Remote_login_drop245.rtf). (Kumar, Shailendra May 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | As shown in the displayed error, the Ovation Developer Studio is unable to start C:\Ovation\CtrlBldr\libTest.exe. This is because the executable is not on the Ovation drop -- and is not specific to the IEC Validation system drop245. Remote login to IEC is not required. The Ovation 3.5.0 build/deployment issue will be investigated. (Swartz, Mark E. May 16, 2012)<br><br>Fixed - (Hutchison, Steven B. May 16, 2012)<br><br>SK:ok in U3 hence closed. (Kumar, Shailendra Jun 12, 2012) <br> |  | 35 | FINDING | 8459 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73300
29580 | FINDING | Copy Ctrl--&gtDB tab is not working In Ovation Holding Register editor | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Copy Ctrl--&gt;DB tab is not working In Ovation Holding Register editor.<br>Steps are as follows-&gt;<br>While checking with ladder sheets in signal diagram, we are using holding registers for different parameters of special functions. Consider Holding register 0 and 1 is used as REG1 and REG2 for ADD special fucntion. Holding Register 2 is used to store the result.Open Holding Register window, enter value for Holding Register 0 &amp; 1.Apply changes to Database and Online, both the options are selected.the resulted value will appear correctly in the 2 register field.but Holding Register 2 value does not copy to database in ovation holding register. (Kumar, Sudheer May 16, 2012) |  |  |  | The affected area is in the software which checks to see if it is valid to copy the values from the selected controller to the database. Previously, this operation was blocked if the controller was non-redundant. Note that the target controller must still be In Control for the operation to be performed. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | More information required. Does Holding Register 2 currently exist in the database? (Swartz, Mark E. May 16, 2012)<br><br>Holding Register 2 is currently exist in tha database . (Kumar, Sudheer May 16, 2012)<br><br>The attached snapshot shows that the applicable Controller is DROP13. What is the mode of this controller? In Control? In Backup?<br>Please also repeat this test on a redundant controller and report the results. (Swartz, Mark E. May 17, 2012) <br> The Applicable Controller Drop 13 is in control mode.<br>I am unable to repeat this test on redundant controller because redundand Controller drop fails on loading sheet with ladder Algorithm. (Kumar, Sudheer May 21, 2012)<br><br>Please note that the Ctrl--&gt;DB button is designed to only update the database if the selected controller is currently &quot;In Control&quot;. <br><br>Currently, it appears that it will also only operate correctly if the controller is redundant (hence the request to repeat this test on a redundant controller -- it is unfortunate that the IEC 3.5.0 Validation Systems do not have any functional redunant controllers). The current limitation preventing Ctrl--&gt;DB functionality for non-redundant controllers will be eliminated. (Swartz, Mark E. May 21, 2012)<br><br><br>Please refer to F#8470 For related to redundant controllers. (Kumar, Sudheer May 22, 2012) |  | 35 | FINDING | 8460 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73302
29581 | FINDING | C: drive on new DBS filled to the max with 55Gb size OvationStationSynchronizer file | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On the new 3.5.0 Westinghouse network, after creating only OSS, DBS &amp; VCH drops with <br>DU records only, the C: drive on the DBS drop filled to the Max.<br>We found a 55Gb size file:<br>C:\Windows\ServiceProfiles\NetworkService\AppData\Local\Temp\OvationStationSynchronizer<br>On the 2 3.5.0 DBS drops in the Val Lab the size of the same file is 4kb &amp; 5kb respectively. (Benzvi, Mati May 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Duplicate of 8303. Please Close. (Hutchison, Steven B. May 16, 2012)<br>---<br>oops - how fast we (me) forget. (Benzvi, Mati May 16, 2012) <br> |  | 35 | FINDING | 8461 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73304
29582 | FINDING | Unable to save the text file after search operation thru "save as" option in file menu in Devoloper studio | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps followed (Drop176)are:-<br><br>1. Opened the devoloper studio <br>2.Clicked on Drops<br>3.Right clicked on the analog points in Drop13 and selected the search operation.<br>4.Selected the find all ponts<br>5.All the analog points in Drop 13 are displayed in Studio (Attached the snap shot Save_as_Studio.jpeg)<br>6.Selected the save as option in File menu then save as window appeared in the studio .<br>7.Given the file name Drop13_Analog.txt and saved in folder D:\JJ\<br>8.After saving the file , searched for file Drop13_Analog.txt, it has not found in System.(Refer the snapshot Save_as_Studio_2.JPG)<br>Attached the remote log in details also. (Jayarajan, Jayakumari May 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a duplicate of Finding 8396. In addition, the issue associated with the &quot;Save As&quot; option is applicable for most Ovation Studio UI dialogs (in addition to the Search results as identified in this Finding and in Finding 8396). <br>Please close this Finding and continue to track the issue via Finding 8396. (Swartz, Mark E. May 17, 2012) <br> |  | 35 | FINDING | 8462 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73306
29584 | FINDING | Trying to ping its third party devices eventually causes an OCR400 to fail. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400 Controller 35/85 (WALT) is configured with Allen-Bradley, Modbus and GE Mark V devices. There are messages from the controller stating that it cannot ping the Modbus and A-B devices (even though pinging them from a telnet session in the controller succeeds). Messages with memPartAlloc appear later and the controller eventually fails and is unreachable over the network. Some Ovation Error Log messages are attached to this finding. (Brown, Sean May 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Several changes have been made since the initial finding to the kernel and the drivers to address these errors. Retest in U6. (Ciccozzi, Anthony Aug 7, 2012) <br> |  | 35 | FINDING | 8464 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73310
29585 | FINDING | IOIC Secondary Power Supply selection was not correct after OvPtImport. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The Secondary Power Supply selection for an IOIC was incorrectly defined after a Power Tools import was performed. The import file had SECONDARY_POWER_SUPPLY=0, but a 1 was in the database. (Brown, Sean May 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The issue is that there are IoDevice object attributes for which the import/export names are not unique. Specifically, the IOIC primary power supply (applicable for IOIC type IoDevices) and the DIOB primary power supply (applicable for Local QLine IoDevices) are both named PRIMARY_POWER_SUPPLY. (Ditto for IOIC secondary power supply and DIOB secondary power supply -- SECONDARY_POWER_SUPPLY.)<br>During OvPtImport, the &quot;wrong&quot; attribute may be updated. For example, even though it is an IOIC, the SECONDARY_POWER_SUPPLY entry in the import file may end up driving the value of the hidden DIOB secondary power supply attribute.<br><br>Development will consider the possibility of changing the import/export name of the DIOB primary and secondary power supply attributes to DIOB_PRIMARY_POWER_SUPPLY and DIOB_SECONDARY_POWER_SUPPLY, respectively, to eliminate conflicts in the future. This however, will also impact DBID. (Swartz, Mark E. May 18, 2012)<br><br>Converted to SDR; closing. (Brown, Sean Sep 26, 2012) <br> |  | 35 | FINDING | 8465 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73312
29586 | FINDING | It is not possible to launch Force application for SIS algorithms. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When Advanced Tunning window is opened for SIS algorithm from Signal Diagram, clicking on &quot;Force...&quot; button results in &quot;Cannot launch Force Window&quot; error. Detailed message is &quot;Some required files might be missing&quot;. After running Process Monitor application, it can be seen that cbViewer.exe process tries to locate Force application under following path <br>&quot;C:\Ovatio\OvationBase\OvSisForceApp.exe&quot; (missing &quot;n&quot; in Ovation directory name). (Czak, Jakub May 18, 2012) |  |  |  | It should be possible to run SIS Force application from advanced tuning window of SIS algorithm. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This appears to be in OvSisForce. The signal diagram viewer calls SendTo_OvSisForce. <br>- (Hutchison, Steven B. May 18, 2012)<br><br>OvSisForce.dll was truncating path to Ovation install directory. (Czak, Jakub May 28, 2012) <br> |  | 35 | FINDING | 8466 |  | FINDING | [10 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73314
29589 | FINDING | Selecting EWS drop with special characters as Ovation drop name in Dev. Studio crashes the Studio | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were performed on DBS drop250 (Net#7) while testing SDR18317:<br>1. In Ovation Developer Studio hierarchy, inserted an Operator Station drop235 with its Ovation drop name as DROP235. Since its DNS Computer Name was also DROP235 so in Studio the DNS Computer Name did not appear in parenthesis next to Ovation drop name which is ok.<br>2. Now, changed the Ovation drop name of 235 with some special characters [~!@#$%^&amp;*]. The studio accepted the details.<br>However, now onwards whenever drop235 is selected in the developer studio, the stuio crashes. Please refer the attached files (jpeg showing the eventviewer details &amp; txt file showing the details when Dev. Studio crashes). Also attached is the remote login info of drop250. (Gupta, Chandresh May 21, 2012) |  |  |  | The method used to format the title bars on various portions of the Ovation Developer Studio (e.g., those which are changed based on the selected item in the hierarchy and/or shown when opening an object) has been changed to accommodate an embedded % character. The affected area is in the routine which formats/creates the title bars in the Ovation Developer Studio. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please note that many of the special characters which were entered (as indicated in the Description) are not valid for DNS Host Names. Reference Microsoft support document 909264.<br>Note that the computer name as entered in the Ovation Developer Studio is the DNS computer name of the machine. Was drop235 actually named with these special characters when joined to the domain?<br><br>cg (05/21/12) - No, the drop235 was not named with any of the special characters while joining the domain. The changes that I made were all done in the developer studio. In this case following are the details:<br>DNS Computer Name - DROP235<br>Ovation Computer Name (as entered in dev. studio) - ~!@#$%^&amp;* (Gupta, Chandresh May 21, 2012)<br><br>The problem occurs because of the embedded percent (%) character in the Ovation Computer Name attribute. Since this attribute is now shown as the object name in certain situations, it also can be shown in the title bar of various portions of the Ovation Developer Studio. The formatting of this string was causing a problem due to the embedded percent character. The method of formating the title bars will be changed to accommodate this character. No invalid character checks will be performed on this attribute, since it is used to associate the database object with a computer which is a member of the domain. (Swartz, Mark E. May 29, 2012) <br> cg (06/11/12) - Finding retested in Ov3.5.0_U3. Working fine with % chanracter. Hence finding closed. (Gupta, Chandresh Jun 11, 2012) |  | 35 | FINDING | 8469 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73320
29590 | FINDING | Controller drop fails on loading sheet with ladder Algorithm. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ov 3.5.0_U2 Controller drop fails on loading sheet with ladder Algorithm.<br>I am creating a new control sheet using Ladder block after loaded this sheet controller is going on fail mode.<br>Please refer attached error log and snapshot. (Kumar, Sudheer May 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8470 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73322
29592 | FINDING | In point copy functionality SVTP "3.5_SDR18181_SVTP_rev1.0_PJ", the Windows name written need to modify. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | IN the point copy functionality SVTP &quot;3.5_SDR18181_SVTP_rev1.0_PJ&quot;, The windows name written need to changes as follows.<br>1. Step 5.1.2: the ¿Insert new point wizard¿ window name should be change by ¿Insert Copy of &lt;source point name&gt; Wizard¿ window.<br>2. Step 5.1.3: the ¿Insert new point wizard¿ window name should be change by ¿Insert Copy of &lt;source point name&gt; Wizard¿ window and the ¿New Points¿ window name should be change by &quot;Copy of &lt; source point name&gt;-¿ window. (Joshi, Parmesh May 22, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-05-22T00:37:42-04:00</p> <p><strong>Modified Date:</strong> 2012-05-22T00:37:42-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8472 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73325
29593 | FINDING | Point Copy Functionality is not working if Source point is configured with alarm limit type as "Point" | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If a source point is having alarm limits (High/Low) configuration as type &quot;Point&quot; and a valid point name is given for the limits, then point copy functionality (using the source point) is not working. (The new point is not creating , showing error as &quot;alarm limit of type P, name must be specified&quot;.<br>please find the attached snap shots names &quot;Alarm Limit Copy Error&quot; and Remote login details. (Joshi, Parmesh May 22, 2012)<br><br>PJ:May 24,2012: The point is copied as follows:<br>1. Select the source point, RightClick and select &quot;Copy&quot; option.<br>2. The &quot; Insert Copy of &lt;Source point Name&gt; Wizard&quot; window will open.<br>3. Give a new name to the copied point. and click on Finish tab<br>4. The Copy of &lt;Source point Name&gt; Wizard&quot; window appears.<br>5. click on &quot;Apply&quot; tab , as we click, the error comes as mentioned above. (Joshi, Parmesh May 24, 2012) |  |  |  | The affected area is in the initial population of attribute values in the new point. Attributes defined as the name or value attribute, object key references, and attributes which are dynamically generated are all bypassed (by default) in the copy operation -- however, a new check will be made to permit certain of these types of attributes by exception (specifically, alarm limits and alarm cutouts). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | How was this point copied?<br>- (Hutchison, Steven B. May 23, 2012)<br><br>Wrong Product.<br>- (Hutchison, Steven B. May 24, 2012)<br><br>The Copy function was designed to not include attributes which are &quot;key references&quot; to other items. This is certainly desirable for hardware references but this constraint should probably be relaxed for items such as alarm fields and cutouts which can support many-to-one references. Development will consider this modification. (Swartz, Mark E. May 25, 2012)<br><br>The design of this function will be modified to include alarm fields and alarm cutouts in the set of attributes which will be copied. Note that other references such as hardware references and simulation point references will not be copied. (Swartz, Mark E. May 29, 2012)<br><br> PJ 07th June 2012: Checked in ov 3.5.0_U3, Found ok. Hence closed. (Joshi, Parmesh Jun 7, 2012) <br> |  | 35 | FINDING | 8473 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73327
29594 | FINDING | Error log message for disable option In 5.2 _Test case 2_i_2 of "3.5 TUDIO_SVTP_Rev3.5_JJ " need to correct. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In 5.2 _Test case 2_i_2 in 3.5 STUDIO_SVTP_Rev3.5_JJ the error log message is written as ¿Offline Mode.¿ in Ovation Error Log (on the Ovation Database Server) <br><br>Instead of ¿Offline Mode.¿ the message in Ovation Error Log (on the Ovation Database Server) appears as &quot;System configured with off line mode disabled&quot;. (Jayarajan, Jayakumari May 22, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Jayarajan, Jayakumari</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Jayarajan, Jayakumari</p> <p><strong>Entry Date:</strong> 2012-05-22T06:40:05-04:00</p> <p><strong>Modified Date:</strong> 2012-05-22T06:40:05-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8474 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73328
29595 | FINDING | In 5.2 Test case 2_h, in 3.5 STUDIO_SVTP_Rev3.5_JJ clear, reload instead of re-load for the affected drops | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Offline Mode is enabled via a new checkbox attribute on the System object of the Ovation database , after that carried out the various test such as <br><br>1. moving control sheets from one control task to another within an Ovation controller<br>2.moving Ovation points from one Ovation drop to another <br>3.Change the broadcast frequency of points<br><br>As per the test case when tried to re-load the affected drops the system given a message to clear the drop and then load.<br><br>So the 5.2 Test case 2_h, in 3.5 STUDIO_SVTP_Rev3.5_JJ need to correct as &quot; h) After making the above mentioned changes, clrar,re-load the affected drops and verify that the changes function correctly&quot; . (Jayarajan, Jayakumari May 22, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Jayarajan, Jayakumari</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Jayarajan, Jayakumari</p> <p><strong>Entry Date:</strong> 2012-05-22T06:57:39-04:00</p> <p><strong>Modified Date:</strong> 2012-05-22T06:57:39-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8475 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73329
29596 | FINDING | Maximum number of opened files was decreased in VxWorks 6.8 kernel | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In VxWorks 6.8 kernel configuration (for Ovation 3.5 controllers) the maximum number of opened files is set to 192. In previous version (VxWorks 5.4) it was set to 255. <br><br>That value could be checked by reading iosFdMaxFiles variable. (Kossowski, Grzegorz May 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Increased file descriptors to 255. (Pingree, Douglas K. May 30, 2012) <br> |  | 35 | FINDING | 8476 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73331
29597 | FINDING | Filter out event does not save in the Ovation Audit Viewer Application . | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0_U2 Audit viewer application does not save any file after filter out event.<br>I have filter out the event by auditview serch tab than try to save as but these Audit file are not saved in the given path. (Kumar, Sudheer May 23, 2012) (Kumar, Sudheer May 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please reference Findings 8396 and 8462 -- same issue. (Swartz, Mark E. May 23, 2012) <br> |  | 35 | FINDING | 8477 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73333
29600 | FINDING | SVG files are not opening in CB editor after making IE9 as default browser. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to recreate the issue...<br><br>(1) Open IE explorer (IE-9) in a system where OV3.5.0 is installed.<br>(2) It will ask &quot;would you like to make IE your default browser?&quot;. Here select the <br> option &quot;YES&quot;.<br>(3) Now open Developer Studio and attempt to open any control sheet.<br>(4) The sheet (SVG file) will open in the IE browser window instead of CBEditor viewer.<br><br> Hence user is not able to open any of the control sheets and also unable to proceed further engineering practices. (Singh, Rajan May 23, 2012) (Hutchison, Steven B. May 23, 2012)<br><br>RS: Selected ¿Don¿t ask again¿ option at first time opening of IE-9 Explorer .<br>After that everything is working fine. (Singh, Rajan May 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works as Desgined - Reset the &quot;Default Program&quot; or &quot;File Association&quot; for Scalar Vector Graphics (SVG). See the following links for details.<br><br>For Server 2008<br>- http://dataerror.blogspot.com/2008/05/changing-file-type-association-in.html<br>For Windows 7:<br>- http://windows.microsoft.com/en-us/windows-vista/change-which-programs-windows-uses-by-default<br><br>For XP<br>- http://support.microsoft.com/kb/307859 (Hutchison, Steven B. May 23, 2012) <br> |  | 35 | FINDING | 8480 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73339
29603 | FINDING | In Trend Right click &ltSystem Viewer&gt gives Firewall block message for the First time. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Trend, opemned some point then Right click &lt;System Viewer&gt; , it gives Firewall block message( refer attached snapshot).It happens for the first time.Checked on drop236 Win7 SP1(64 bit ) machine.Remote login steps are also attached. (Kumar, Shailendra May 24, 2012) | none |  |  | Ensure OvSystemViewer is not listed in firewall exceptions before loading Ovation. After loading Ovation the first time OvSystemViewer is executed there should not be a popup window concerning features of OvSystemViewer being blocked by the firewall. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added OvSystemViewer.exe to the list of firewall exceptions in cfgfirewall.bat. (Burgoon, Frank J. May 24, 2012)<br><br>SK:Ok in U3 ,hence closed. (Kumar, Shailendra Jun 26, 2012) <br> |  | 35 | FINDING | 8483 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73345
29604 | FINDING | Copy Operation,the Base Sheet number gets converted to its eqvivalent Octal number and is assigned to the sheet. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While performing the copy operation, the base sheet number (070) provided to the sheet gets converted into its equivalent Octal number value (56)and this number is assigned to the sheet.<br><br>Steps followed are:<br>Tools -&gt; Operation -&gt; Copy Operation -&gt; Select a sheet to be copied -&gt;Next -&gt;Provide the required Drop Number: 13, Task Number: 2, Base Sheet Number: &quot;0101&quot;. Finish. <br>This copies the sheet into Drop13, Task2 and as sheet number &quot;65&quot;. <br><br>This is observed only when any number is prefixed with 0. eg. 010 = 8, 0707 = 390, etc... (Sachan, Pallavi May 24, 2012) (Hutchison, Steven B. May 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Also true for Import Operation. Fixed <br>- (Hutchison, Steven B. May 24, 2012)<br><br>Found Fixed. Hence Closed. (Sachan, Pallavi Jun 7, 2012) <br> |  | 35 | FINDING | 8484 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73347
29605 | FINDING | Export operation changes the sheet name into some greek characters, inconsistently. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While performing Export Operation, it is observed that the sheet name changes to some greek characters.<br><br>The same was observed with 3.5.0_U0 while smoke test with a XPID sheet Export/Import operation.<br>This time it is observed with 3.5.0_U2 simple Ladder sheet Export operation.<br><br>Note that these greek characters are not allowed to enter as sheet name while Insert New Sheet Operation is performed.<br><br>Kindly find the attached &quot;sheet name changed to greek characters_3.5.0_U0.jpeg&quot; ; &quot;greek characters_3.5.0_U2.jpeg&quot;. (Sachan, Pallavi May 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Was the title modified when the sheet was re-imported? Or Was the title modified when the sheet was exported?<br>- (Hutchison, Steven B. May 24, 2012)<br><br>No, Title was not modified at all. First time the change was observed when the sheet was re-imported. Second time the change was observed at the time of export. (Sachan, Pallavi May 25, 2012) <br> Fixed in U7 - PLEASE RESET IN TIME FOR A CORRECTION FOR U8 - THANKS <br>- (Hutchison, Steven B. Sep 4, 2012)<br><br>Performed various import operations, but the above scenario was not observed again. Hence finding is Closed. (Sachan, Pallavi Sep 7, 2012) |  | 35 | FINDING | 8485 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73349
29608 | FINDING | Devoloper studio crashes while enabling the check boxes 29,30,31 in initial tab of Packed Digital points | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Inserted a new packed digital point(JJ_OV35_FP1_PD1) in by right clicking the Packed digital point in the devolper<br> studio.Given the point name in point tab , then gone initial tab , there check boxes for values are enabled from 1,2,3<br> in consequent order. when try enable the 29th check box the studio crashed. <br><br>Attached the snap shot and the remote login details of drop253 also for reference. (Jayarajan, Jayakumari May 24, 2012) |  |  |  | The affected area is in the handling of this 32-checkbox item in the user interface portion of the Ovation Developer Studio. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This problem is due to the way in which this 32-checkbox widget is converted to a number in the User Interface. This will be corrected by internally treating this as an unsigned item. (Swartz, Mark E. Jul 17, 2012)<br><br>JJ_20thAug2012<br><br>Checked and found now we can check the 29th box then there is no crash also (Jayarajan, Jayakumari Aug 20, 2012) <br> |  | 35 | FINDING | 8488 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Patel, Sunil EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73355
29611 | FINDING | 3.5_Control Functions SVTP_rev2.3_TN should be modified according to the Point Name. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In the Test case of 5.1.2, the 2nd line of &quot;Verify the Algorithms outputs do not have BAD quality&quot; can be modified according to Point type. For reference, in the Mamode Algorithm assigned to me, the output Mamode word is packed point, cannot be checked for the quality.<br>So the test case can me modified to according to the point type. (N, Thamaraiselvi May 24, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Control Functions (CF)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch N, Thamaraiselvi</p> <p><strong>Entry Date:</strong> 2012-05-24T07:43:54-04:00</p> <p><strong>Modified Date:</strong> 2012-05-24T07:43:54-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8491 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73360
29616 | FINDING | Changing Default network then browsing point in PI gives unhandled exception error. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On drop236(Win7 SP1-64 bit ) opened Ovationsession manager and changed the default network name from FE350C to FE350.<br>Then Opened PI, clicked &lt;Browse Point&gt; it gives unhandled exception error(refer attached JPG).<br>Also attached is the Remote login steps. (Kumar, Shailendra May 25, 2012) | none |  |  | Change default network in OvSessionManager then bring up point browser from PI or Trend. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected for U3. (Burgoon, Frank J. May 25, 2012)<br><br>SK:Ok in U9 hence closed. (Kumar, Shailendra Oct 23, 2012) <br> |  | 35 | FINDING | 8496 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73370
29617 | FINDING | Controller_SVTP is missing 5.23 in the Test Record Sign-Off sheet | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Controller_SVTP is missing 5.23 in the Test Record Sign-Off sheet:<br> 5.23 TEST CASE 23: Security &amp; Misc. (Benzvi, Mati May 28, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2012-05-28T12:16:18-04:00</p> <p><strong>Modified Date:</strong> 2012-05-28T12:16:18-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8497 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73371
29620 | FINDING | Blank "Load preview" window crashes the developer studio while performing any mouse operation on the window. | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When &quot;Drop load preview&quot; is enabled from system level in developer studio then while loading any type of drop (EWS or Controller), &quot;Load Preview&quot; window appears prior to loading.<br><br>If no change is done on the drop and load the drop, the blank &quot;Load Preview&quot; window appears prior to loading.<br><br>Problem: If some mouse operation is performed on that blank &quot;Load Preview&quot; window (resize the window, clicking on blank space etc), a popup comes showing &quot;Ovation Developer studio for windows application file has stop working, Click on &quot;Close Program&quot; button is further closing the developer studio.<br><br>Note: 1.If the &quot;Load Preview&quot; is not blank, then the developer studio is not crashing while performing the same mouse operation.<br> 2. The appearance of blank &quot;Load preview&quot; window is also not good.<br><br>please find attached snap shot name &quot;studio crash&quot; and remote login details. (Joshi, Parmesh May 30, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | When there are no differences, the dialog is not being populated with any controls and a click event in the pane will cause a crash.<br>Note, however, that if the user does not resize the window or click in the empty pane, the Continue and Abort buttons work as expected. Therefore, this does not warrant a category of 2.<br><br>The software will be changed to detect that there are no differences and show a more informative message. (Swartz, Mark E. May 30, 2012)<br><br>Checked in U7 Build, Found ok. IF no items are to be loaded then pop up comes as &quot;No items to preview&quot; while loading Hence Closed. (Joshi, Parmesh Sep 4, 2012) <br> |  | 35 | FINDING | 8500 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73377
29621 | FINDING | [Point Name] Column can not be restored if it is removed. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps are:<br>1. Open PI application - Click search button. Ovation point browser window gets appeared.<br>2. Select Filter and start. Point list gets updated.<br>3. Right click on Column ribbon bar and select [coloum chooser]option. [Customization] window gets appeared.<br>4. Right click on a Column available on Column ribbon bar and select [Remove this Coloumn]option. Removed coloum gets moved to customization window. This coloum can be restored through drag and drop from customization window to Column ribbon bar.<br>Observation: If [point Name]Column removed, not moved to customization window. So, [point Name] Column cannot be restored. PI application needs to be restarted. (Pandey, Vijay May 30, 2012) | none |  |  | Bring up point browser window from Point Information and from Trend. Point Name column should not be able to be moved or hidden | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Point Name column is not intended to be moved or hidden. Changes have been made to implement the correct behavior. (Burgoon, Frank J. May 30, 2012)<br>VP: Retested with U3. Found issue fixed. Hence finding is closed. (Pandey, Vijay Jun 7, 2012) <br> |  | 35 | FINDING | 8501 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73379
29622 | FINDING | Deleted control sheets name is not showing on "Load Preview" window. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | 1.When a new control sheet is creted and then &quot;Load Preview&quot; window is showing the sheet name on &quot;New Object&quot; tab with &quot;Object Name&quot; as &quot;&lt;sheet No.&gt; &lt;Sheet Name&gt;&quot; and &quot;Object Type&quot; as &quot;control Sheet&quot;. please see attached file name &quot;sheet creation.jpeg&quot;<br>2. When the same sheet is deleted and loaded then &quot;Load Preview&quot; window will appears showing the &quot;Deleted Objects&quot;tab is with &quot;object name&quot; as &quot;00A3&quot;(sheet point name) however it should show the same name as while creation.(&lt;sheet No.&gt; &lt;Sheet Name&gt;) please see attached file named &quot;sheet deletion.jpeg&quot;<br>please find attached the remoted login details. <br>Note: The load priview should be enable from system level. (Joshi, Parmesh May 30, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Swartz, Mark E. Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-05-30T02:56:10-04:00</p> <p><strong>Modified Date:</strong> 2012-06-05T01:54:47-04:00</p> | 0 |  | Ovation for Windows/General/Software | This is the way it works. Since the Control Sheet has been deleted from the Ovation Database by the user (e.g., via the Ovation Developer Studio), the extra information about the control sheet (e.g., sheet number and name) has also been deleted. The only information available for display is the information which is contained in the controller, which consists of its 4 character sheet number (e.g., &quot;00A3&quot;). (Swartz, Mark E. May 30, 2012)<br><br>PJ: 1st June 2012:If this is case then corresponding SVTP should be modify by putting a note that &quot;If a control sheet is deleted then &quot;deleted objects&quot; tab will not show the sheet name or number, it will show its 4 character sheet number. (Joshi, Parmesh Jun 1, 2012)<br><br>As stated, this is how it was designed and how it works. (Swartz, Mark E. Jun 1, 2012) <br> |  | 35 | FINDING | 8502 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73380
29624 | FINDING | Unpack16 unconnected output pins it"s not showing in the signal diagram Viewer | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I am creating a control sheet in control builder and used Unpack16 Algo in a control sheet. Then opened this control sheet in signal digram viewer .In signal Diagram showing only connected output pins, unconnected output pins it&quot;s not showing .<br>Please refer attached screenshot (Kumar, Sudheer May 31, 2012) (Hutchison, Steven B. Jun 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it Works. Optional outputs do not have points and therefore their is not value to display. (Hutchison, Steven B. Jun 6, 2012)<br><br>Observation :<br>In Ovation 3.5.0 another algos unconnected Optional output pins it&quot;s showing in the signal diagram Viewer.<br>and Ovation 3.4.0 Unpack16 unconnected Optional output pins also showing in the signal diagram Viewer. (Kumar, Sudheer Jun 7, 2012) (Hutchison, Steven B. Aug 15, 2012) <br> |  | 35 | FINDING | 8504 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73384
29625 | FINDING | Control Options -&gt Reconcile Operation is non-functional. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step1: Parameters are tuned from Signal Diagram.<br>Step2: Go to Developer Studio -&gt; Select Controller drop/ Control Sheet -&gt; Right Click -&gt; Control Options -&gt; Select Reconcile Operation.<br>Reconcile Window Appears and there are no tuning changes shown in the window.<br>Step3: Click next, On Finish screen, Click on sheet , Sheet opens. <br>Go to File -&gt; Reconcile. No operation is seen.<br>And the parameters changed from signal diagram are not uploaded to the database. (Sachan, Pallavi May 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The above process is invalid. See section 15.11 of the 3.4 control builder manual for details. (Hutchison, Steven B. Jun 6, 2012)<br><br>Closed Confirmed. (Sachan, Pallavi Jun 6, 2012) <br> |  | 35 | FINDING | 8505 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73386
29626 | FINDING | Redundant EWS drop names appearing incomplete in Find: All Objects window | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were performed on 3.5.0 Net#7:<br>1. In Dev Studio, right click on redundant EWS DROP234/DROP236 &amp; select &quot;Find&quot; option in the context menu.<br>2. Find: All Objects sub-window opened. <br>3. In this sub-window there are 2 Radio buttons. The description of second Radio button which says &quot;Find in DROP234/DROP236....&quot; is not appearing completely. The last portion of text is missing in it due to long name of the redundant EWS drop.<br>The same needs to be corrected.<br>Please refer attached snapshot file Find_long_name.jpg where the issue is marked with RED box. (Gupta, Chandresh May 31, 2012) |  |  |  | Ovation Developer Studio - Find dialog on redundant EWS drop. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. Now the full text of the description should show correctly. (Thirunavukkarasu, Utthandi Aug 29, 2012)<br><br>cg (09/20/12) - Finding retested in U8. Now, the text is appearing in full if the Computer names are normally defined like drop234 or drop236. Please refer attached snapshot file F#8506.jpg.<br>However, if the Computer name of the drop is different &amp; contains more no. of characters then the Find window shows it incomplete. Please refer attached snapshot file F#8506a.jpg. Based on this I am Failing this finding. (Gupta, Chandresh Sep 20, 2012)<br><br>Yes, it will be truncated at the end when the full computer name is very long. The length of the text shown here has been extended to allow maximum possible horizontal extent of the Find window. If it excess that length then it will the truncated at the end. This is a normal/expected behavior. (Thirunavukkarasu, Utthandi Oct 16, 2012)<br><br>cg (10/16/12) - Based on the developers comments this finding is closed. (Gupta, Chandresh Oct 16, 2012) <br> |  | 35 | FINDING | 8506 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73388
29627 | FINDING | Could not open signal diagram from Controller Diagnostics--&gtPoint Details for first time. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On drop236 opened controller diagnostics selected controller drop navigate to &lt;Point Details&gt; tab it opens orignated points.Now right click on point used in sheet and clicked signal diagram.<br>It opens blank cbviewer with error showing that sheet does not exist.If same point is opened in PI and signal diagram is opened through PI it opens sucessfully.<br>After this opening signal diagram through controller diagnostics--&gt;Point details opens it sucessfully.<br>Attached is the error and login details of the drop. (Kumar, Shailendra May 31, 2012) (Kumar, Shailendra May 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is caused by trying to open a sheet before it has been full distributed. (Christy, Benjamin Jan 30, 2013) <br> |  | 35 | FINDING | 8507 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73390
29629 | FINDING | In TR 3.5_SDR18317_SVTP_rev1.0_CG.doc test case 5.1.7 (f) - Copy is not applicable | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | TR 3.5_SDR18317_SVTP_rev1.0_CG.doc test case 5.1.7 (f) says to perform [Copy] operation from right click menu at the Drop object. However, there is no such Copy option in the context menu. Hence this test case is not applicable.<br>Also, test case 5.1.7 (e) describes &quot;Recocile&quot;. Spelling of this needs to be changed to &quot;Reconcile&quot;. (Gupta, Chandresh May 31, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-05-31T06:43:42-04:00</p> <p><strong>Modified Date:</strong> 2012-05-31T06:43:42-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8509 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73393
29630 | FINDING | page bubbles should be replaced with page connector in 3.5_CB_SVTP_rev2.7_TN | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In the Test case of 5.1.13 of SRF#962, the 2nd sentence contains the word &quot;page bubble logic&quot; should be replaced with page connector &quot;logic&quot;.I have tested this case &amp; observed that in the &quot;page bubble logic&quot;, the description which configure in the ppoint configuration does not visible on the connecting sheet, but with the page connector works. (N, Thamaraiselvi May 31, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN CB (WCB)</p> <p><strong>Release Level:</strong> 3.5.0_U2 04-MAY-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch N, Thamaraiselvi</p> <p><strong>Entry Date:</strong> 2012-05-31T07:55:35-04:00</p> <p><strong>Modified Date:</strong> 2012-05-31T07:55:35-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8510 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73394
29637 | FINDING | Signal Diagram(cbViewer) gets crash inconsistently when loading of same controller is on any of the system. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | It is observed that<br>1.When signal diagram is tuned and other user is loading the same controller Signal Diagram application gets crashed sometimes.<br>2.When controller is loading on one system, and 7-8 signal diagrams are opened consecutively on other system of same controller, then also Signal Diagram application gets crashed sometimes.<br>3.Observations found while controllers 7-57 and 13 were loading. (Athavale, Samiradixit Jun 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Loading a controller appears to be unrelated to the signal diagram crashing. See Finding 8411.<br><br>Can you get it to crash with just one or two signal diagrams open? (Hutchison, Steven B. Jun 6, 2012)<br><br>Signal Diagram(cbViewer) is not getting crash if one or two signal diagrams are opened when loading of same controller is on any of the system. (Athavale, Samiradixit Aug 30, 2012)<br><br>This appears to be a duplicate of SDR 17864.<br>- (Hutchison, Steven B. Sep 11, 2012) <br> |  | 35 | FINDING | 8517 |  | FINDING | [10 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73408
29639 | FINDING | Same Ovation point can be assigned to more than one output of special function Algo in LADDER logic. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I am creating one control sheet (Sheet No #1001) in the control builder using ladder with two ADD (special function) Algo.<br>First ADD (special function) using REG1 Parameter -Register, REG2 Parameter -Register and RSLT Parameter &quot;Point Name (Ex .XYZ) then another ladder logic is made using ADD (special function) REG1 Parameter -Constant ,REG2 Parameter -Constant and RSLT Parameter &quot;Point Name (Ex.XYZ), both RSLT parameter are using same output point . It should gives error that point is already used .<br>Please refer attached screenshot (Kumar, Sudheer Jun 1, 2012) (Hutchison, Steven B. Jun 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Ladder support is provided for backward compatibility only. No plans to fix<br>- (Hutchison, Steven B. Jun 6, 2012)<br><br>Observation <br>1.Same Ovation point can be assigned to more than one output of special function Algo in LADDER logic. While, the ovation control builder, Same Ovation point can not be assigned to more than one output.Please refer atteched screendshot. (Kumar, Sudheer Jun 7, 2012)<br><br>I understand. No Plans To Fix.<br>- (Hutchison, Steven B. Jun 7, 2012) <br> |  | 35 | FINDING | 8519 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73412
29643 | FINDING | There is no action taken place on Releases the left mouse button over the poke or button. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1.Open the Ovation developer Studio(OVA3.5.0_U2).<br>2.Go to process diagram config window through (drop 182-&gt;configuration-&gt;process diagrams-&gt;process diagram config. window) the path.<br>3.Check the radio button of Execute Action On release is true on process diagram config. Window.<br>4.Downloaded the drop182 &amp; restarted the graphics.<br>5.Open graphics window but no action taken place for releases the left mouse button over the pokes program 3,diagram/group(2)etc.<br>Note:- I have checked above behavior for drop as well as system levels. (Prasad, Parmatma Jun 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Update to check the registry entry. (Spillane, Donal A. Aug 24, 2012)<br>Retested in Ov3.5.0_U7 release,the issue has been resolved. (Prasad, Parmatma Aug 27, 2012) <br> |  | 35 | FINDING | 8523 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73420
29647 | FINDING | MS field of Pri Ctlr doesn"t match with that of Backup Ctlr unless a second drop load of Pri Ctlr is performed | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While performing drop load of OCR400 controller, it was observed that the Modified Sequence (MS field of controller DU record in PI)of Primary Controller doesn&quot;t match with that of Backup controller. However, loading the Primary Controller once more will update its Modified sequence Number equal to that of Backup Controller. an example for Drop18/Drop68 is attached with this finding.<br>Please note that this doesn&quot;t happen always, but has been observed several times. (Lal, Ramesh Jun 4, 2012)<br><br>6/18/12: RL - Similar observation was made on OCR1100 Controller as well. (Lal, Ramesh Jun 18, 2012) |  |  |  | The affected area is in the Oracle database trigger named tr1_object_hierarchy, which is created during the creation of the Ovation database (and during an Oracle binary import using do_ptadmin_import) by the object_hierarchy.trig.sql. In addition, the Ovation database schema revision will be updated to a value of 37 to indicate this change. The application OvPtBridge.exe will handle the modification of the tr1_object_hierarchy trigger and the updating of the schema revision to 37 when executed during the installation of the Ovation software associated with this change. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | At the conclusion of a successful load operation to an Ovation drop, the MS field of the DU record on the target is updated to the maximum modified sequence value of all loadable objects at the time the load operation was initiated. This value is based on the maximum modified sequence of all of the drop&quot;s points, control sheets, holding registers -- and the drop object itself. <br><br>The Ovation database uses Oracle triggers to handle the updating of an object&quot;s modified sequence number. This occurs whenever an object&quot;s attributes are inserted, updated, or deleted. In addition, if an object is insert or deleted, the parent object&quot;s modified sequence is also updated. <br><br>As stated above, since the drop object is also included in the calculation of a drop&quot;s maximum modified sequence number, the insert or deletion of any objects which are direct children of the drop objects will also result in the updating of a drop&quot;s modified sequence number. This includes the internally created DDB objects which are direct children of the drops which originate those DDBs.<br><br>Since DDB objects can be implicitly created during a load of a drop (especially during the initial load of a drop), it is possible that the target will appear to be mismatched with respect to the database almost immediately after the load operation has completed. This can be cleared-up by an additional load operation (as observed above). (Swartz, Mark E. Aug 14, 2012) <br> The Oracle database trigger used during the updating of a parent object&quot;s modified sequence number during the insert or delete of an object will be changed to ignore the parent object update for the case of DDB Objects. (Swartz, Mark E. Aug 14, 2012)<br><br><br>8/30/2012: MS field updates correctly in 3.5_U7. Finding closed. (Lal, Ramesh Aug 30, 2012) |  | 35 | FINDING | 8527 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73428
29648 | FINDING | Ovation Simulation function doesn"t distinguish between Long point record and Deluxe point record | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Ovation Simulation application doesn&quot;t distinguish between Long Point record type and Deluxe Point record type.For example, an LA point can be simulated by a DA point, an LD point can be simulated by a DD point and so on. (Lal, Ramesh Jun 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is ok. As long as general record type matches (i.e. analog vs digital vs packed), this is valid. (Perdeus, Matthew Jun 19, 2012)<br><br>6/19/12:RL - O.K. Finding closed. (Lal, Ramesh Jun 19, 2012) <br> |  | 35 | FINDING | 8528 |  | FINDING | [10 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73430
29651 | FINDING | In ALARM TYPE column of Historical Review window nothing is displayed. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Its observed on Drop236 (Win7 SP1-64 bit ) its observed that opening Historical Review Window ,Navigate to Alarm tab, under Alarm type column nothing is displayed although in Live Alarm window , ALarm type is being displayed in History tab(Refer Alarm Type.JPG).<br>On investigation its found that Alarm type is also not displayed in Historical Point review.<br>For reference attached the Remote login steps. (Kumar, Shailendra Jun 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Check in next build U4 (Matreja Shyam Jun 29, 2012)<br>SK:Historical Review is now showing Alarm type, hence closed. (Kumar, Shailendra Aug 8, 2012) <br> |  | 35 | FINDING | 8531 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73436
29652 | FINDING | Blank Control sheet is showing on "Load Preview" window even after loading the drop. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1. Create a new control sheet, keep the sheet blank. compile, save &amp; load the drop.<br>Observation: The load preview window shows the new created control sheet name and its algorithm point on &quot;new objects&quot; tab. please see the snap shots attached named &quot;Blank sheet_Before loading&quot;. Click on &quot;Continue&quot; to complete the load. Loading completed successfully. No flag shown on the drop.<br>2. Now Again load the same drop .<br>Observation : The Load preview window is still showing the previous control sheet name in &quot;new objects&quot; tab, however the sheet&quot;s algo point is not showing, that is ok. Please see the attached file name &quot;Blank sheet_after loading&quot; .<br>Problem: The control sheet name also should not show on &quot;load preview&quot; window as it is already loaded and no flag on drop. <br>Note : If the control sheet is not blank, then the above problem is not appearing.<br>please find the remote login details as attached. (Joshi, Parmesh Jun 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please verify whether or not the &quot;blank sheet&quot; is actually loaded on the controller using Controller Diagnostics. Empty sheets, since they have no content, may not be actually loaded on the controller. If that is the case, then the behavior is exactly as expected. (Swartz, Mark E. Jun 5, 2012)<br><br>PJ: 06th June: Checked in controller disgnostics, found that the blank sheet is actually not loaded in the controller (not found).It is understood that if a sheet is kept blank then it will not actually loaded on controller (even after No flag is shown in developer studio in the corresponding controller), because of that the load preview window is showing the sheet. <br><br>But if an existing control sheet is made blank (which was not blank earlier), then during loading, the controller load preview will show the sheet on modify tab and after loading the control sheet not found on diagnostics window. In this case, if we load the controller again, then load preview window should show that control sheet,because the same sheet is not found on controller diagnostics, if there is interface between load preview and controller diagnostics. (Joshi, Parmesh Jun 6, 2012) <br> This behavior is as expected and designed. Please note that it makes no sense (nor is it proper) to have a control sheet which is empty of content. The sheet shows up in the preview (as it should) because it exists in the database and presumably represents &quot;work in progress&quot;. The behavior of an empty sheet not being loaded on the controller is as expected and per design. The sheet continues to show in the preview (even after a previous complete load) because it still is in the database and not in the target. (Swartz, Mark E. Jun 6, 2012)<br><br>PJ: In this case will the blank control sheet can be seen on signal diagram, as the blank control sheet is showing on signal diagram after loading. (Joshi, Parmesh Jun 8, 2012)<br><br>The blank sheet is distributed to the MMIs. Therefore, it is visible in the signal diagram viewer. (Swartz, Mark E. Jun 8, 2012)<br>As per developer comments and explanation, the behaviour is as expected, so the SVTP should be modify accordingly mentioning a note on step-5.1.8 that , newly created BLANK control sheet will not load to controller and will always show on load preview window. The same note should also be mention on DIR&quot;s. (Joshi, Parmesh Jun 12, 2012)<br><br>The existance of BLANK control sheets in the system shuold only be considered to be a temporary condition. It is obviously not proper. The fact that the Preview window draws the user&quot;s attention to this fact is a feature (not a bug) and not necessarily cause for identification in the DIR. However, if Validation feels the need to include it, they should change the state of this Finding to &quot;DIR&quot;. (Swartz, Mark E. Jun 12, 2012)<br>change the status to DIR to be added there and accordingly SVTP need to modify. (Joshi, Parmesh Jun 15, 2012)<br><br>IC 9/27/12 - since this is expected behavior, this finding will serve as the documention of this item. Closing finding as WIW. (Capani, Nooch Sep 27, 2012) |  | 35 | FINDING | 8532 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73438
29655 | FINDING | Vcoordinator does not start after VCH upgrade to U3 | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Vcoordinator does not start after VCH drop upgrade to U3.<br>---<br>To start the VCH and before downloading the VCs we must:<br>a. Reset the IP &amp; Subnet in the C:\Ovation\OvationVirtual\vxsimnetd.conf file<br>b. In cmdtool run: vcoordinator -I<br>c. Reboot (Benzvi, Mati Jun 5, 2012) |  |  |  | After installation process of Ovation and vxsim, vcoordinator service should be running. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Will be corrected with new installation file and procedure in U4. (Perdeus, Matthew Jun 19, 2012)<br>---<br>msb - Install/Update procedure updated in U4:<br> Vxsim Installation-32b in 3.5.0_U4.txt<br> Vxsim Installation-64b in 3.5.0_U4.txt (Benzvi, Mati Jul 23, 2012) <br> |  | 35 | FINDING | 8535 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73444
29656 | FINDING | VCs cannot be "Stop"ed by the VcoordManager program | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | VCs cannot be &quot;Stop&quot;ed by the VcoordManager program<br>missing SimApi.exe program (Benzvi, Mati Jun 5, 2012) |  |  |  | Test &quot;stop&quot; and &quot;start&quot; functionality of new vcoordmanager gui. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | There was an issue on the build machine where the &quot;staging&quot; directory did not exist and some files were not getting copied properly. They were getting copied to a file instead of to a directory. The incorrect file was deleted, causing the directory to be created on the next make_ishield run. (Perdeus, Matthew Jun 6, 2012)<br>---<br>msb - Ok in 3.5.0_U4<br> VCH - drop127<br> VC - 142 -&gt; Stop, Start<br> VC - 143 -&gt; Stop, Start (Benzvi, Mati Jul 23, 2012) <br> |  | 35 | FINDING | 8536 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73446
29657 | FINDING | In signal Diagram , summary diagram is enable in Point menu even diagram is nt configured. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In signal Diagram , summary diagram is enable in Point menu even diagram is nt configured.If summary diagram is not configured with point then diagram should be diable in point menu, every where it&quot;s behaving correct except once browsing through signal diagram.Pleasefind attached for clarity. (Singh, Ghanshyam Jun 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | No Plans to Fix. - (Hutchison, Steven B. Jun 6, 2012)<br><br>GS(18/7/2012)-As developer and Nooch&quot;s comment, finding closed. (Singh, Ghanshyam Jul 18, 2012) <br> |  | 35 | FINDING | 8537 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73448
29658 | FINDING | Graphics abitrator is not running when "go to refrence" intiated multiple times from PI. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Graphics abitrator is not running when &quot;go to refrence&quot; intiated multimple time/mishandled from PI.Steps to be followed to recreate the issue.<br>1.Open the PI and select a point which is used atleast one signal diagram.<br>2.Open a where used button on PI,see attached picture for clarity.<br>3.In window of &quot;where used&quot; details click on &quot;go to refrence&quot; multipule/mishandled time irespective of clicked diagram opened or not.<br>After several click &quot;Graphics abitrator is not running&quot; message comes and graphics and alarm window doesn&quot;t not open untill repective drop restarts. (Singh, Ghanshyam Jun 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I&quot;ve followed your procedure and cannot duplicate the problem. Is there more to this? (Burgoon, Frank J. Jun 6, 2012)<br><br>GS(07/12/2012):It&quot;s difficult to re create because for this you have to multiple times click on the &quot;where used&quot; button on PI . Don&quot;t stop click even you find the where used diagram/control sheet .Hope you will able to recreate. (Singh, Ghanshyam Jul 13, 2012)<br><br>I have yet again failed to reproduce this behavior. Perhaps this has been fixed since U2. Perhaps there is a sequence of steps, or maybe a hardware configuration that still reproduces this problem. (Burgoon, Frank J. Aug 28, 2012)<br><br>GS(01/10/2012): In present build U9, this issue could not be recreated. Perhaps system is stable, so that problem is no more persisting . Hence finding is Closed. (Singh, Ghanshyam Oct 1, 2012) <br> |  | 35 | FINDING | 8538 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73450
29659 | FINDING | After collecting the information in "system information collection",window is not able to give a print log command. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | After collecting the information in &quot;system information collection&quot;,window is not able to give a print log command.There is a button for print log command.Before and during collection of information the &quot;print log&quot; button is diable.After collection of information ,it is enable but not wroking. (Singh, Ghanshyam Jun 6, 2012)<br><br>GS: In present build this issue is already found fixed. Kindly change the action to Lib , so that I can close the finding. (Singh, Ghanshyam Oct 1, 2012)<br>--<br>msb - Closed (GS: Fixed in present build) (Benzvi, Mati Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8539 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73452
29660 | FINDING | In "Review collected information" window, "print report" button is not working. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In &quot;Review collected information&quot; window, &quot;Print Report&quot; button is not working.After collecting the information in &quot;system information collection&quot; go to &quot;Next&quot; button and reach to &quot;Review collected information&quot; .In &quot;Review collected information&quot; window, there is a &quot;print report&quot; button which is working after clicking on it. (Singh, Ghanshyam Jun 6, 2012)<br><br>GS:In present build this issue is already found fixed. Kindly change the action to Lib , so that I can close the finding. (Singh, Ghanshyam Oct 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | --<br>msb - Closed (GS: Fixed in present build) (Benzvi, Mati Oct 31, 2012) <br> |  | 35 | FINDING | 8540 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73454
29661 | FINDING | Test case 5.1.6 of 3.5_CONTROL_FUNCTIONS_SVTP_rev2.3_XX needs modification | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Operation through Membrane Keybord for changing auto/manual mode, increase/decrease setpoint/output in Signal Diagram is not supported. Therefore,Test case 5.1.6 of 3.5_CONTROL_FUNCTIONS_SVTP_rev2.3_XX should be made NA. (Khanna, Anant Jun 7, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Control Functions (CF)</p> <p><strong>Release Level:</strong> 3.5.0_U2</p> <p><strong>Originator:</strong> Khanna, Anant</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Khanna, Anant</p> <p><strong>Entry Date:</strong> 2012-06-07T05:17:22-04:00</p> <p><strong>Modified Date:</strong> 2012-06-07T05:17:22-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8541 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73455
29662 | FINDING | In 3.5_Win_Basic_Security_svtp_rev1.3_SDK Title needs to be modified under section 5.6.7 and 5.6.8 | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In 3.5_Win_Basic_Security_svtp_rev1.3_SDK under section 5.6.7 and 5.6.8 Title needs to be<br>interchanged, 5.6.7 Title should be User Right Assignments Policies and 5.6.8 Title should be<br>Security Option Policies. (Kumar, Sudheer Jun 7, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Documentation (DOC)</p> <p><strong>Subproduct:</strong> Developer Studio (DS)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Kumar, Sudheer</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Kumar, Sudheer</p> <p><strong>Entry Date:</strong> 2012-06-07T06:33:03-04:00</p> <p><strong>Modified Date:</strong> 2012-06-26T16:28:37-04:00</p> | 0 |  | Ovation for Windows/General/Software | LC 06/26/2012: This is for a fix to a test procedure, not a user guide. Assigning this to Nooch. (Casteel, Linda Jun 26, 2012) <br> |  | 35 | FINDING | 8542 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73456
29663 | FINDING | 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_SDK needs to be modified under Description. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_SDK needs to be modified under description: To test this functionality, perform the listed tests- Page on 17<br><br>1) Test 5.6.1 to 5.6.7 apply both Users and Computer Polices modified to Test 5.6.1 to 5.6.6 apply both Users and Computers Polices.<br>2) Test 5.6.8 to 5.6.11 apply only to computers policies modified to Test 5.6.7 to 5.6.8 apply only to computers policies (Kumar, Sudheer Jun 7, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Documentation (DOC)</p> <p><strong>Subproduct:</strong> Developer Studio (DS)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Kumar, Sudheer</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Kumar, Sudheer</p> <p><strong>Entry Date:</strong> 2012-06-07T06:44:53-04:00</p> <p><strong>Modified Date:</strong> 2012-06-26T16:27:43-04:00</p> | 0 |  | Ovation for Windows/General/Software | LC 06/26/2012: This is a test procedure fix, not a user guide fix. Assigning this to Nooch. (Casteel, Linda Jun 26, 2012) <br> |  | 35 | FINDING | 8543 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73457
29664 | FINDING | context menu "open item in control sheet" is not working for the point which is already exist in control sheet. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | step to reproduce:<br>1. Creat a new point in a existing control sheet, complie, load and save the sheet.<br>2. Load the controller, the load preview will show the new point on new object tab.<br>3. Select the point on load preview window, Right click and click on &quot;open item in control sheet&quot;<br>observation : a pop up appears showing that &quot;unable to find point in sheet&quot;, though the point is available on the sheet. (Joshi, Parmesh Jun 7, 2012) |  |  |  | The affected area is in the software which attempts to locate a point name reference in the set of control sheets within that particular Unit. When the search is performed from a Load Preview window, the location should be in the area where control sheets are stored prior to loading on the target. Since this software is also used to view point name references in control sheets during a reconcile operation, this &quot;function&quot; is also affected. In addition to testing the scenario described by this Finding, tests must also be performed to ensure that viewing point references in Control Sheets from a Reconcile Results window continues to work properly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Is the control sheet simply referencing the Analog point (i.e., using the point as an input only) or is it driving the value of the Analog point? Please test a situation where an Analog point is updated (i.e., the value is driven) by a control sheet. (Swartz, Mark E. Jun 7, 2012)<br><br>PJ, 08th June-12: The point used in control sheets are of both type, as an input point and also driving the value to analog point. The case is as follow:<br><br>1. In an existing control sheet, an summation (SUM) algorithm is added and two input points and one output point (all new) are connected to the algorithm. The new points are created, by &quot;Create undefined points&quot;.compile and saved the control sheet.<br>2. Now load the controller, the &quot;Load preview window will show the 3 new analog points and one algorithm point (SUM) in &quot;New objects&quot; tab.<br>3. Right click on any of above points (analog &amp; algorithm), and click on &quot;open item in control sheet&quot; , the same message is coming as in problem i.e. &quot;unable to find point in sheet&quot;. (Joshi, Parmesh Jun 8, 2012) <br> The software which opens a Control Sheet view from the Preview window is common to the software which opens a Control Sheet view from a Reconcile Results window. Unfortunately, both methods are looking at the control sheets in the same directory. In the case of Reconcile, the user must be shown a Control Sheet view which is consistent with the &quot;currently loaded&quot; control sheet. In the case of Preview, the user must be shown a Control Sheet view which has not yet been loaded (i.e., they are still on the Database Server). <br><br>This explains why these points which were newly added to the control sheets were not found -- those modified control sheets have not been loaded yet.<br><br>The software will be changed to handle the searching of a Point Name in different control sheet directories, based on whether the user is searching from a Load Preview window or a Reconcile Results window. (Swartz, Mark E. Aug 17, 2012)<br><br>PJ: 24th Aug&quot;12: checked in ov 3.5.0_U7, Found that if the control sheet is driving a value of analog poing (Output point) then the control sheet open for that point But for the point which is used as an input is not opening control sheet.Want to know is this the correct behaviour for input points? (Joshi, Parmesh Aug 24, 2012)<br>This is expected behavior. The Open item in control sheet is designed to open one control sheet instance (whether from Load Preview or Reconcile). A user defined point can be referenced on many sheets but its value can be driven by only one sheet. The &quot;Open item in control sheet&quot; will only show a named point in a control sheet if its value is driven by the a control sheet (i.e., only &quot;outputs&quot;). (Swartz, Mark E. Aug 24, 2012)<br><br>Understood the concept , Hence Closed. (Joshi, Parmesh Aug 26, 2012) |  | 35 | FINDING | 8544 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73459
29665 | FINDING | "Help" Button of Load preview is not functioning. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The &quot;Help&quot; button on load preview is not functioning, not going to any link after clicking. <br>Seems to be off. (Joshi, Parmesh Jun 7, 2012) |  |  |  | The affected area is in the Ovation Developer Studio load preview dialog. Code has been enabled for the Help button. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Help button will be enabled. (Swartz, Mark E. Jun 12, 2012)<br><br> PJ: 20 July 2012: Checked with OV 3.5.0_U4, The Help Button is now enabled. Found OK. Hence Closed. (Joshi, Parmesh Jul 20, 2012) <br> |  | 35 | FINDING | 8545 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73461
29670 | FINDING | A "Cleared" Non redundant controller drop is showing blank "Load preview" window while loading. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When an non redundant controller drop (drop13) is cleared and then loaded then the load preview window should show all the control sheets and points on &quot;new objects&quot; window and all holding registers and received points (if defined earlier) on corresponding tabs, But the load preview window is showing blank.<br>Note: The same is observed on redundant controller drop and EWS drops , those are working fine. i.e. load preview window showing all the points and control sheets, not blank.<br>please find attached remote login details. (Joshi, Parmesh Jun 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please independently verify that the &quot;Cleared&quot; non-redundant controller which is referenced in this Finding (drop13) is indeed cleared. The Controller Diagnostics application should be used to view the set of control sheets and Ovation points (originated and received) currently contained in the target. If there are control sheets and points other than the DU point, then drop13 really was not cleared and the &quot;Load Preview&quot; window is accurately reporting the comparison between the target contents and the database configuration. (Swartz, Mark E. Jun 8, 2012)<br><br>PJ, 12th June: Verified that the non redundant controller (drop13) is actually cleared by observing from controller diagnostics window. The disgnostics do not show any points and control sheets except DU , drop point after clearing. At this stage if load is perform, the load preview window is blank. (Joshi, Parmesh Jun 12, 2012)<br><br>This problem is a direct result of the unprintable control characters contained in one of the control sheets in this controller (drop13). Specifically, it is the same sheet which was identified in Finding 8485. The problem will be resolved when the attributes for this control sheet are corrected.<br><br>Please close this finding and track the issue via Finding 8485. (Swartz, Mark E. Jun 13, 2012)<br><br>I could not simulate the problem with finding 8485. The F#8485 is related to greek letters coming in control sheets name. This is not related to drop13 (non redundant controller). please specify the link of this finding with F#8485. (Joshi, Parmesh Jun 15, 2012) <br> This issue IS directly related to F#8485, which produced &quot;greek letters&quot; in control sheet names. Sheet 100 in drop13 contains a contrl character in its name. This INVALID character is preventing the preview window from showing its data. The fix for F#8485 will prevent &quot;greek letters&quot; from getting in the database in the future, but it will not remove those characters if they are already in the database. Please correct the invalid sheet name characters. The issue with this finding has nothing to do with the Preview Function&quot;s inability to show a cleared non-redundant controller. It has to do with bogus data in the database produced by other software and tracked by F#8485. No changes are required for Load Preview, hence NAR. However, Validator is required to change/fix the &quot;greek letters&quot; associated with F#8485. (Swartz, Mark E. Jun 15, 2012)<br><br>The Finding F#8485 has been fixed in U7 build. But this problem is still existing in the same build. Still a cleared non redundant controller is showing &quot;No results to preview&quot; pop up window. (Joshi, Parmesh Sep 14, 2012)<br>As stated previously, this controller (drop13) still contains a sheet (0x005B), number 100 in control task 2 which contains invalid characters in the sheet name. Validator is still required to change/fix the &quot;greek letters&quot; associated with F#8485. (Swartz, Mark E. Sep 14, 2012)<br>Checked after deleting all invalid char. sheets and found ok. Hence Closed. (Joshi, Parmesh Sep 21, 2012) |  | 35 | FINDING | 8550 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73471
29671 | FINDING | RUNT (Total Run Time) of SAMPLER algo does not get updated properly in Properties Summary of Signal Diagram. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.Sampler algorithm&gt;Signal Diagram&gt; Properties Summary&gt;Base&gt;Second is selected.<br>2.Algorithm Control &gt;Start so Run in Signal diagram is getting updated second by second.<br>3.Run is updating correctly in runtime sampler algo in Signal diagram and in Algorithm summary, but in Properties summary RUNT is not updating properly. It is lagging by 5 seconds. Please find the attached snapshot.<br>4.Control sheet is tested with Controller 13 &amp; 7/57. Control sheet is prepared in Controller Task3. (Athavale, Samiradixit Jun 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works As Designed - Properties Summary Updates at a slower frequency to minimize controller impact.<br><br>As per developer&quot;s comment,finding is closed. (Athavale, Samiradixit Jul 12, 2012) <br> |  | 35 | FINDING | 8551 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73473
29674 | FINDING | SDR 18264 [A change in a SIS-Calc isn"t marked as a change within the Ovation Developer Studio] Failed. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | When an LSCALC program is changed and the sheet is saved, the logic solver does not show the status flag. Hence, SDR failed the validation. (Pandey, Vijay Jun 12, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Safety Instrumented System (SIS)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Swartz, Mark E. Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2012-06-12T00:20:59-04:00</p> <p><strong>Modified Date:</strong> 2012-06-12T07:39:34-04:00</p> | 0 |  | Ovation for Windows/General/Software | Transferring to same responsible engineer as the referenced SDR (18264). (Swartz, Mark E. Jun 12, 2012) <br> |  | 35 | FINDING | 8554 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73478
29675 | FINDING | loading of drop while the same drop"s 2 load preview window opens(from different EWS) hanging the control builder. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If in one workstation (say EWS1) a blank drop&quot;s load preview window (controller drop) opened and from another workstation (say EWS2), perform chages in the same drop (e.g. create a new point)and start loading (from EWS2), the load preview window will open and show the new created point. Now perform one by one as follows:<br>a)start loading from EWS1(by clicking on &quot;Continue&quot; tab),then the load will be aborted, showing popups. This is ok.<br><br>b) start loading from EWS2 (by clicking on &quot;Continue&quot; tab),then the loading stuck on &quot;Processing internally reference point&quot;. This will consequently hanging of control builder operation of all the EWS e.g. new control sheet is not creating. <br>Workaround: Start &quot;Load&quot; from EWS1 (by clicking on &quot;Continue&quot; tab),this will show popup mentioning &quot;load aborted&quot; and load preview window close. after that, loading EWS2 is completed and control bulilder functionality reverts to normal.<br><br>note: Same problem (of case b) is not appearing if loading of drop is done from EWS2 without performing changes on the drop i.e. both drop load preview windows are blank.<br>please find attached the remote login details. (Joshi, Parmesh Jun 12, 2012) (Swartz, Mark E. Jun 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | It is not valid to perform more than one load operation at a time to a target drop. (Swartz, Mark E. Jun 12, 2012)<br><br>It is agreed that we should not perform more than one load operation at a time to a target drop and case a) is showing the message as load aborted message for the same. That is ok. But for case b), the developer studio getting hang.<br><br>If a user perform case b) then developer studio studio should not hang , instead should display the same message as in case a) (Load aborted). (Joshi, Parmesh Jun 15, 2012)<br><br>The Ovation Engineering Tools was not designed to detect and handle multiple (and simultaneous/concurrent) inadvertent loading operations to a single target drop. Case b) represents a situation where this was not detected. This is the way it works. Good engineering practices should be utilized when performing load operation to process control computers. If enhancements to the design are necessary, a Catagory 5 SDR could be generated. (Swartz, Mark E. Jun 15, 2012) <br> IC 7/16/12 - closed as WIW, no plans to change. (Capani, Nooch Jul 16, 2012) |  | 35 | FINDING | 8555 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73480
29676 | FINDING | "Checkbox" function is not working properly in Ovation 3.5.0. | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0 Developer Studio, if we search a point by name and after searching when the Object list comes, the Object comes with a &quot;Checkbox&quot; leftside of it. Trying to left mouse click over the &quot;Checkbox&quot; does not select the item. The item can be selected only by left mouse click over the item name (object).<br>Trying to uncheck the &quot;Checkbox&quot; also does not work. The item can be deselected only by pressing Ctrl+left mouse click over the item name (object).<br>So, here the function of the Checkbox is not working. Snapshot is attached for reference. (Mitra, Sambuddha Jun 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I believe this behavior is not new to Ovatin 3.5.0 and have been this way in the past. Checkbox is just an indication of what has been selected for furthur action like opening the objects. (Thirunavukkarasu, Utthandi Jul 9, 2012)<br><br>Understand the Checkbox function. So, closing the finding. (Mitra, Sambuddha Jul 10, 2012) <br> |  | 35 | FINDING | 8556 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73482
29677 | FINDING | SVTP "3.5_SRF1250_ SVTP_rev1.3_PJ" need modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | SVTP 3.5_SRF1250_ SVTP_rev1.3_PJ&quot; test case 5.1.9: A note should be mentionaed that if a drop is cleared and loaded and its DU point will always show on &quot;Modified tabs&quot;. (Joshi, Parmesh Jun 12, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-06-12T07:37:11-04:00</p> <p><strong>Modified Date:</strong> 2012-06-12T07:37:11-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8557 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73483
29678 | FINDING | Style Editor -&gt Line Properties -&gt Stroke width is non functional for Dashed Line type. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | It is observed that ,Stroke width for selection of Dashed Line does not change, while for all other lines it is working fine. (Sachan, Pallavi Jun 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot Duplicate. - Tested line style in both styles and entities. Worked as Expected.<br>- (Hutchison, Steven B. Jun 13, 2012)<br><br>Kindly find the attached &quot;F_8558_MIS.jpeg&quot; , this is observed for all shapes and line styles. Both in Control sheet canvas and create Algorithm Symbol canvas. (Sachan, Pallavi Jun 14, 2012)<br><br>Fixed - (Hutchison, Steven B. Jun 14, 2012) <br> Found Fixed in U4. Hence Closed. (Sachan, Pallavi Jul 18, 2012) |  | 35 | FINDING | 8558 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73485
29679 | FINDING | cbEditor crashes while a control macro is editted and saved on control sheet. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps followed are: 1.Create a control macro. Create a symbol for the same. Save.<br>2.Use the macro in a control sheet, now EDIT macro and SAVE. Close the macro.<br>3.Return on same sheet and click on macro editted.<br>This crashes the cbEditor.exe. (Sachan, Pallavi Jun 13, 2012)<br><br>Kindly find the cbEditor crash with edit macro.jpeg attached. (Sachan, Pallavi Jun 13, 2012) (Sachan, Pallavi Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I am unable to recreate this crash. Please place the mini-dump on the share drive.<br><br>See the following links to configure your system to collect a mini-dump.<br><br> http://msdn.microsoft.com/en-us/library/windows/desktop/bb787181%28v=vs.85%29.aspx (Hutchison, Steven B. Jun 13, 2012)<br><br>Using details from 3.3.1, CrashDumps.reg was used. Kindly find attached F_8559_DMP.zip file for dump file. (Sachan, Pallavi Jun 14, 2012)<br><br>Please send me the ControlMacros directory and the SVG file that caused the issue.<br>- (Hutchison, Steven B. Jun 14, 2012)<br><br>Kindly find one of the control sheets as &lt;Control Sheet F8559.zip&gt; and the Control Macro directory as &lt;ControlMacros.zip&gt; attached. <br>Also note that this is observed on 32-bit OS machines on &lt;Net#7 and Net#8&gt; both networks in Val Lab. (Sachan, Pallavi Jun 19, 2012)<br><br>Cannot Duplicate - Please provide more information as to how the macro was edited.<br>- (Hutchison, Steven B. Aug 15, 2012) <br> The above steps are repeated, but this issue is not observed in current build. Hence Finding is Closed. (Sachan, Pallavi Sep 7, 2012) |  | 35 | FINDING | 8559 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73487
29680 | FINDING | SVTP "3.5_SRF1250_ SVTP_rev1.3_PJ" need to be modify. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In SVTP &quot;3.5_SRF1250_ SVTP_rev1.3_PJ&quot; there is nowhere mentioned that the &quot;Load Preview&quot; window will me having context menu items while Right clicking on any object shown in load preview window.<br>A seperate point test (after test 5.1.9) need to be added on the SVTP. (Joshi, Parmesh Jun 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-06-13T06:10:22-04:00</p> <p><strong>Modified Date:</strong> 2012-06-13T06:26:41-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8560 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73488
29681 | FINDING | SVTP "3.5_SRF1250_ SVTP_rev1.3_PJ" need modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In SVTP &quot;3.5_SRF1250_ SVTP_rev1.3_PJ&quot; test case 5.1.7 &quot;Click OK on ¿Load Preview¿ window and verify that the drop is loaded as normal.&quot; should me modiy as &quot;Click on &quot;Continue&quot; on ¿Load Preview¿ window and verify that the drop is loaded as normal.&quot; (Joshi, Parmesh Jun 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-06-13T06:13:29-04:00</p> <p><strong>Modified Date:</strong> 2012-06-13T06:13:29-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8561 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73489
29682 | FINDING | "Load preview" window is not able to open holding register from context menu. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | When a holding register is created , it will show on &quot;Modified Objects&quot; tab of &quot;Load Preview&quot; window while loading.<br>Right Clicking on the holding register on &quot;Load Preview&quot; window, shows the &quot;Open item&quot; and &quot;Open item in control sheet&quot; options in context menu.<br>Both the options are greyed out i.e. the holding register window is not able to open from here. (Joshi, Parmesh Jun 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Swartz, Mark E. Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-06-13T06:35:25-04:00</p> <p><strong>Modified Date:</strong> 2012-06-15T09:00:38-04:00</p> | 0 |  | Ovation for Windows/General/Software | Way it works. There are no plans to support the opening of modified Holding Registers from the Load Preview window. (Swartz, Mark E. Jun 13, 2012)<br><br>As per developer comments there is no plan to support this functionality. Hence SVTP should be modify mentioning a note that &quot; Holding registers can not be open from load preview window&quot;. Moved finding against SVTP. (Joshi, Parmesh Jun 15, 2012) <br> |  | 35 | FINDING | 8562 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73490
29683 | FINDING | Save As utility for Macro does not overwrite existing Macro. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Create a Macro. Go to File -&gt; Save As, click on existing name. Confirm SaveAs window appears, click on Yes, this gives Invalid Macro name error which says &quot;Cannot redefine a Standard algorithm with a control Macro.<br>User should be allowed to overwrite if required. (Sachan, Pallavi Jun 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. Jun 13, 2012) <br> Found Fixed in U4. Hence Closed. (Sachan, Pallavi Jul 18, 2012) |  | 35 | FINDING | 8563 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73492
29685 | FINDING | Historical Review does not work for OPH point Group. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In studio defined point group through right click EDB group.Added those points in the group which are historically collected.<br>Downloaded/Rebooted the workstation, then opened Historical Review window and did Historical review with Selection of OPH group(refer attachment) with all filters checked.The result was blank window.<br>If Historical Review is done for individaul points of OPH group it returns value coorectly. (Kumar, Shailendra Jun 13, 2012)<br><br>Above steps were done on drop236 (Win7 SP1-64 bit ) machine and remote login steps are attached. (Kumar, Shailendra Jun 13, 2012) |  |  |  | please test it again | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SK:Ok in U9 ,hence closed. (Kumar, Shailendra Oct 23, 2012) <br> |  | 35 | FINDING | 8565 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73496
29687 | FINDING | Multinet point"s trend is not coming properly while opening trend from graphic. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Open Graphic display which consist of one multinet points (for example,open graphic display of FE350, NET#8 which having a point of network FE241 NET#4.)and open the trend of the point from right click menu.<br>Observation: The trend diaplay showing incorrect qualified point name. Showing point name as &lt;Point name&gt;@FE350. It should show as &lt;point name&gt;@FE241. Consequently the trend status is showing as &quot;Point not found&quot; <br>please find attached snap shots &quot; multinet trend&quot; and &quot;remote login details&quot;. <br>Note: Checked on ovation lower version (OV 3.3.1), here the problem does not exist. (Joshi, Parmesh Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SPD_get_point_info was found to be returning truncated point name.<br>Changed code to use SPD_get_name instead of SPD_get_point_info so that fully qualified point name is acquired. (Bargaje Prashant Jun 18, 2012)<br><br>Checked with ov 3.5.0_U4, Found ok., Hence closed. (Joshi, Parmesh Jul 20, 2012) <br> |  | 35 | FINDING | 8567 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Contento, James AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Spillane, Donal AUTOSOL PWS PITT | [6 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73500
29688 | FINDING | OCB points show "ACKNOWLEDGED" even when alarm is not configured for that. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation Point Information, under Alarm tab, Parameter of &quot;Alarm Acknowledged Status&quot; of OCB points show Value &quot;ACKNOWLEDGED&quot; even when alarm is not configured for that point.<br>For reference, please see the attached snapshot. (Mitra, Sambuddha Jun 14, 2012)<br><br>This issue can be seen by remote login to Ov.3.5.0 drop250 under controller drop33/83 Task4 sheet &quot;sm_test_117&quot;. Remote login details is attached. (Mitra, Sambuddha Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The &quot;Alarm Acknowledged Status&quot; entry in PI only reflects the state of bit 5 of the 1W field. All Ovation points behave the same way. (Burgoon, Frank J. Jun 14, 2012)<br><br>Understand this. Hence, closing the finding. (Mitra, Sambuddha Jul 10, 2012) <br> |  | 35 | FINDING | 8568 |  | FINDING | [10 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73502
29689 | FINDING | A new OCR1100 cannot boot (missing vxWorks file). | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The file vxWorks.ocr1100 is missing from C:\tftpboot. This prevents a new OCR1100 from booting. (Brown, Sean Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected installshield. (Pingree, Douglas K. Jul 6, 2012) <br> |  | 35 | FINDING | 8569 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73504
29690 | FINDING | Engineering Audit entries cannot be archived. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When an Archive of Engineering Audit entries is performed in Audit Viewer, the following error message appears:<br><br>¦&lt;OvPtAudit.cpp:1377&gt;¦[OvPtApi]: (Audit select structure not initialized)<br><br>When OK is selected, another error window appears:<br><br>Encountered an improper argument.<br><br>The archive was attempted because the Engineering Audit tablespace is full. Since engineering functions cannot be performed under this condition, the Engineering Audit feature must be turned off. (Brown, Sean Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This particular issue could not be duplicated on development systems. Later attempts to duplicate this particular issue on the Validation system was also unsuccessful. Development will investigate. (Swartz, Mark E. Jun 15, 2012)<br><br>The messages appeared again during multiple archiving attempts, but not always. The number of entries to be archived may be a factor. (Brown, Sean Jun 15, 2012)<br><br>Cannot duplicate on development system. Can the state be changed to Monitoring? (Swartz, Mark E. Aug 2, 2012)<br><br>Issue has not been observed since last finding update; closing. (Brown, Sean Sep 26, 2012) <br> |  | 35 | FINDING | 8570 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73506
29691 | FINDING | OCR1100: Control Synchronization is not working. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR1100 Controller 18/68 (WALT) is configured to use the dedicated c2b cable. Bit 8 of the FF field (for both controllers) is not set, and the Error Log shows multiple instances of<br><br>LINK STATUS CHANGED : PORT N4 DOWN<br>LINK STATUS CHANGED : PORT N4 UP<br><br>for both controllers. Opening a telnet session to the controllers to look for more information could not be performed. (Brown, Sean Jun 14, 2012)<br><br>Other messages repeated for both controllers in the Error Log:<br><br>Interface Status : Interface N2: Speed=100Mbs Duplex=Half Duplex<br>Interface Status : Interface N4: Speed=1Gb Duplex=Full Duplex (Brown, Sean Jun 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected duplex issue. (Pingree, Douglas K. Jul 10, 2012) <br> |  | 35 | FINDING | 8571 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73508
29692 | FINDING | Recoincile window pops up error message instead of getting closed | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Signal Diagram open a control sheet and make some changes in the tuning parameters of any algorithm,e.g. PID.Now in the Developer Studio select the Controller drop which contains that sheet. Right click and select Reconcile.Select the drop to reconcile.In the Reconcile window select the sheet and click Apply.The differences between Database and Controller get reconciled. Now press OK. It doesn&quot;t close the Reconcile window rather pops up the message &quot;Nothing selected&quot;. Since there is nothing to select, it should close the window. Please refer the attached snapshot. (Lal, Ramesh Jun 14, 2012)<br><br>9/20/12:RL - Finding closed based on Dev&quot;s explanation. (Lal, Ramesh Sep 20, 2012) |  |  |  | If OK were to be pressed, and window goes away, it might imply some action was taken, when in fact none was taken. Same error message will occur if the APPLY button is pressed, so the message is correct. The OK button is the same as pressing, APPLY and then CANCEL... bottom line...works fine the way it is. - ssp | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8572 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73510
29693 | FINDING | It is possible to configure automatic proof test for simplex Logic Solver | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Logic Solver&quot;s properties under &quot;Proof Testing Tab&quot; it is possible to check &quot;Enable automatic proof test to run at reminder time&quot; checkbox even if LS is configured as simplex. According to documentation it shouldn&quot;t be possible. (Czak, Jakub Jun 15, 2012)<br><br>If simplex SLS is configured to perform automatic prooftest, only the alarm will be given when the time of the prooftest pass. There is no threat for simplex SLS to start prooftesting while it normal work. Therefor possibility of checking automatic prooftesting in Developer Studio should be blocked.<br>Allowing prooftest configuration for simplex SLS is missleading for the user.<br>Reassigning. (Raciborski, Mikolaj Apr 3, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8573 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73512
29694 | FINDING | Audit Viewer timestamps are off by 1 hour. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Engineering Audit entry timestamps are 1 hour behind in Audit Viewer. This means the search dates/times must be adjusted to retrieve data as well. (Brown, Sean Jun 15, 2012) |  |  |  | The affected area is in the software responsible for converting the retrieved timestamps from the database (which are stored in GMT) to local time for display to the user. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | It appears that the entries in the database are being correctly stored in UTC time (conversion from local time to UTC seems to be correct during storage). Development will investigate the retrieval logic. (Swartz, Mark E. Jun 15, 2012)<br>The logic used to calculate the timezone bias behaves differently with the Ovation 3.5.0 release due to the change in compilers. The logic has been modified accordingly. (Swartz, Mark E. Aug 8, 2012)<br><br>Resolved in U6; closing. (Brown, Sean Aug 17, 2012) <br> |  | 35 | FINDING | 8574 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73514
29695 | FINDING | Archiving more than 100,000 Engineering Audit entries results in data being permanently lost. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When Engineering Audit entries are archived from Audit Viewer, only the PART0 XML file is created before the entries are removed from the database. (Brown, Sean Jun 15, 2012)<br><br>Failed in U4, although the original problem has been improved. More than 100000 entries are archived, but apparently only in multiples of 100000. For example, 744158 entries were archived. Audit Viewer reported that 744158 entries were archived to 7 files and the Audit entry shows that 744158 entries were deleted. The files contain a total of 700000 entries, which means that 44158 entries were not archived before being deleted. (Brown, Sean Jul 18, 2012) |  |  |  | The affected area is in the software responsible for retrieving the Engineering Tools audit entries. Specifically, the query connection will be closed down explicitly after the completion of either a normal viewer retrieval or after the completion of the entire set of entries during archive. In addition, the logic associated with the handling of multiple archive files has been changed. Testing must include the archiving of more than 100,000 entries. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This issue is most likely an inadvertant consequence of an earlier attempt to correct Finding 8321. The query connection was inadvertantly terminated after the archiving of the first file (i.e., 100,000 entries) and the next portion of the retrieval subsequently failed. The software will be re-written to maintain the connection to the database until the entire archive operation (even across multiple files) has been completed. (Swartz, Mark E. Jul 6, 2012)<br><br>This issue does not have to do with the inadvertant consequence of an earlier attempt to correct Finding 8321. The issue is the logic associated with detecting when to stop archiving entries in the case of multiple files. The logic is breaking out before writing out the last file. This will be corrected. (Swartz, Mark E. Jul 18, 2012)<br><br>Resolved in U5; closing. (Brown, Sean Aug 6, 2012) <br> |  | 35 | FINDING | 8575 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73516
29696 | FINDING | New SIS alarm mapping file is ignored by SIS alarm handler |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When new logic solver is added to system and LS and controller are loaded, SIS alarm handler ignores new alarm mapping file. After controller is cleared and loaded again new file is accepted. (Czak, Jakub Jun 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | New file was marked with &quot;AddLS&quot; status but after that it was overwritten with &quot;UpdateLs&quot; so correct action was not taken. This behavior was corrected. (Czak, Jakub Jun 18, 2012) <br> |  | 35 | FINDING | 8576 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73518
29697 | FINDING | Incorrect SIDs of points in alarm mapping file. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | SIS points have incorrect SIDs in alarm mapping file. Because of that SIS alarms subsystem is not able to set alarms for SIS points. (Czak, Jakub Jun 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected string to integer conversion in OvSisAlarmMapping.dll that was causing that issue. (Czak, Jakub Jun 18, 2012) <br> |  | 35 | FINDING | 8577 |  | FINDING | [10 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73520
29698 | FINDING | OCR400 is failing during drop load (17/67). | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Matt has been investigating ongoing issues with OCR400 Controller 17/67 (WALT). It has approximately 30,000 originating points, which may be relevant. Prior to U3, the MAIN task was stopping when the controllers were booting. This does not occur in U3, but the controller fails during a drop load. It appears that something in the load process is starving other tasks. (Brown, Sean Jun 18, 2012) |  |  |  | Clear and load drop17/67. Drop should not fail during load. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Many items were addressed in U4 to increase load time. Was able to successfully load both drops. Please retry. (Perdeus, Matthew Jul 26, 2012) <br> |  | 35 | FINDING | 8578 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73522
29699 | FINDING | OCR1100 Controller failed during loading of Sys Test control sheet. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Few control sheets were imported from Ovation 3.4 into DROP35/DROP85 OCR1100 Controller. During loading of these sheets it was observed that DROP35 loaded succssfully but DROP85 failed during load operation. Ovation Error log shows following message:<br>drop85 (coord): memPartFree: invalid block 0x392b20c in partition 0x65dce0<br> fatal kernel task-level exception!<br>Controller Error:OPP Subsystem Error:OPP System Error - Fatal : 0x12 : 0xffffffff : 0x0 : 0x0<br>Controller Error : OPP couldn&quot;t get pointers to 0x0 dynamic and static data<br>REDUND_PROC MSG : Switching to Failed mode<br><br>The error was shown to Ben. The relevant portion of error log is attached with the finding (Lal, Ramesh Jun 18, 2012)<br>6/20/12:RL - Assigned few analog/digital/packed points to actual I/O hardware and tried to load Drop35 (OCR1100). It failed during Load operation. Screenshot(Drop35_Failed_During_Load_June20) of Error log is attached with the finding. (Lal, Ramesh Jun 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected a problem with assigning I/O to bits in packed points. (Pingree, Douglas K. Jun 28, 2012)<br><br>7/27/12:RL - Tested in 3.5_U4 by assigning bits of Packed point to I/O channels. Controller was loaded without error.Finding closed. (Lal, Ramesh Jul 27, 2012) <br> |  | 35 | FINDING | 8579 |  | FINDING | [10 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73524
29701 | FINDING | Modification of Custom frame does not get propagated to Signal Diagram Viewer clients | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | As per the SDR-18591 we perform the steps as below:<br><br>NEW CUSTOM FRAME<br>-Created a custom frame under ovptsvr/systemName/networkName/unitName<br> loaded the drop<br>-Verified that the new frame is found in Ovation\CtrlBldr\on-line unit directories on the clients<br>-The new frame propagated and get utilized by Signal Diagram Viewer throughout the system<br><br>MODIFIED CUSTOM FRAME<br>- Change the custom frame under ovptsvr/systemName/networkName/unitName and loaded the drop. <br>- After modification and the modified frame was not distributed in signal diagram but it was distributed in control builder(control sheets). <br><br>DELETED CUSTOM FRAME:<br>- Deleted the custom frame and loaded the drop. <br>- Verified the custom frame was distributed<br><br>We observed that the creating new custom frame and Delete custom frame functioning properly<br>the only thing after modification of the custom frame does not distribute in signal diagram.<br><br>The modified information should be displayed in signal Diagram Viewer. (K, SendhilKumar Jun 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. Sep 11, 2012) <br> |  | 35 | FINDING | 8581 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73528
29702 | FINDING | "Diagram Name" should be replaced with "Diagram Number". | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ov.3.5.0 developer studio, under a Ovation drop configuration--&gt;Alarm--&gt;Iconic--&gt;Groups, when a new diagram is inserted, a window opens with the attribute &quot;Diagram Name&quot;, that should be replaced with &quot;Diagram Number&quot; as per the help file.<br>Snapshot and remote login details is attached for reference. (Mitra, Sambuddha Jun 19, 2012) | SJ 08/13/2012: The screenshot updated to reflect Diagram Name. SJ 09/13/2012: The screenshot updated to reflect Diagram Name. SJ 09/13/2012: The screenshot and content updated to reflect Diagram Name. |  |  | SJ 08/13/2012: The screenshot updated to reflect Diagram Name. The new online help will have the changes incorporated. SJ 09/13/2012: The screenshot updated to reflect Diagram Name. Please recheck in Ov.3.5.0_U8 build. You can also find the updated Operator Station Configuration Guide (OW350_21) on M: drive (\\uspit-fp03\SourceIntegrity) SJ September 24, 2012: The Help file updated. Please see Ov.3.5.0_U9 build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Diagram Name is correct. In Ovation, Diagrams (or Graphics) have names, not just numbers. The use of names has been in use since at least Ovation 3.3.1. The issue is not with the Ovation Developer Studio, it is the help file. (Swartz, Mark E. Jul 2, 2012)<br><br>LC 07-06-2012: Tranferring this to Swati. This change involves a new screen capture in the Operator Station Configuration Manual. The name of the topic is &quot;To insert a new Iconic Alarm diagram for the Operator Station.&quot; (Casteel, Linda Jul 6, 2012)<br><br>SJ 08/13/2012: The screenshot updated to reflect Diagram Name. (Jain, Swati Aug 13, 2012)<br><br>SM 08/20/2012: Verified in Ov.3.5.0_U6. The Help file is not updated. Please find the JPEG attachment file &quot;F_8582_350U6_Help&quot; regarding the issue. In that image &quot;Number&quot; should be replaced with &quot;Name&quot;, marked in that image.<br>The correct Help file will be as per the JPEG attachment file &quot;F_8582_Correct&quot;. (Mitra, Sambuddha Aug 20, 2012) (Mitra, Sambuddha Aug 20, 2012)<br><br>SJ 09/13/2012: The screenshot updated to reflect Diagram Name. Please recheck in Ov.3.5.0_U8 build. You can also find the updated Operator Station Configuration Guide (OW350_21) on M: drive (\\uspit-fp03\SourceIntegrity) (Jain, Swati Sep 13, 2012)<br><br>SM 09/18/2012: Verified in Ov.3.5.0_U8. The Help file is partially updated, not fully corrected. Please see the attached JPEG file &quot;Snap_Help_U8&quot;. It shows the error. Here &quot;diagram number&quot; should be replaced with &quot;diagram name&quot;. (Mitra, Sambuddha Sep 18, 2012)<br><br>SJ September 24, 2012: The Help file updated. Please see Ov.3.5.0_U9 build. You can also find the updated Operator Station Configuration Guide (OW350_21) on M: drive (\\uspit-fp03\SourceIntegrity) (Jain, Swati Sep 24, 2012)<br><br>SM 09/24/2012: Verified in Ov.3.5.0_U9. The Help file is updated with correct information regarding this. Hence closing the finding. (Mitra, Sambuddha Sep 24, 2012) <br> |  | 35 | FINDING | 8582 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73530
29703 | FINDING | On VCH drop and its VCs the NIC information is different in the DU record and System Graphics | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On VCH drop and its VCs the NIC information is different in the DU record and in the System Status graphics (1800 &amp; 1801).<br>On the VCH:<br>KM - Interface Type = Generic Ethernet<br>VE - Interface Vendor = Unknown<br>K0 - Channel 0 State = Active<br>K1 - Channel 1 State = Unknown<br><br>while on the VCs of the same VCH drop the same info appears as:<br>KM - Interface Type = SAS 100 MBit Ethernet<br>VE - Interface Vendor = 10<br>K0 - Channel 0 State = Active<br>K1 - Channel 1 State = Unknown (Benzvi, Mati Jun 19, 2012) (Benzvi, Mati Jun 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is similar to Finding 8848.<br>The VCH should be operating the same as any MMI not configured with OHI. <br>The 10 for the vxsim is for the WindRiver simnet driver. The text for PI should be updated for this. (Perdeus, Matthew Oct 31, 2012)<br>---<br>msb - in DU record of VC: VE = Wind River (Benzvi, Mati May 23, 2013) <br> |  | 35 | FINDING | 8583 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73532
29705 | FINDING | Imported SIS Controller from Ov-340 to Ov-350 has all SIS_IO_CHANNEL_TYPE = Undefined Channel Type | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In PGH lab SIS network (Ov-350) all the points and SIS information were exported from <br>a working Ov-340 network with the sis flag before upgrading to Ov-3.5.0.<br>When the same data is imported, the SIS controller is giving upon download <br>30 consistency check errors for: <br> IO_Channel_Type = Undefined Channel Type<br>while in the import file the same Channels have SIS_IO_CHANNEL_NUMBER=&quot;#&quot;<br>where # is the index of the pull down list in Studio:<br> 0 = Undefined Channel Type<br> 1 = Analog Input Channel<br> 2 = HART Analog Input Channel<br> 3 = HART Two-State Output Channel<br> 4 = Digital Input Channel<br> 5 = Digital Output Channel (Benzvi, Mati Jun 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot duplicate. Please provide the other portion of the daily backup and the steps which were followed to import the full database, so that we can reproduce. (Swartz, Mark E. Jul 3, 2012)<br>---<br>msb - 8/19 - The import and log files are on drop135 in D:\SIS_OV340_Drop135_DBS (Benzvi, Mati Aug 19, 2012)<br><br>Cannot duplicate. No SIS Channel Consistency errors following import of provided backup files. All SIS I/O Channels with assigned Ovation points have a configured Channel Type. (Swartz, Mark E. Aug 20, 2012) <br> |  | 35 | FINDING | 8585 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73536
29707 | FINDING | Logic Solvers can not be loaded on an upgraded Ovation 3.5 system. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | A 3.4 system with a controller using SIS Logic Solvers was upgraded to 3.5. After the upgrade when attempting to load the logic solvers, the error &quot;Hardware Inconsistency Error&quot; was encountered for each logic solver. (Wood, Tom Jun 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | &quot;Hardware Inconsistency Error&quot; indicates that SIS Identifier on DB Server is different then one that SDS got from switch as DHCP parameter. To verify if that is the case, please telnet to SIS switch, use &quot;enable&quot; command to go to priviledged mode, use &quot;show running&quot; command to show current SIS switch configuration. Check if option 224 in DHCP parameters for both SDSes from redundant pair is consistent with SIS identifier on DB server. Do the same thing on second switch. If values are correct, try rebooting SDSes. If not, upload new configuration to switches and reboot SDSes. (Czak, Jakub Jun 26, 2012)<br><br><br>See attached file. (Wood, Tom Jul 2, 2012)<br><br>It was confirmed that this issue was caused beacause there was discrepancy between SIS identifieres of SDSes in switch configuration and on DB server. After updating switch configuration problem disappeared. (Czak, Jakub Aug 4, 2012) <br> |  | 35 | FINDING | 8587 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73540
29709 | FINDING | Ovation System viewer, opens a blank dropdown window when clicked on Abnormal, under Ovation I/O in Drop Summary. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Ovation system viewer when viewed at Network level, shows Drop Summary window.<br>Here the drops which are in alarm are referred to as Abnormal under Ovation I/O tab.<br>When Clicked on Abnormal, a blank dropdown window appears. <br>When Clicked on blank window it opens I/O Channels which are actually in alarm /Abnormal condition.<br>Maybe the Foreground and back ground colors are same(white), due to which the list of alarm conditions is not visible, where as they can be selected. (Sachan, Pallavi Jun 22, 2012) |  |  |  | rerun the same test. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this should be fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8589 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73544
29717 | FINDING | Symbol Browser Menu does not have Control Macros option. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | To add a control Macro user has to go to add algorithm menu, this can not be done by symbol browser. As Symbol browser doesnot have control macro option in it.<br>Because of this control macro cannot be added to favourite folder. (Sachan, Pallavi Jun 25, 2012) |  |  |  | Test the above condition. You may need to hit refresh to see the current list of available control macro symbols. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. It may require a refresh to see the symbols.<br>- (Hutchison, Steven B. Jun 29, 2012) <br> Found Fixed in U4 (a refresh was required). Hence Closed. (Sachan, Pallavi Jul 18, 2012) |  | 35 | FINDING | 8597 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73560
29718 | FINDING | If the Control Builder exits unexpectedly when working on multiple files, files could not be recovered. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When working on multiple files of control builder, if control builder exits unexpectedly, Recover Files does not recover the work lost.<br>As explained in OW340_80 manual section 7.8 Steps 1 &amp; 2 are fine but at step3, no Recover File Window appears, hence further steps 4 &amp; 5 could not be attained. Instead, &quot;Close all other Control Builder instances&quot; window is seen, when clicked on OK. One instance of Blank Control Builder is present. (Sachan, Pallavi Jun 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Could not duplicate. Sheet must be modified before a recovery file is created. The easiest way to modify a sheet is to delete some algorithms. Each sheet must be opened individually to get the recovery dialog. (Hutchison, Steven B. Jun 29, 2012)<br><br>Individual sheets have the recovery dialog, but when we want to recover multiple files its not acheivable.<br>Multiple files were opened and some contents from each sheet was deleted, just for purpose of editing the sheet. And Control builder instances were killed from Task Manager. Now when a new instance of Control builder is opened and above mentioned operations are performed, Recover Files option didnot open any Recover File selection Window as mentioned in Manual. (Sachan, Pallavi Jul 12, 2012)<br><br>Could not duplicate. - (Hutchison, Steven B. Jul 12, 2012) <br> |  | 35 | FINDING | 8598 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73562
29720 | FINDING | Accessing points of a remote network(Ov3.2.0)from an Ov3.5.0 machine via PI causes a .NET framework unhandled exception | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Open Point information on a 3.5.0 drop -&gt; click on ovation point browser -&gt; Select the Ov3.2.0 Network/Unit -&gt; Press OK -&gt; Press Start -&gt; Scroll down to view all the points.<br>Once a user opts to scroll down, the .NET framework unhandled exception error window is witnessed. (Refer to the attached snapshot) (Khanna, Anant Jun 28, 2012) |  |  |  | The Point Browser has been affected. The exception that was throw is now being handled. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The finding has been fixed in U8 build. (Khanna, Anant Sep 19, 2012) <br> |  | 35 | FINDING | 8600 |  | FINDING | [10 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73566
29721 | FINDING | Active buttons do not get highlighted in Ovation Point Review | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Once a point is selected in Ovation Point Review, the value tab is seen on the menu bar where a user has the option to scan on/off, value clamp on/off, etc.<br>If a user opts to change a point from scan on to scan off, the yellow highlight is not active on the scan off button.<br>Similar for other buttons present in the value tab. (scan/clamp/test mode/latched quality/engg check/reasonability check)<br>The active button is not getting highlighted, it should work similar to the functionality present in Point Info.<br>In actual the buttons functionality is working fine, but the active buttons are not getting highlighted. (Khanna, Anant Jun 28, 2012)<br>The same problem is seen in Ov3.3.1 and Ov3.4.0 (Khanna, Anant Jun 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | WIW no plans to fix. Point Review accommodates multiple points, but Point Information only displays the data for a single point. (Augustine, Lisa Sep 10, 2012) <br> Finding closed as per developer&quot;s comment (Khanna, Anant Sep 18, 2012) |  | 35 | FINDING | 8601 |  | FINDING | [10 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73568
29722 | FINDING | In Ovation Point Review, the menu bar is not displayed as per the filter applied | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation point review, if a user applies a filter by any record type, the menu displayed under the &quot;Value&quot; tab and &quot;Alarm\Limit&quot; tab is static for all record types.<br>For example: In ovation Point review, filter by &quot;DU&quot; record type, a user is still able to the view the &quot;Value&quot; tab and &quot;Alarm\Limit&quot; tab. If the same DU point is opened in Ovation point information, the &quot;Value&quot; tab and &quot;Alarm\Limit&quot; tab will not be visible.<br>The menu bar present in Ovation Point Review is static irrespective of the filter been applied.<br>The options which are not applicable for a particular record type are not grayed out and a user is able to select these options. (Eg: scan off\on, alarm check on\off, etc)<br>The menu should be dynamic, depending on the record type been filtered in Ovation point review. (Similar functionality to Ovation Point info)<br>The same behavior is witnessed in Ov3.3.1 and Ov3.4.0 (Khanna, Anant Jun 28, 2012) (Augustine, Lisa Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | WIW No plans to fix. (Augustine, Lisa Sep 10, 2012) <br> Finding closed as per developer&quot;s comment (Khanna, Anant Sep 18, 2012) |  | 35 | FINDING | 8602 |  | FINDING | [10 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73570
29725 | FINDING | Controller fails during the load operation of logic sheet with distributor algo | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | A logic sheet is created with all Input and output points. Compiled the sheet and loaded the sheet as per the test case 5.1.2 and 5.1.3 in 3.5_SRF1450_SVTP_rev1.2_JJ.doc<br><br>Then after completion of load operation controller goes back into fail mode.<br><br>Following messages were observed in error log<br><br>&quot;Error retrieving local memory on sheet 38.svg required size is 148 but retrieving 112&lt;/Err&gt;<br>&lt;Err dts=&quot;06/28/12 11:32:24&quot; dtl=&quot;1340863344&quot; source=&quot;ov35-drop253-u2&quot; priority=&quot;1&quot; identifier=&quot;drop82&quot;&gt;REDUND_PROC MSG : Switching to Failed mode&lt;/Err&gt;&quot;<br><br>Please find attached the attached the error log.txt file . (Jayarajan, Jayakumari Jun 28, 2012) |  |  |  | The affected area includes the template information utilized by the Ovation Engineering Tools. Specifically, 160 bytes of local memory will be specified during a load (specifically, an ADD) of LC points configured for the DISTRIBUTOR algorithm. A clear operation to the controller will be required in order for the new amount of local memory to be specified during the next load operation. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The templates need to be corrected. (Pingree, Douglas K. Jun 29, 2012)<br>The templates used by the Ovation Engineering Tool software have been changes for the DISTRIBUTOR algorithm. (Swartz, Mark E. Jul 3, 2012)<br><br>Jayakumari J(19July2012)<br><br>Tested in u4 and no controller failure observed. (Jayarajan, Jayakumari Jul 19, 2012) <br> |  | 35 | FINDING | 8605 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73576
29729 | FINDING | Signal Diagram fully qaulified point name shows Network Name instead of Network Alias. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Signal Diagram, Algorithm summary , Function Summary shows point names as &lt;pn.unit@nework name&gt;. <br>When we perform RightClick operations point opens in any other Ovation application as as &lt;pn.unit@nework alias&gt;.<br>This should be consistent for all applications. (Sachan, Pallavi Jun 29, 2012)<br><br>Is this for local network points or remote network points? (Hutchison, Steven B. Jun 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is local network point. Kindly find attached &lt;F#8609.jpg&gt; eg.&lt;PS-OPK-00F3-01.UNIT0@IVALNET3&gt;, when performed right click PI or any other point menus, it opens point as &lt;PS-OPK-00F3-01.UNIT0@FE350&gt;. (Sachan, Pallavi Jul 2, 2012)<br><br>The previous releases (3.3.1/3.4.0) shows point name as PS-OPK-00F3-01.UNIT0@, this is that in 3.5.0 point name is shown as fully qualified. Just for consistency, this should be changed to look as &lt;pn.unit@nework alias&gt;. (Sachan, Pallavi Jul 12, 2012)<br><br>No Plans To Fix. - (Hutchison, Steven B. Jul 12, 2012) <br> Closed as per developer&quot;s comments. (Sachan, Pallavi Jul 18, 2012) |  | 35 | FINDING | 8609 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73584
29730 | FINDING | SIS sheetwith same secure parameter point name can be loaded to more than one logic solver. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-03-11 02:26 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-03-11 02:26 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Below scenaerio not happens every time but happened number of times in last three days. steps are followed to recreate the issue.<br>1. Created SIS sheet [SLS01-SEC] with secure parameters in logic solver1 [SLS01], save it and loaded the sheet to logic solver1 and controller successfully.<br>2. Select control option in studio and export the above sheet to a directory.<br>3. Select control option and imported the above exported sheet to Logic Solver2.<br>Sheets gets imported successfully, no error appeared for already origination of secure parameter point name in Logic Solver1.<br>4. Secure parameter with same name as configured in logic solver1, get updated in Secure parameter list of logic solver2 in studio. For reference screenshot [SEC PARA SLS01 N SLS02.jpg] is attached.<br>5. Same secure parameters in SIS Sheet SLS01-SEC loaded to more than one logic solver (SLS01/SLS02). <br><br>Observation after loading SLS02.<br>On compiling sheet [SLS01-SEC] in SLS01 error appeared for secure parameter point name is already originated in SLS02. SLS01 cannot be loaded. (Pandey, Vijay Jun 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <br> |  | 35 | FINDING | 8610 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 93259
29731 | FINDING | On performing Lock opertaion on already locked logic solver, no message comes and lock operation gets started again. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-28 07:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-28 07:20 |  |  |  | 2017-02-28 07:20 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In studio, right click on logic solver. There is two icon [Lock/Unlock].<br>If logic solver in locked state and we perform lock operation. Locking operation gets started instead of saying that logic solver is already in locked state. No message comes.<br><br>Observation2:<br>In studio, there is no indication for logic solver current state [Locked/Unlocked]. (Pandey, Vijay Jun 29, 2012) |  |  |  | In the configured system, following test should be performed: 1.Lock one of logic solver 2.Try to lock it second time - an information should be displayed that Logic solver is already locked. 3.unlock the logic solver 4. try to unlock second time - an ifonrmation should be displayed that Logic solver is already unlocked. The status of logic solver can be seen from SIS Diagnostics | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This will be fixed in Ovation 3.5.1 (Raciborski, Mikolaj Jul 15, 2013) <br> |  | 35 | FINDING | 8611 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | Ovation 3.5.1_U2 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | 3.5.1 |  |  | FINDING | [6 empty] | 109433
29732 | FINDING | OL Cylinder & OL Gauge are non functional when they are called from Macro. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1.If Macro is prepared with OL Cylinder &amp; OL Gauge &amp; $D1 (for OL Cylinder), $D2 (for OL Gauge) parameters are assigned. Compile the macro.<br>2.The same Macro is called in graphics.PS4_350_D13_VAR-OUT point is assigned for both $D1 &amp; $D2.Download the diagram.<br>3.In runtime Graphics application both OL Cylinder &amp; OL Gauge are non functional. They do not change their appearance even when value of the assigned parameter is changing.<br>4.Where as if simple OL Cylinder &amp; OL Gauge are taken in graphics and assigned with same point PS4_350_D13_VAR-OUT,both are functional and showing change in appearance when value of corresponding point gets changed.<br>5.Please refer the attached Screen shot for reference. (Athavale, Samiradixit Jul 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can you please check to see if the items in the macro are in the FOREGROUND section. If not, move the items to the FOREGROUND, recompile the macro and the main diagram and download.<br>If the items are in the FOREGROUND can you please attach to this finding the source for the MACRO and the main. (Spillane, Donal A. Jul 2, 2012)<br><br>Items in Macro are in Foreground.Please find the attached source code of Macro and main. (Athavale, Samiradixit Jul 3, 2012) <br> The issue has to do with not specifying the record field for the cylinder and gague in the macro. The issue can be resolved by changing the macro to use $D1 AV and $D2 AV or by passing the record type into the macro with the point name as \PS4_350_D13_VAR-OUT\ AV.<br><br>The Graphics Builder can not determine a point type for a $D point in a macro and therefore can not default the record field. In a main or a window where the point name is specified the builder can determine the point type and default the record field (in this case it is an analog point and will default to AV). (Spillane, Donal A. Jul 6, 2012)<br><br>After putting record field after point type in graphics for called macro,OL Cylinder &amp; OL Gauge change their behaviour and become functional.Hence Finding is closed. (Athavale, Samiradixit Jul 25, 2012) |  | 35 | FINDING | 8612 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73589
29733 | FINDING | OCR400 Control Task 2 Sheet Set Size is incorrect after OvPtImport. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400 Controller 11/61 was exported from an Ovation 3.3.1 system (FE221). The export was modified (system, network, IP addresses, etc.) and that file was imported into an Ovation 3.5.0 system (SISsys1). The Control Task 2 Sheet Set Size of the controller after being imported (65000) does not match the value in the import file (500000). (Brown, Sean Jul 2, 2012)<br><br>Occurred again after importing OCR400 Controller 43/93 (EMILY). Sheet Set Size entries for Tasks 1 and 2 are incorrect. Excerpts from OVPT import and export files are attached. (Brown, Sean Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot duplicate. Modified an existing controller Control Task 2 Sheet Set Size of 500000 bytes, exported, deleted the drop (from Ovation Developer Studio), and imported. After import, size is 500000 bytes. Please provide example import file. (Swartz, Mark E. Jul 2, 2012)<br><br>Import file was uploaded. Will attempt to recreate as well. (Brown, Sean Jul 3, 2012)<br><br>Cannot duplicate with uploaded import file. (Swartz, Mark E. Jul 6, 2012)<br><br>Created SDR 19051; closing. (Brown, Sean Sep 26, 2012) <br> |  | 35 | FINDING | 8613 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73591
29734 | FINDING | In 3.5 controller, Incorrect version of Hart modules firmware are available. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Incorrect HART module firmware versions are available.<br>Controller Diagnostics shows incorrect versions of firmware in the controller for following Hart modules. a)HART Standard Analog Output &quot; FW Rev 8. b)HART High Performance Analog Input&quot; FW Rev 6. c)HART High Performance Analog Output&quot; FW Rev 6. For reference screenshots of controller diagostics for above modules are attached.<br>As per 3.4 DIR,The latest HART firmware versions were as follow:<br>a) HART High Performance Analog Input&quot; FW Rev 07. b) HART High Performance Analog Output- FW Rev 07. c) HART Standard Analog Input - FW Rev 10. d) HART Standard Analog Output &quot; FW Rev 12 (Pandey, Vijay Jul 3, 2012) (Pandey, Vijay Jul 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Incorrect versions were being released with 3.5. (Pingree, Douglas K. Aug 3, 2012)<br>vp-08/27/12- Retested with 3.5.0_U7, controller diagnostics shows following versions of firmware in the controller for following Hart modules. a)HART High Performance Analog Input&quot; FW Rev.08. <br>b)HART High Performance Analog Output- FW Rev. 07 c)HART Standard Analog Output &quot; FW Rev. 12. <br>As per developer 3.5.0 should have mentioned firmware. Hence finding is closed. (Pandey, Vijay Aug 27, 2012) <br> |  | 35 | FINDING | 8614 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73593
29735 | FINDING | "Algorithn" should be replaced with "Algorithm". | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In many places of SVTP (such as 5.20.1 Test: &amp; etc.) H:\Tests\3.5.0\3.5_Algorithms_SVTP_rev2.0_SM.doc file, &quot;Algorithn&quot; is written, that should be replaced with &quot;Algorithm&quot;. (Mitra, Sambuddha Jul 3, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Algorithms (ALG)</p> <p><strong>Release Level:</strong> 3.5.0</p> <p><strong>Originator:</strong> Mitra, Sambuddha</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Mitra, Sambuddha</p> <p><strong>Entry Date:</strong> 2012-07-03T06:31:25-04:00</p> <p><strong>Modified Date:</strong> 2012-07-03T06:31:25-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8615 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73594
29736 | FINDING | Ovation developer Studio getting crashed once added a new OPC Servers in studio. | Patel, Sunil EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Ovation developer Studio getting crashed once OPC server added in new OPC Servers.In studio configuration go to insert opc server in opc section through browsing Prog ID then Ovation developer Studio getting crashed. (Singh, Ghanshyam Jul 3, 2012)<br><br>GS(22/08/2012)- I am able to recreate the issue in U6 at IEC. I think you should remote login in IEC lab .Please find attach for remote login on drop-247 in net#7 in IEC lab. (Singh, Ghanshyam Aug 21, 2012)<br><br>GS(04/09/2012)- I am still able to recreate the issue in U7 at IEC. (Singh, Ghanshyam Sep 3, 2012)<br>IC 9/11/12 - marked finding as OPEN(failed retest. (Capani, Nooch Sep 11, 2012)<br><br>GS(16/09/2012)-We can add OPC server from DBS drop in studio , but EWS studio still getting crashed. it seems that OPC compatibility is unstable in 3.5.0. (Singh, Ghanshyam Sep 17, 2012)<br><br>GS(20/09/2012)-As finding &quot;8907&quot; is libed for GBNT crash while receving OPC point, so can I belive present issue also will be taken care ? (Singh, Ghanshyam Sep 20, 2012)<br><br>SSP(16/10/2012) - Yes, this should be retested after the fix for FINDING #8907 is submitted. - Sunil Patel (Patel, Sunil Oct 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8616 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73596
29737 | FINDING | On new machine when preferences are not saved, the docking layout in Trend application does not work as expected. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were done to reproduce this:<br><br>1)Clear all preferences, <br>2)Run new instance of Trend<br>3)Under Format tab, Details panel and Properties panel checkboxes appear unchecked. Correct behavior is they should appear checked.<br>4)Then check these boxes.<br>5)Then try various docking options for properties panel like various docking positions, floating docking position etc. Incorrect behavior is observed after this.<br>Only way to correct this again open new trend window.<br><br>Shown above problem to Prashant. (Kumar, Shailendra Jul 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed this issue. (Bargaje Prashant Jul 6, 2012)<br><br>SK:ok in U4, hence closed. (Kumar, Shailendra Jul 27, 2012) <br> |  | 35 | FINDING | 8617 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73598
29738 | FINDING | Occasionally we observed the error"graphics MFC Application has stooped working"while customize exisiting graphics. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Several cases have been observed where graphics has been customized<br>under&gt;right click&gt;Properties&gt;parameter ($D1,$D2...etc).<br>we have been observerd &quot;graphics MFC Application has stooped working&quot; its getting crash the graphics application<br><br>Please find the attached snap shot for reference. (K, SendhilKumar Jul 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can you retest this finding with the latest update. I have tried to reproduce this here, with no success. I have logged into your system but it appears the algorithms and graphics are no longer available. If you can reproduce can you let me know exactly what graphics you are using and the procedures used to cause it. (Spillane, Donal A. Aug 24, 2012)<br>----------------------------------------------------------------<br>SKK:we are trying to recreate this issue and we could not find proper step to reproduce this issue.but Occasionally its happening while customize exisiting graphics. (K, SendhilKumar Oct 9, 2012) <br> I have found situations where the graphics program is not freeing GDI objects correctly for certain drawable items. A change has been made to correct this. (Spillane, Donal A. Oct 11, 2012)<br>---<br>msb - Closed: Converted to SDR 19130 (Benzvi, Mati Oct 13, 2012) |  | 35 | FINDING | 8618 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | K, SendhilKumar PROCESS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73600
29739 | FINDING | OvationOnlineSynchrnonizer error/warnings messages displayed once a remote network is configured in Ov3.5.0 | Hutchison, Steven EMR SYSS PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In order to view the signal diagrams of a remote network, we need to configure the remote network by using the application OvationOnLineSynchronizer.exe.<br>Once the remote network is configured at the registry level: HKEY_LOCAL_MACHINE\SOFTWARE\Westinghouse\OnLineSync\Remote\FE350C, we witness errors/warnings related to OvationOnLineSynchronizer.exe in the Event log.(Error and warning messages have been attached along with the snapshot)<br>Also, we are still not able to access the signal diagrams of a remote network present on the same domain.<br>Remote login details attached. (Khanna, Anant Jul 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed Remote Path Configuration - (Hutchison, Steven B. Jul 12, 2012)<br><br>Fixed Registry Initialization and Defined Reasonable Defaults<br>- (Hutchison, Steven B. Aug 14, 2012) <br> The error/warning messages displayed in the event log have been fixed in U4 build.<br>But we are still unable to access the signal diagrams of a remote network present on the same domain. The @NETWORK_NAME folder is still not visible although entry of the remote network is done at registry level. (Khanna, Anant Jul 20, 2012)<br><br>After rebooting the DBS today, we have noticed that the @NETWORK_NAME folder is now visible. The signal diagrams of the remote network are now accessible.<br>However, once the remote network is configured, we again witness errors/warnings related to OvationOnLineSynchronizer.exe in the Event log. The problem of errors/warnings in the event log still persists in U4 build. (Khanna, Anant Jul 25, 2012)<br><br>ANK(08/23/2012)- Tested the finding in U6, the same problem persists. Finding has not yet been fixed, the errors/warnings are still flooding in the event log. (Khanna, Anant Aug 22, 2012)<br><br>Fixed nuance crash message - Verify that Registry Entry &quot;HKEY_Local_Machine\Software\Westinghouse\OnLineSync&quot; key &quot;Trace.Enabled&quot; is not &quot;True&quot;. <br>- (Hutchison, Steven B. Sep 11, 2012)<br><br>ANK(09/21/2012)- The problem still persists in U8. The error messages are still seen in U8.<br>You could remote login to drop 250 to see the error log.<br>Also, there is no key named &quot; Trace.Enabled&quot; in the registry. (Khanna, Anant Sep 21, 2012)<br><br>Please save the event log as an Event File (evtx) and send it to me via send this file.<br>- (Hutchison, Steven B. Oct 19, 2012)<br>---<br>msb - Pallavi, please follow up on this MIR request (Benzvi, Mati Sep 23, 2013) |  | 35 | FINDING | 8619 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73602
29740 | FINDING | Loading of Controller drop33/drop83 (which is in control mode) hangs. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 6 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2024-01-11 09:08 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2024-01-11 09:08 |  |  |  | 2024-01-11 09:08 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | steps to Reproduced<br>1.open developer studio.<br>2.Perform some changes (e.g. create an analog point or change any point attribute or create a control sheet) in controller drop33/drop83.<br>3.When loading the controller, then the Controller drop33/drop83 loading is hanged at different stages<br>(the Snapshots attached for hanged state on different stages).<br><br>Note1: Same observation is also in controller drop7/drop57.<br><br>Note2: please find attached remote login procedure for Drop250. (Prasad, Parmatma Jul 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Drop load dynamics have changed with U4. Please re-test. (Pingree, Douglas K. Jul 30, 2012)<br>Checked with build OV350_U4,the problem still exist.<br>Hence Failed. (Prasad, Parmatma Aug 6, 2012)<br>I have found one more observation followed by above:when controller drop33/83(which is in control mode) is cleared then it goes to failed mode permanently.To make it in normal mode, Reboot is required.<br>please find attached txt of &quot;drop33_fail_noreboot.txt&quot;. (Prasad, Parmatma Aug 7, 2012) <br> |  | 35 | FINDING | 8620 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | x |  |  | FINDING | [6 empty] | 212598
29741 | FINDING | "Refresh"is required once,from "Import Operation" window before browsing the file (.svg) to be imported. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1. Export a control sheet (.svg) and keep the file in any location (say d drive).<br>2. Perform the import operation by Control option--&gt; Import operation.<br>3. Import operation window will open.<br>4. Browse the control sheet svg file to be imported ( exported file from d drive) from &quot;import Operation&quot;window.<br>Observation: The svg file kept in d drive is not browsed/found.<br>5. Click on &quot;Refresh&quot; button in &quot;Import operation&quot; window and browse<br>Observation: Now the svg file on d drive is browsed/found.<br>Problem: When a svg file, which need to be imported is browsed first time from &quot;import operation&quot; window, the &quot;Refresh&quot; is required once, to see the svg file on the location .<br>please find attached remote login details. (Joshi, Parmesh Jul 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The cache file is not updated when the sheet is exported. Way It Works No Plans to Fix.<br>- (Hutchison, Steven B. Jul 12, 2012)<br><br>As per developer comments, it is WIW, Hence Closed. (Joshi, Parmesh Jul 20, 2012) <br> |  | 35 | FINDING | 8621 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73606
29742 | FINDING | Publish Operation is not working correctly for destination as "Output to Directory" | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | When a publish operation is performed and selected destination option as &quot;Output to directory&quot;. The following observation are found:<br>1. The points are always coming in published pdf file irrespective of the &quot;Include Points&quot; are checked or not. please see the attachments named &quot;droplayout_out to directory_PointsNotIncluded&quot; and &quot;droplayout_out to directory_include points&quot;<br>2. When destination is selected as &quot;Output to Directory&quot; then any of its sub categories (Use original file name/Auto generated) should be checked by default, but nothing is selected. In this case pulished file is coming as &quot;use original file name&quot; format. please see the attachment as &quot;Publish_operation.jpeg&quot;.<br>please fine remote login details as attached. (Joshi, Parmesh Jul 5, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Control Builder - Unified (CBU)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Hutchison, Steven B. Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-07-05T02:28:56-04:00</p> <p><strong>Modified Date:</strong> 2012-07-05T02:28:56-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8622 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73607
29743 | FINDING | Error window appears on clicking menu buttons when logged in as an operator -Error Log | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Login as an Operator -&gt; Ovation Applications -&gt; Error Log, Click on the view menu button -&gt; Select the Priority level/Refresh/Enable Auto Refresh.<br>On selection of any of these options, the operator would witness an error message (refer to the attached snapshot)<br>Also, if a user tries to delete an entry of the error log, the same error message is displayed.<br>Remote login details attached (Khanna, Anant Jul 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Please test it in the next build. i.e U4 (Matreja Shyam Jul 10, 2012) <br> The finding has been resolved in Ov3.5.0_U4 build successfully. (Khanna, Anant Jul 20, 2012) |  | 35 | FINDING | 8623 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73609
29744 | FINDING | Reasonability low limit is not editable(greyed_out)_ in plant mode for Deluxe Anlog points | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Reasonability low limit is not editable(greyed_out)_ in plant mode for Deluxe Anlog points ,even though the Reasonability low limit value is assigned for points.<br><br>Steps to reproduce: <br>1.Create an analog point ( DA) in any type of ovation drop (Controller). <br>2.Assigned value to High and low limit setting field of the point by selecting the plant mode tab<br> 3.Load the corresponding drop and observe the point in PI window <br><br>It is observed that after selecting the plant mode , reasonability high limit filed is editable but reasonability low limit field is not ediable (greyed out)<br><br>Please find the attached snap shot _REASONABILITY_LOW LIMIT.jpg for reference. (Jayarajan, Jayakumari Jul 5, 2012) | none |  |  | Check that low reasonability limits on plant modes can be changed. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Bug in OvPointDirObjects was corrected. (Burgoon, Frank J. Jul 5, 2012)<br><br>Jayakumari j(19July12)<br><br>Tested in U4 and Reasonability low limit is editable. (Jayarajan, Jayakumari Jul 19, 2012) <br> |  | 35 | FINDING | 8624 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73611
29745 | FINDING | Bit details in Point Information window needs to be updated for all point record types | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 8 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While testing SRF1283 - Cutout Sensor Alarms, came across mismatch of bit details in Point Information window. The same needs to be updated as follows:<br>1. LB field of LA &amp; DA record types - Bit 15 (currently showing Reserved)<br>2. LB field of LD, DD, LP &amp; DP record types - Bit 15 (currently showing Not Applicable)<br>3. YF, YG, YH, YI, YJ, YK fields of DA, DD &amp; DP record types - Bit 15 (currently showing Reserved)<br>Snapshot files &amp; remote login infor to DBS drop250 are attached. (Gupta, Chandresh Jul 5, 2012) | none |  |  | Check that fields display correctly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed for U4. (Burgoon, Frank J. Jul 5, 2012)<br><br>cg (07/20/12) - Finding retested in U4. Bit details are displaying correctly at the locations mentioned in the description field above. Hence finding closed.<br><br>These details have to be updated in the related HELP files also. For that I will post another finding against HELP. Thanks!!! (Gupta, Chandresh Jul 20, 2012) <br> |  | 35 | FINDING | 8625 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73613
29746 | FINDING | Style Editor: "Font Family" and "Text Color not working on "Test Properties" option for some algorithms. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Style editor window, In &quot;Text properties&quot; option, &quot;Font Family&quot; and &quot;Tex Color&quot; is not working for the following algorithms:<br>1. ALARM LIMITS,DEVICSX,DFIELD,ANALOG DEVICE,DISTtIBUTOR,MOTOR 2 SPD, DEVICE,FIRST OUT,HEART BEAT,MOTOR,MOTOR 2-SPD,MOTOR 4-SPD,MOTOR NC,PRIORITY,PRIORITY EXT,PRIORITY REJ,RLIC CONFIG,RSR STSTUS,RUNTIME,RVP STATUS,SAMPLER,STATISTICS,VALVE,VALVE NC,CALC BLOCK,DIG CALC BLOCK.<br>2. All FOUNDATION FIELD BUS Algorithms.<br>3. All SAFETY INSTRUMENTED SYSTEM Algorithms.<br>please find attached remote login details. (Joshi, Parmesh Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | No Plans To Fix - Local Attributes in Elements in Symbol Overrides the Cascaded Style Text Settings.<br>- (Hutchison, Steven B. Jul 12, 2012)<br><br>PJ:20-July 2012: As per developer, the problem is because of local attribute overides style text setting, Hence closed. (Joshi, Parmesh Jul 20, 2012) <br> |  | 35 | FINDING | 8626 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73615
29747 | FINDING | On GBNT:New Varalble dialog, [Ok]button gives error message instead of closing the dialog. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Open GBNT: Variable dialog.Right click on Locals/Globals section then selct New Variable.<br>[GBNT: New Variable]dialog opens up. Set the parameteres, press [Apply] button, new variable gets added to lacal/Global section. Then press [ok]button,instead of closing the [GBNT: New Variable]dialog, &quot;Local variable with same name already exists&quot; error message appears.<br>For reference &quot;GBNT variable error message.jpg&quot; scrrenshot is attached (Pandey, Vijay Jul 6, 2012) | NA |  |  | NA | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The OK button is NOT a Close button!! The functionality of the OK button is the same as the Apply button PLUS it then closes the dialog afterwards if there are no errors. Pressing the Apply button to add a new variable and then pressing the OK button afterwards is the same as pressing the Apply button twice. That is why you get the error saying the variable already exists. The &quot;X&quot; button in the top right of any dialog is used to simply close the dialog without performing any function!!! (Johnson, Kathy Jul 6, 2012)<br>Thanks for the explanation. Findinding is closed (Pandey, Vijay Jul 9, 2012) <br> |  | 35 | FINDING | 8627 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73617
29748 | FINDING | SVTP "3.5_CB_SVTP_rev2.7_PJ": Step "5.2.30" is missing. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | On SVTP &quot;3.5_CB_SVTP_rev2.7_PJ&quot;: Step &quot;5.2.30&quot; is missing. (Joshi, Parmesh Jul 6, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-07-06T05:09:48-04:00</p> <p><strong>Modified Date:</strong> 2012-07-06T05:09:48-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8628 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73618
29749 | FINDING | On right pane of the [Add Algorithm] window, symbol and pin information for SIS secure parameters algos are not proper. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps are followed:<br>In Cbeditor, open a control sheet. Click on [Add Control Algorithm] button. [Add Algorithm] window appeared. Expand [Safety Instrumented System]algos. Select[NONSECPARAM/SECPARAM/GSECPARAMREF] SIS secure parameters algos, on right pane of the window symbol for selected algo gets appeared. <br>Observation: For above algos, symbols and pin informations are not proper and nedds to be aligned.For reference &quot;cbeditor sis secure algos symbol.jpg&quot; screenshot is attached. (Pandey, Vijay Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way It Works No Plans To Fix. - (Hutchison, Steven B. Jul 12, 2012)<br>As per developer comments finding is closed. (Pandey, Vijay Sep 2, 2012) <br> |  | 35 | FINDING | 8629 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73620
29750 | FINDING | Field labelled Cutout Sensor is not available in the Alarm Params group of Alarm tab in Point Information window | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Field labelled Cutout Sensor is not available in the Alarm Params group of Alarm tab in Point Information window. Hence, test case 5.4 of TR SRF1283_SVTP_rev1.1.doc could not be done. This is applicable for all point record types. Snapshot file &amp; remote login info to drop250 is attached. (Gupta, Chandresh Jul 6, 2012) |  |  |  | The Point Information window as well as lower level dlls (OvPointInfoDataSource.dll, OvPointDirObjects.dll, and OvCommon.dll) have been updated to display the &quot;Cutout Sensor&quot; field in the Alarm Parameters of the Alarm Tab for LA, LD, LP, DA, DP, and DD points. The software has also been updated to display the &quot;Cutout Sensor&quot; field for each plant mode located on the Plant Mode tab for DD, DA, and DP points. Finally, the LB Field drop down on the configuration tab, has been updated to reflect that bit 15 is the Cutout Sensor bit. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Point Information window will be updated to display the &quot;Cutout Sensor&quot; field in the Alarm Parameters of the Alarm Tab for LA, LD, LP, DA, DP, and DD points. It will also be updated to display the &quot;Cutout Sensor&quot; field for each plant mode located on the Plant Mode tab for DD, DA, and DP points. The LB Field drop down on the configuration tab, will also be updated to reflect that bit 15 is the Cutout Sensor bit. (Augustine, Lisa Jul 10, 2012)<br><br>cg (07/20/12) - Finding retested in U4. Cutout Sensor field is properly appearing in the Alarm tab (for LA/LD/LP/DA/DD/DP points) &amp; Plant mode tab (for DA/DD/DP points) in PI. Hence this finding is closed. (Gupta, Chandresh Jul 20, 2012) <br> |  | 35 | FINDING | 8630 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73622
29751 | FINDING | OCR1100 controller could not be loaded after doing changes in LP point"s bit assignment to output channels of DO card | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In OCR1100 DROP35/DROP85 created a Packed Point and assigned its few bits to Digital Output card&quot;s output channels. Loaded the controllers. The I/O points worked as expected. Now removed the IO channel assignment from one of the bits while keeping IO module assignment as is e.g. 1.2.2 Digital Output 5-60 VDC. Tried to load the controller. Load operation got hanged at the stage &quot;Retrieving Point list from Target&quot; and Developer studio had to be killed to abort the operation.At one instance Load operation (after a long wait) ended up with the Error &quot;DROP35&quot; is unavailable. The problem was shown to Ben.The snapshots of error messages are attached with the finding. (Lal, Ramesh Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 7/6/12 - please check if this behavior is the same/different in a OCR400 and update the Description. Thanks! (Capani, Nooch Jul 6, 2012)<br><br>This problem is due to an invalid configuration. The controller has no way to determine that the point is not completely configured. Most likely the hd, it, bp fields are set randomly and could contain values that are in range. The only way to prevent this is through a database check. I am marking this as the Way it Works. (Pingree, Douglas K. Jul 6, 2012)<br><br>7/09/12:RL - When user does changes in LP point bit allocation to I/O channels this type of situation is not very uncommon.If there are large number of points, then it will be difficult for the use to manually detect the problem. Therefore, under such situation the user should be warned at the configuration stage itself. Please forward the finding to the concerned person who can provide some feature to detect the problem so that controller hang situation could be avoided. (Lal, Ramesh Jul 9, 2012) (Pingree, Douglas K. Jul 10, 2012) <br> Forwarding to Kim Costlow for evaluation. (Pingree, Douglas K. Jul 10, 2012)<br><br>This issue was resolved. Please retest. (Costlow, Kimberly A. Jun 3, 2013) |  | 35 | FINDING | 8631 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  | 1/14/2014: The problem still exists in 3.5.0 (and also in 3.5.1)hence this finding was kept open. But in view of Developer&quot;s suggestion to perform Developer Studio&quot;s Consistency check to identify such situation, the finding is closed. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73624
29752 | FINDING | During loading OCR1100 controller, Developer Studio become closed. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 7 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step Followed:-<br>1:- Create a Control sheet in Drop18/Drop68 controller &amp; add the AND Algo.<br>2:- Complie the above created sheet . It is successfully compleated.<br>3:- Load the Drop18.<br>4:- During loading , it is observed that Studio is not responding it become hang.<br> Now clik on the loading window , &quot;Ovation Developer Studio for Window application file &quot; <br> Window is appear.<br> As shown in screen shots&quot;OV_Win_App_File.jpg&quot;<br>5:- Now press the Close the program Option. Studio become closed.<br><br>For more information Please the attachment(OV_Win_App_File.jpg, 18-3-5001-GA_BOOL_ALGO.svg,<br> Ovation Error Log, Win Application log error.jpg ) (Agarwal, Gaurav Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Based on information in the attached Ovation Error Log:<br>7/5/2012 4:00:03PM - Attempted load to drop18.<br>The log indicates that sheet [5001_GA_BOOL_ALGO] in Task 3 was loading and the control task was closed. However, we do not see a corresponding &quot;Load Completed&quot; message for drop18.<br><br>Another load attempt of drop18 was made at 7/5/2012 16:03:57. A corresponding &quot;Load Completed&quot; message was displayed at 7/5/2012 16:09:53. The assumption is that this was successful.<br><br>Another load attempt of drop18 was made at 7/6/2012 08:57:47. This load also does not have a corresponding &quot;Load Completed&quot; message, but it corresponds to the attached snapshot of the Ovation Studio Hang message in the Windows Application Error Log at 7/6/2012 09:00:59.<br><br>More information required:<br><br>Please confirm if the above interpretation of the Ovation Error Log is correct.<br><br>Please confirm if the initial load of this sheet (at 7/5/2012 4:00:03PM) succeeded, failed, or crashed the Studio.<br><br>Please confirm whether or not the subsequent load of the sheet (at 7/5/2012 16:03:57) succeeded.<br><br>Please state what changes were made to drop18 (the controller and the database associated with the controller) between the load attempts on 7/5/2012 16:03:57 and the &quot;final&quot; logged load attempt on 7/6/2012 8:57:47. (Swartz, Mark E. Jul 6, 2012) <br> The Ovation Developer Studio does not crash, it hangs waiting for a response from the controller. If the user clicks on the update dialog, they are given a choice as to whether or not to continue waiting. If the user chooses to wait, the error which is eventually reported is a PEDIT return code of 11, which indicates a timeout.<br>It appears that incremental loads are problematic due to timeout problems from the controller (in particular, PEDIT). Transferring to the controller group for further investigation. (Swartz, Mark E. Jul 9, 2012)<br><br>IC 8/6/12 - issue degrades system use, changed to CAT 2. (Capani, Nooch Aug 6, 2012)<br><br>Please specify specific PEDIT error that is returned. (Pingree, Douglas K. Aug 22, 2012)<br><br>GA:-<br>Following Error Message is popping up.<br>&quot;<br>*--------------------&gt; Error Information &lt;--------------------*<br>Unable to complete the requested operation <br>Code : 0x80004005 Source : Ovation Developer Studio<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br>&lt;OvSysPtUserObject.cpp:2921&gt; [External]: (Unable to update target sequence number)<br>&lt;OvSysPtUserObject.cpp:12756&gt; [External]: (error (11) from PEDITSimpleModify, OpStat = (0), ErrNum = (0))<br>&lt;OvSysPtUserObject.cpp:12752&gt; [External]: (error modifying drop point for target &quot;DROP68&quot;, SID (0x80000044))<br>&quot;<br>For more information please find the attached screenshot &amp; OvPtStudioErr_Drop18_68.txt file. (Agarwal, Gaurav Aug 22, 2012)<br><br>Corrected deadlock issue between gni_admd and pedit. Please test with U8. (Pingree, Douglas K. Sep 11, 2012)<br><br>ga:-<br>Used build:- Ov 3.5.0_U9<br>That issue has been resolved &amp; incrmental load is working fine . Hence finding is closed. (Agarwal, Gaurav Sep 25, 2012) |  | 35 | FINDING | 8632 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73626
29753 | FINDING | In OCR1100 Controller hard wired LP point bits are reported incorrectly | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In OCR1100 Controller DROP35/DROP85 Bit 10 of LP point D35-LP-I3 is connected to channel#8 of Digital Input card and Bit 15 to Channel#16.Values of these bits are reported correctly (1) when Terminal B &amp; Terminal C are shorted by wire. Now IO channel# 8 is removed from bit 10 in the Developer studio while IO module is still &quot;1.2.1 Contact Input w/Onboard 48V wetting&quot;. After loading the controller it is observed that channel#8 still remains assigned to bit 10 in the PI and bit 10 continues to toggle between 0 and 1 (though there is no shorting done at Terminal B nnd Terminal C for channel#8. Please refer the snspshot attached with the finding. (Lal, Ramesh Jul 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 7/6/12 - please check if this behavior is the same/different in a OCR400 and update the Description. Thanks! (Capani, Nooch Jul 6, 2012)<br><br>RB 9/20/12 - Please re-test in U8. (Boehmer, Robert W. Sep 20, 2012)<br><br>9/24/12:RL - Retested on OCR400 Controller in 3.5_U9. The behaviour is same. Finding failed retest. (Lal, Ramesh Sep 24, 2012)<br><br>When a point is setup for hardware and no channel is specified the controller uses the default channel 1. The reason the bit was toggling was that on the card channel 1 is toggling due to being driven by a relay. It may be an issue though that dev studio allows a point to be defined in such a way (Christy, Benjamin Oct 19, 2012)<br><br>Per Ben&quot;s explanation I am changing this to Works As Designed. This is not a controller issue. (Boehmer, Robert W. Nov 1, 2012)<br>---<br>msb - Closed: converted to SDR 19266 (Benzvi, Mati Nov 29, 2012) <br> 11/14/12:RL - Based on Ben&quot;s observation, it would be appropriate if Developer&quot;s studio reports<br> error if it detects a faulty configuration similar to the one described above.<br> Hence, the responsible engineer is being changed for this finding. (Lal, Ramesh Nov 14, 2012)<br><br>11/19/12:RL -The responsible engineer changed to Mark Swartz. (Lal, Ramesh Nov 18, 2012)<br><br>Note that the attached screen shot does not indicate that the target drop has been loaded, since the Point Information application should show the same information on the Hardware tab as what is shown in the Ovation Developer Studio -- something is not refreshed or up-to-date. However, further investigation does confirm the observed incorrect behavior which is the issue raised by this Finding.<br><br>The software will be changed to treat a packed point bit configured in this way (i.e., IO_Location is specified but IO_Channel is not) as a non-hardware point OR to prevent this type of configuration during the save of the point via object-level validation (as is done with Analog points).<br>Note that this issue also exists for digital (and deluxe digital) points.<br>Note that his behavior is also not new to Ovation 3.5. (Swartz, Mark E. Nov 21, 2012) |  | 35 | FINDING | 8633 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73628
29754 | FINDING | Changing Controller Type from OCR161 to OCR400/OCR1100 causes an error message to be displayed. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | An error window appears in Studio when an imported OCR161 is changed to an OCR400 or OCR1100, although the Controller Type modification appears to be successful. The error message shows [Unknown or unsupported Controller Style]. (Brown, Sean Jul 9, 2012) |  |  |  | The affected area is in the format of the error message which is reported when a controller with an unsupported style is encountered. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Are there any other OCR161 &quot;controllers&quot; currently in the database which have not yet been converted? (Swartz, Mark E. Jul 9, 2012)<br><br>OCR161 VirtualController Drop148 is currently being imported to the EMILY system. (Brown, Sean Jul 9, 2012)<br><br>These error messages were due to the fact that there were additional OCR161 style controllers present in the database. The error message will be modified to indicate the name and object key of the particular controllers which are still OCR161. (Swartz, Mark E. Jul 9, 2012)<br><br>OK in U4; closing. (Brown, Sean Jul 31, 2012) <br> |  | 35 | FINDING | 8634 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73630
29755 | FINDING | Need to udate SVTP 3.5_SRF1633_SVTP_rev1.3_GA.doc, That "ALARM OFF Delay" replace with Alarm return delay time. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Need to update SVTP 3.5_SRF1633_SVTP_rev1.3_GA.doc that &quot;ALARM OFF Delay&quot; should be replace with &quot;Alarm return delay time&quot;. <br><br> For more detail please find the attach Screenshot &quot;Alarm Return delay.jpg&quot; (Agarwal, Gaurav Jul 10, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2012-07-10T10:36:45-04:00</p> <p><strong>Modified Date:</strong> 2012-07-10T10:36:45-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8635 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73631
29756 | FINDING | Newly-defined OCR400 Controller fails after being loaded with Ladders (11/61 for DB Server Drop135). | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400 Controller 11/61 (SIS) was imported/moved from an Ovation 3.3.1 system. 11 fails after being loaded. The Error Buffer messages say that Task 3 is being stopped. Ben was looking into the problem; this finding is being created to document the issue. (Brown, Sean Jul 10, 2012)<br><br><br>The problem appears to be ladder related.<br>- (Hutchison, Steven B. Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Transferring to Kuba. Kuba, please work with Ben if necessary. (Pingree, Douglas K. Aug 3, 2012)<br><br>It is highly probable that this the same issue as the one tracked by finding 8705. Can I get access to that system to confirm that? (Czak, Jakub Aug 4, 2012)<br><br>This issue is not SIS problem. Controller does not have SIS I/O device defined. After load CTTask crashes when executing Alg_LadderSolver function. Sheet that contains those algorithms compiles but during compilation &quot;Unexpected Special Function Type&quot; error message is displayed. (Czak, Jakub Aug 8, 2012)<br><br>After resolving the errors in the control sheet, the drop still fails. The errors mentioned above were using Deluxe Points for a special function in a 7x9 ladder.<br>- (Hutchison, Steven B. Aug 8, 2012) <br> IC 9/27/12 - close, track as SDR 19061. (Capani, Nooch Sep 27, 2012) |  | 35 | FINDING | 8636 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73633
29757 | FINDING | Correct functionality of SIS analog IO channel[Bad If Limited,Over Range,under range] attributes need to be documented. | Maggu, Mukesh EMR SYSS PWS NOIDA | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | SIS analog point not go Bad state on exceeding Point value than configured Analog percent range. Steps are followed: Configured SIS analog type IO channel and its [Bad If Limited]attributes to checked or active state. Loaded [SLS01]Logic solver1. While loading logic solver [Confirm]window appeared, there is no astrisk sign before the channel which attributes modified. [Bad If Limited]attribute option is not modifying its state for SIS all Analog type channel.<br>For reference &quot;SIS AI ATTRIBUTES-SLS LOAD.jpg&quot; screenshot is attached. Open the point in PI, on exceeding the Analog point value than configured Analog percent range, Analog point not go to Bad state. <br><br>&quot;Ovation_gateway_new_drop250_login_steps_1.docx&quot; file for Remote Login steps is attached. (Pandey, Vijay Jul 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Analog over range percentage means how much value of the point can go over top of scale before bad quality is set. That means this attribute cannot be set below top of scale. In case of incorrect configuration Logic Solver uses default value. The same applies to &quot;Analog under range percantage&quot;.<br><br>&quot;Bad if limited&quot; attribute is set for channel but actually it is parameter of LSAI block. Setting that option for a channel means that this parameter will be used in every LSAI assigned to that channel. When you change it, during load asterisk should be placed next to every Control Module that uses LSAI algorithms assigned to given channel.<br><br>Please verify if setting over and under range attributes correctly works as expected and if changing &quot;Bad if limited&quot; attribute marks appropriate control modules as modified during LS load. (Czak, Jakub Jul 11, 2012)<br><br>VP 07/16/12- Functionality of [Bad if limited, over range, under range] attributes are observed as mentioned below, It is different from functionality given in existing document. Observation: &quot;Analog over range&quot; is an attribute of channel, it is in percents and doesn&quot;t have anything to do with &quot;Top of scale&quot;. It says at what point high limit should be set on channel. It also can be set below 100. &quot;Bad if limited&quot; is parameter of LSAI, In Ovation it is configurable from channel level because Status of output from LSAI should be bad if channel is in high or low limit state. If additional block to LSAI output (e.g. AVTR) is added then bad status is propagated to next algorithm even though quality of Ovation point assigned to given channel is still good. <br><br>Correct function of &quot;Bad if limited&quot;, &quot;Analog over range&quot; and &quot;Analog under range&quot; attributes need to be documented. (Pandey, Vijay Jul 16, 2012) (Ritenbaugh, David W. Aug 6, 2012)<br><br>VP-10/23/12- Retested in 3.5.0_U9. studio help document not updated. (Pandey, Vijay Oct 22, 2012) <br> |  | 35 | FINDING | 8637 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73635
29760 | FINDING | SIS sensor alarms not working | Hutchison, Steven EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Empty sheet with ALRM number is created in one of control modules. During LS load it should be filled automatically with logic required for SIS sensor alarms generation. This functionality is not working. (Czak, Jakub Jul 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed (Template File Not Released) - (Hutchison, Steven B. Jul 12, 2012) <br> |  | 35 | FINDING | 8640 |  | FINDING | [10 empty] | Implementation | 3.5.0_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73640
29762 | FINDING | During Clear the Controller,virtual controller goes into failed mode. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step Followed:- <br>1:- Open the Developer studio &amp; go to Virtual controller drop(e.g:-Drop145)<br>2:- Open the point processing configuration window &amp; enabled the Millisecound Resolution.<br>3:- Download the drop. it is successfully downloaded.<br>4:- Clear the controller.<br>5:- it is observed that after some times Virtual controller drop goes into failed mode. (Agarwal, Gaurav Jul 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Enabled 1ms OPP in a virtual controller. Downloaded, reboot, cleared, loaded repeatedly. Can not duplicate. (Perdeus, Matthew Oct 31, 2012) <br> |  | 35 | FINDING | 8642 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73644
29763 | FINDING | In studio, most of SIS IO channel attributes repeated two times in Add Column list, shows different value on selection. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In studio, expand SLS01- right click on SIS I/O channel and select search option. [Add column] window for attributes get appeared. Most of IO channel attributes repeated two times in listFor reference &quot;&quot;SLS IO CHANNEL ATTRIBUTES REPEAT.jpg&quot; is attached.e.g. There &quot;Detect open and short circuit&quot; option available two times . Screenshot &quot;SLS IO CHANNEL DET N OPEN SHRT CIRCT.jpg&quot; is attached. On selecting two option, two column with same &quot;Detect open and short circuit&quot; attribute get appeared. One shows correct configuration other shows incorrect attribute configuration. For reference screenshot &quot;SLS IO CHANNEL ATTRIBUTES COLOUMN.jpg.&quot; (Pandey, Vijay Jul 13, 2012) (Swartz, Mark E. Jul 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it works (works per design). The SIS I/O Channel database objects were defined/designed to have various duplicate sets of attributes. When editing a SIS I/O Channel via Open in the Ovation Developer Studio, the Channel Type attribute dictates which set of attributes are shown/hidden on the Attribute tab. (Swartz, Mark E. Jul 13, 2012)<br>VP-07/13/12- Same attribute for a channel shows different configuration in two column. For reference screenshot &quot;SLS IO CHANNEL ATTRIBUTES COLOUMN.jpg.&quot; is attached.Please see the steps. Steps are followed: Configured SLS01&quot;S IO channel-1 as LSDI, &quot;Detect and Open circuit&quot; attributes is checked or enable. For reference screenshot &quot;SLS DI CHANNEL ATTRIBUTES.jpg&quot;. In studio, expand SLS01- right click on SIS I/O channel and select [Search] option. [Add column] window for attributes get appeared. There is &quot;Detect open and short circuit&quot; option available two times . Screenshot &quot;SLS IO CHANNEL DET N OPEN SHRT CIRCT.jpg&quot; is attached.<br>select both option and [OK]. Two column with same &quot;Detect open and short circuit&quot; name get appeared. One shows correct configuration other shows incorrect attribute configuration. For reference screenshot &quot;SLS IO CHANNEL ATTRIBUTES COLOUMN.jpg&quot; is attached. (Pandey, Vijay Jul 13, 2012)<br><br>Those are NOT the same attribute. They are different attributes -- different items in the database. They were designed with the same name and label, hence your confusion. The search column which you state has the incorrect attribute configuration was hidden when the IO channel-1 was first edited. All attributes show up in the search window and can be brought up in the Search dialog -- even those attributes which are not applicable to the Channel Type. When the SIS I/O Channel is opened (the full edit dialog), the proper attributes (those that are used internally throughout the Ovation system) are displayed. These are the proper attributes which are eventually loaded to the Logic Solvers. (Swartz, Mark E. Jul 13, 2012)<br><br>Thanks for the detailed explanation. Finding is closed (Pandey, Vijay Jul 13, 2012) <br> |  | 35 | FINDING | 8643 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73646
29764 | FINDING | In TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc, test case 5.1.1 & 5.1.2 needs to be changed for latest OS platform | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc, test case 5.1.1 says about Win Server2003 OS platform &amp; 5.1.2 says about XP OS platform. Since Ov3.5.0 does not support Win Server2003 &amp; XP the test cases needs to be changed to Win Server2008 &amp; W7 respectively. (Gupta, Chandresh Jul 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Securtiy (WSEC)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-07-13T05:07:03-04:00</p> <p><strong>Modified Date:</strong> 2012-07-13T05:07:03-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8644 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73647
29765 | FINDING | In TR 3.5_SystemTests_SVTP_rev2.D_CG.doc, test case 5.3.14 needs to be changed to say Kaspersky | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In TR 3.5_SystemTests_SVTP_rev2.D_CG.doc, test case 5.3.14 says to install Symantec Anti Virus software. However, 3.5.0 supports Kaspersky Anti Virus software &amp; we have KAV clients installed on 3.5.0 drops in IEC. Hence the test case needs to be changed accordingly. (Gupta, Chandresh Jul 13, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> System Test (ST)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-07-13T05:32:45-04:00</p> <p><strong>Modified Date:</strong> 2012-07-13T05:32:45-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8645 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73648
29766 | FINDING | Drop245 (DBS) system is much slower than other System in the same network. | Augustine, Lisa EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Drop Details:- <br>Drop:- Drop245(DBS)<br>OS:- Win2K8 R2 Standard, SP1, 64bit Operating System<br>OCR 1100 Controller Drop:- Drop18/drop68 <br> <br>It is observed that when performed either operator or Engineering function in this drop, <br>it become much slower than other drop in the same system.<br><br>For more information please find task manager the Screen shots &quot;Wind Task Manager.jpg&quot; (Agarwal, Gaurav Jul 16, 2012)<br><br>IC 8/6/12, per SCB: if you remote into 245, operation seems to be at normal speed. (Capani, Nooch Aug 6, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Augustine, Lisa</p> <p><strong>Notify List:</strong> Augustine, Lisa Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2012-07-16T14:54:08-04:00</p> <p><strong>Modified Date:</strong> 2012-08-06T16:29:29-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8646 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73649
29767 | FINDING | In TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_SDK.doc, test case 5.6 needs to be changed for latest OS platform. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_SDK.doc, test case 5.6 (User &amp; Computer Group Policies ),some test cases test only on XP OS platform . Since Ov3.5.0 does not support Win Server2003 &amp; XP the test cases needs to be changed to Win Server2008 &amp; W7 respectively. (Kumar, Sudheer Jul 17, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Securtiy (WSEC)</p> <p><strong>Release Level:</strong> 3.5.0_U3 05-JUN-12</p> <p><strong>Originator:</strong> Kumar, Sudheer</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Kumar, Sudheer</p> <p><strong>Entry Date:</strong> 2012-07-17T01:37:16-04:00</p> <p><strong>Modified Date:</strong> 2012-07-17T01:37:16-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8647 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73650
29768 | FINDING | All OCRs have UNKNOWN states for both network channels. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400s and OCR1100s have fixed values of K0=0 and K1=0 for DU records since U4 was installed. This makes it impossible to determine the status of each channel. (Brown, Sean Jul 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected states for all controllers. (Pingree, Douglas K. Jul 30, 2012)<br><br>UNKNOWN states no longer being reported in U5; closing.<br><br>NOTE: OCR1100s show correct states, however OCR400s still reporting Backup connection as Failed for Single configuration (Finding 8381). (Brown, Sean Aug 6, 2012) <br> |  | 35 | FINDING | 8648 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73652
29769 | FINDING | Ovation Install of U4 cannot open Studio, unable to update Device Catalog | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Upon upgrade of 3.5.0 to U4 on 2 Servers, when Studio is started, it get stuck at:<br> [Updating Device Catalog, please wait...].<br>The C:\Program Data\Syconet\Netdevice\DevCatalog.XML is not updated with PF &amp; DN data.<br> (size = 1 kb instead of 13 kb)<br><br>Workaround to continue without updating the DevCatalog.XML<br>Set registry: SyconIgnoreCatalogUpdate = 1<br>--<br>In the Pgh Lab: Problem seen on DBS 125 &amp; 245, OK on DBS 135. (Benzvi, Mati Jul 17, 2012) | During testing it was observed on certain drops that when Studio was started, it hung with this message being displayed: [Updating Device Catalog, please wait...]. This error causes the C:\Program Data\Syconet\Netdevice\DevCatalog.XML to not update properly resulting in the inability of doing Profibus and DeviceNet engineering changes. The problem occurs becuase of the corruption to MSXML 4.0 SP3 Parser (KB2721691) Solution: Repair KB2721691 KB2721691 is part of MS12-043 patch released in Jul-2012 Direction: Insert the latest MS-W7_WS08 Patch DVD. In MS12\ms12-043 directory, double click on msxml-KB2721691-enu.exe Choose the Repair option. Remove the SyconIgnoreCatalogUpdate = 1 registry entry (or set it to 0) Start Studio. |  |  | Open Studio on each 64b drop | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - 9/26 -<br> Problem occurs because of the corruption to MSXML 4.0 SP3 Parser (KB2721691)<br> Solution: Repair KB2721691<br> KB2721691 is part of MS12-043 patch released in Jul-2012<br> Direction: <br> Insert the latest MS-W7_WS08 Patch DVD.<br> In MS12\ms12-043 directory, double click on msxml-KB2721691-enu.exe<br> Choose the Repair option.<br> Remove the SyconIgnoreCatalogUpdate = 1 registry entry (or set it to 0)<br> Start Studio. (Benzvi, Mati Sep 26, 2012) (Benzvi, Mati Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19174 (Benzvi, Mati Oct 24, 2012) <br> IC 9/27 - updated DIR Info. (Capani, Nooch Sep 27, 2012) |  | 35 | FINDING | 8649 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | SDR/DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73654
29770 | FINDING | Ovation System Registration utility is missing in U4 build. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When the system is upgraded from U3 to U4, OvSysRegAgentUI.exe is missing from C:\Ovation\SystemRegistration\Bin . Hence application could not be run. (Singh, Ghanshyam Jul 18, 2012)<br><br>This is under investigation. This might be related to Ovation installer issue. (Quintos, Ronaldo M. Jul 20, 2012)<br><br>GS:(08/22/2012)-Tested in U6 and found fixed. Hence finding is closed. (Singh, Ghanshyam Aug 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8650 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73656
29771 | FINDING | TELNET to the Controller drop in cmd window shows -&gt as default path | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1. Open Command Prompt window.<br>2. Type &quot;telnet dropxx&quot; where xx is the Controller drop.<br>3. Till U3 build the default path appearing in cmd prompt window was &quot;[ocr400] dropxx&gt;&quot;.<br>4. In U4 build the default path appearing is &quot;-&gt;&quot;.<br>This creates confusion to the user as to whether telnet was successful or not. (Gupta, Chandresh Jul 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Telnet is only being used temporarily for validation and debugging purposes. It will be removed by the end of the 3.5 release. (Pingree, Douglas K. Jul 27, 2012)<br><br>cg (07/30/12) - Based on the developers comments this finding is closed. (Gupta, Chandresh Jul 30, 2012) <br> |  | 35 | FINDING | 8651 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73658
29772 | FINDING | Milisecound resolution is not change, while alarm is creating preodically. | Perdeus, Matthew AUTOSOL PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Drop:- Drop245<br>OS:- Win2k8 R2 Standard, 64bit, SP1<br>OCR1100 Controller:- Drop18/68<br><br>1:- Create a Ovation either controller or drop points(e.g:-LA, DA, LD etc.)<br>2:- Enable the milisecound resolution in controller &amp; MMI.<br>3:- Open the Alarm window.<br>4:- Now create a alarm from above created points.(e.g:- Suppose XXX_LA is a Analog point&amp;<br> Alarm is created at 8:22:32:756 PM )<br>5:- After some time alarm goes into return state &amp; again create a alarm.<br>6:- Repeats the above step 5 to 6 times then it is observed that Milisecound resolution is always same .<br> <br><br>Note:- Above points are not configured in I/O &amp; sheets.<br><br>For more information please find the attached screen shots&quot; Unchanged Milisecound resolution.jpg&quot; (Agarwal, Gaurav Jul 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | For a non-I/O or non-control point, this would be expected, at least in the short term testing period. These points are still alarmed by OPP which always triggers at the same time. Try looking at U5 and U7 fields to see if they are changing. (Perdeus, Matthew Sep 10, 2012)<br><br>GA:- <br>As per developer comment check U5 &amp; U7 Fields , It is observed that when checked With Real Controller Points,These are changing but when checked with Vitual controller points, Thease are not chaning. (Agarwal, Gaurav Sep 13, 2012)<br>GA:- <br>I checked real I/O &amp; Control points, Milisecound resolution is not chaning, while alarm is creating preodically (Agarwal, Gaurav Sep 13, 2012)<br><br>Is the latest comment in regard to virtual controllers only? (Perdeus, Matthew Oct 17, 2012)<br><br>GA:-<br>The Latest comment is regard to Real Controller. (Agarwal, Gaurav Oct 17, 2012)<br><br>Please retry this with points in a control task other that 1000 ms. (Perdeus, Matthew Oct 18, 2012) <br> |  | 35 | FINDING | 8652 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73660
29773 | FINDING | GBNT Macro number portion of macro name is exceeding the defined range. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovtion 3.5.0_U4, GBNT Macro Number portion of macro name is exceeding the defined range. According to manual defined range is (0-65535). (Kumar, Sudheer Jul 19, 2012) | LC 09/11/2012: Updated the MACRO Command to provide correct information on naming macros. |  |  | LC 09/11/2012: Check the MACRO Command section for updates. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a documentation error in the Graphics Language Reference mannual. The MACRO command must not have been updated with the 3.3.1 changes to support macro names (alphanumerics, dash, underscore chars only - up to 35 chars in length). Prior to Ovation 3.3.1, macros were named by number(1-65535). Now, however, the macro can be named by any series of up to 35 digits (or any of the other previously noted chars). Examples: macro1234567890l.src, macro_this_is_a_valid_name.src, macronotlimitedtoanumber.src, macro999kathy6666.src, ... (Johnson, Kathy Jul 23, 2012) <br> LC 09/11/2012: Updated the MACRO Command in the help file and the Graphics Language manual to provide the correct information on naming macros -- only 35 characters. This change will be in the U8 build. (Casteel, Linda Sep 11, 2012) |  | 35 | FINDING | 8653 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73662
29774 | FINDING | OCR1100s often get stuck in Startup/Offline mode during boot. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Since updating to U4, there have been multiple instances of OCR1100s not going into Control or Backup after a reboot. Two examples:<br><br>1. 32/82 (EMILY). 32 was downloaded with U4 and soft-rebooted; 82 had been been downloaded with U4, but had not been rebooted. 82 was in Control. 32 got stuck in Offline/Startup while booting. When a soft reboot was eventually performed on 82, 32 went into Control; 82 booted up normally and went into Backup. The controllers behaved correctly after subsequent soft and hard reboots (the problem did not occur again). The same behavior occurred with 18/68 (WALT) when it was updated with U4.<br><br>2. At some point after 18/68 failed over correctly several times, power was lost in the lab. When it was restored, 18 and 68 powered up simultaneously. 18 was stuck in Offline/Startup mode. Rebooting the partner allowed 18 to change to Control. (Brown, Sean Jul 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Unable to recreate. The validation system had mis-matched U&quot;s. Monitor. (Ciccozzi, Anthony Sep 10, 2012)<br><br>The problem also occurred when both OCR partners had the same software. However, this issue has not been recently observed. Closing. (Brown, Sean Sep 20, 2012) <br> |  | 35 | FINDING | 8654 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73664
29778 | FINDING | Trend window is crashing when window is maximized | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps are as follows:<br>1. Open Signal Diagram window containing some logic.<br>2. Select a point LA/LD --&gt; right click --&gt; select &quot;Trend&quot; from context menu.<br>3. Trend window opens &amp; starts populating the selected point with all its attributes.<br>At this moment MAXIMIZE the window by double clicking on the title bar.<br>Doing so the Trend window pops up a subwindow saying &quot;Unhandled exception has occurred in your application&quot;. Please refer the attached snapshot trend_crash_U4.jpeg. The details are as shown in the attached text file trend_crash_details_U4.txt. <br>4. Upon clicking &quot;Quit&quot; button the Trend window goes away.<br><br>Remote login steps to drop250 (Net#7 DBS) is also attached. (Gupta, Chandresh Jul 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest in 3.5.0_U6 (Bargaje Prashant Aug 9, 2012)<br><br>cg (08/21/12) - Finding retested in 3.5.0_U6. Now trend window is not crashing. Hence finding closed. (Gupta, Chandresh Aug 21, 2012) <br> |  | 35 | FINDING | 8658 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73671
29779 | FINDING | Setpoint/MAStation algorithm output values keep on increasing/decreasing after button is released. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 6 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps to recreate are as follows:<br>1. Created a Control Sheet containing SETPOINT, PID, MASTATION &amp; LEADLAG algorithms.<br>2. Saved, Compiled &amp; Loaded the control sheet in Net#7 drop32.<br>3. Opened the created control sheet in Signal Diagram. By default the &quot;Algorithm Control&quot; window appears at the right pane alongwith &quot;Properties Summary&quot; window.<br>4. Drag the &quot;Algorithm Control&quot; window from right pane &amp; drop it to the bottom of Signal Diagram. So this window will align with &quot;Event Log, Algorithm summary &amp; Function Summary&quot; windows.<br>5. Select MASTATION or SETPOINT algorithm. In &quot;Algorithm Control&quot; window click on &quot;Increment Output or Increment Bias value&quot; button. Doing so the output value of the algorithm increments once. <br>6. Now again click on the same button. This time the value increments &amp; keeps on increasing forever (if not stopped by clicking on any other algo on that sheet).<br>7. Same behavior happens upon clicking &quot;Decrement Output or Decrement Bias value&quot; button. This time the algorithm value keeps on decreasing until stopped.<br>Also, the Event Log of Signal Diagram keeps on flooding with the New &amp; Previous value details.<br>Please refer the attached snapshot file Increment-decrement-values.jpg.<br>Remote login details file to drop250 (Net#7 DBS) is also attached. (Gupta, Chandresh Jul 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Unable to Duplicate - Please review the description and enhance the description of steps 5 or 6. Some facts may include; How long is the button pressed, Which buttons are pressed, How the mouse is moved, etc.,<br><br>- (Hutchison, Steven B. Aug 15, 2012)<br><br>cg (08/16/12) - I am able to duplicate the scenario on Net#7 DBS drop250 (whose remote login details are attached). Please note that we have Ovation 3.5.0_U4 build here. <br>Also attached are 2 snapshot files:<br>1. Increment-decrement-values1.jpg - showing the MAStation selected &amp; Event Log window (marked with RED box).<br>2. Increment-decrement-values2.jpg - showing the MAStation selected &amp; Increment/Decrement Output button (marked with RED box).<br>The issue occurs during 2nd or 3rd time of mouse button click &amp; not during 1st time. These buttons are just given a single click. Press the mouse LEFT button &amp; release it immediately. The mouse is kept on the buttons itself.<br>Action field of the finding is changed to DRR. (Gupta, Chandresh Aug 16, 2012)<br><br><br>Cannot Duplicate - I still could not duplicate this issue. I have changed cbViewer to further guard the inc/dec buttons. Please place cbViewer.exe into %CB_HOME% and retest. If it works I will release it to the library and include it in U7<br>- (Hutchison, Steven B. Aug 16, 2012)<br><br>cg (08/17/12) - The new cbViewer.exe file was placed on Net#7 EWS drop251 into %CB_HOME% &amp; tried to duplicate the issue. This time the Increment/Decrement buttons worked fine &amp; values of algorithm were just increasing/decreasing as per the clicks of these buttons. Please see the attached snapshot file Incr-Decr-newcbviewer.jpg showing the Event Log. (Gupta, Chandresh Aug 17, 2012) <br> Fixed - (Hutchison, Steven B. Sep 4, 2012)<br><br>cg (09/19/12) - Finding retested in Ov3.5.0_U8. Working fine hence closed. (Gupta, Chandresh Sep 19, 2012) |  | 35 | FINDING | 8659 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73673
29780 | FINDING | Logic Solver firmware upgrade "Ovation.Sis.SlsUpgrade.Console.exe" tool is not available in C:\Ovation\OvationBase. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Logic Solver firmware upgrade &quot;Ovation.Sis.SlsUpgrade.Console.exe&quot; tool is not available in C:\Ovation\OvationBase. For reference &quot;ovation.sis.slsupgrade.console missing in ovationbase.jpg&quot; screenshot of cmd session is attached. (Pandey, Vijay Jul 20, 2012) (Czak, Jakub Jul 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem was caused by incorrect Visual Studio project settings. (Czak, Jakub Jul 23, 2012)<br>VP: retested with 3.5.0_U6, found fixed. Hence finding is closed. (Pandey, Vijay Aug 24, 2012) <br> |  | 35 | FINDING | 8660 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73675
29781 | FINDING | Base Station 128 originates 47999 points fails to dropload after upgrade to U4 | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Base Station (128) was configured with: Maximum Point Limit: Expanded (48000 Pts) and loaded<br>successfully in U3 with 47999 originated points by Traffic sheets.<br>After the upgrade to U4, every dropload fail with error:<br>*--------------------&gt; Error Information &lt;--------------------*<br>Unable to complete the requested operation <br>Code : 0x80004005 Source : Ovation Developer Studio<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br>[External]: (object not loaded)<br>[External]: (failure during point load)<br>[External]: (subsequent error (6) from PEDITModify, OpStat = (7), ErrNum = (5))<br>[External]: (Attempted to recover by issuing modify command, resulting in:)<br>[External]: (SHC_E_PT_EXISTS: point to be added already exists)<br>[External]: (during load of Object &quot;D128-LC-DATAMAPALG-04998&quot;, key (149139), SID (0x80023832))<br>--------------------------------------------------------------<br>I attempted to clear and reload a couple of times, but still getting the error. (Benzvi, Mati Jul 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Works OK after deleting few localy Originated points.<br> Reference to Alarm limit points originated by another drop in 10 local points pushed<br> the total count of points (Originated + Recieved) over the 48K limit. (Benzvi, Mati Jul 21, 2012) <br> |  | 35 | FINDING | 8661 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73677
29782 | FINDING | White over Silver footer of Ovation Point Browser is hard to read | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The color of the Footer message of the [Ovation Point Browser] in Point Info, Trend, etc.<br>when using the Default selection = [Color Scheme: Silver] is FG = White over BG = Silver.<br>Pretty hard to read for my aging eyes.<br>Please echange the foreground to Black. (Benzvi, Mati Jul 20, 2012) | none |  |  | Point Browser status bar. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Silver color scheme corrected. (Burgoon, Frank J. Jul 27, 2012)<br>---<br>msb - OK in Ov-3.5.0 @ 10-Aug-2012<br> [Color Scheme: Silver] is FG = Black over BG = Silver (Benzvi, Mati Aug 10, 2012) <br> |  | 35 | FINDING | 8662 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73679
29785 | FINDING | A pop-up window is seen everytime System Viewer application is opened. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Everytime Ovation System Viewer application is opened, a pop-up window saying &quot;on not valuecolorobj HWY1Ext&quot; Press OK, same window appears twice and then goes off.This is seen in 3.5.0_U4 build.<br><br>Kindly find the attached SystemViewer_popup.jpeg file. (Sachan, Pallavi Jul 23, 2012) |  |  |  | rerun this test. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this has been fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8665 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73683
29786 | FINDING | Subwindows showing the details of Codes is blinking and non-readable in 32-bit machines. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Subwindows showing the details of Codes in the DropSummary Window like Color Codes for DropID, Status Codes for Drop Status, Faults for Fault Code and Fault ID, etc.. are blinking continuously and hence non-readable in 32-bit machines. (Sachan, Pallavi Jul 23, 2012) |  |  |  | rerun the same test. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this should be fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8666 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73685
29787 | FINDING | Controller Diagnostics does not show the GOx processor type as required by SRF #1379 | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Controller Diagnostics does not show the GOx processor type as required by SRF #1379.<br>----<br>SRF #1379: 3.3 Controller Functionality -<br> The OCR1100 will detect at boot what version it is (G01 and G02). If G02, the OCR1100 will<br> be able to detect the SFP type (speed and media). The controller will log this information.<br> This information will also be made available to Controller Diagnostics and the System <br> Registration utility<br>---<br>Ref: 3.5_Controller_SVTP_Rev5.1 - Test 5.23.4: Controller Diagnostics (CD)<br> Verify CD displays the controller version:<br> a. &quot;OCR400 G01&quot;for a OCR400 with a G01 processor.<br> b. &quot;OCR400 G02&quot;for a OCR400 with a G02 processor.<br> c. &quot;OCR1100 G01&quot;for a OCR1100 with a G01 processor.<br> d. &quot;OCR1100 G02&quot;for a OCR1100 with a G02 processor. (Benzvi, Mati Jul 23, 2012) (Pingree, Douglas K. Jul 27, 2012) (Benzvi, Mati Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added group number (Christy, Benjamin Sep 10, 2012)<br>---<br>msb - OK in 3.5.0_U8 @ 19-Sep-2012 (fixed in OCR1100 only)<br> Emily Network:<br> Drop18/68 (OCR1100 with G01), Drop32/82 (OCR1100 with G02)<br> Drop20/70 (OCR400 with G01), Drop43/93 (OCR400 with G02)<br><br> Diagnositics:<br> drop18/68 - Controller Type: OCR1100 G01<br> drop32/82 - Controller Type: OCR1100 G02<br> Drop20/70 - Controller Type: OCR400 <br> Drop43/93 - Controller Type: OCR400 (Benzvi, Mati Sep 19, 2012) <br> |  | 35 | FINDING | 8667 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73687
29788 | FINDING | Virtual controller is going into fault mode due to watch dog timeout. This is causing points to time out. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Virtual controller is going into fault mode due to watch dog timeout. This is causing points to time out.<br><br>The fault code for the timed out drops (Drop 3 as an example) is:<br>FC 66, FK 10, FS 3, FO 22440, FG 0, FH 0, FI 0<br><br>FS 3 = Fault Parameter 1 0x0003 Redundant watchdog error <br> A critical task in the Controller has timed out. (Benzvi, Mati Jul 23, 2012) |  |  |  | Ensure vxsim drops are not going into fault mode due to watch dog timeouts. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Watchdog timeouts extended for vxsim. (Perdeus, Matthew Jul 26, 2012)<br>---<br>msb OK in 3.5.0_U7 @ 12-Sep-2012. Monitoring. (Benzvi, Mati Sep 12, 2012) <br> |  | 35 | FINDING | 8668 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73689
29789 | FINDING | Switch configuration Tool with invalid Configuration progressed if changes made in [Include DHCP p.]checkbox. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps are:<br>1.In studio, right click on SISNET1 and select Create switch configuration then select Generate &amp; Upload. Observation: By default DHCP checkbox is checked. Tooltip shows configuration is not valid. For reference screenshot &quot;SWITCH CONF TOOL DHCP ERROR.jpg&quot;. <br>2.Unchecked DHCP checkbox then checked again this time Tooltip says configuration is valid. For reference screenshot &quot;SWITCH CONF TOOL DHCP NO ERROR.jpg&quot; (Pandey, Vijay Jul 24, 2012) (Swartz, Mark E. Jul 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Switch tool was not validating configuration after state of checkbox changed. This behavior was corrected. (Czak, Jakub Aug 4, 2012)<br>VP: Retested with 3.5.0_U6, found fixed. Hence finding is closed. (Pandey, Vijay Aug 24, 2012) <br> |  | 35 | FINDING | 8669 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73691
29790 | FINDING | VxSim controller doesn"t synchronize its time to any source time | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | There is no time synchronization of the VxSim controller. The time on VxSim controller is set up on startup and not synchronized at all during run time. This means that VxSim time can drift from VCH time during run time, which causes the VxSim controllers can have different time on one VCH. (Zochowski, Piotr Jul 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added SNTP to VxSim kernel in U5. (Pingree, Douglas K. Aug 7, 2012) <br> Verified on final build and ipsntp task was running on VxSim, which means that the SNTP is running on the controller. (Zochowski, Piotr Nov 6, 2012) |  | 35 | FINDING | 8670 |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73693
29791 | FINDING | Fieldbus functions not operational from operator stations. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:46 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:46 |  |  |  | 2019-07-02 10:46 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When any function dealing with Fieldus modules or their associated devices is attempted through the developers studio an error message is generated as follows:<br><br>Unable to complete the requested operation<br>Code 0x80004005 Source: Ovation Developer Studio (Wood, Tom Jul 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 7/24/12 Val+Dev+Doc mtg - this issue should be assigned to Steve H. (Capani, Nooch Jul 24, 2012)<br><br>Workaround Available. Please See Me For Details.<br>- (Hutchison, Steven B. Jul 24, 2012) <br> |  | 35 | FINDING | 8671 |  | FINDING | Plymire, Alvan AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | Pratley, Bob EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U5 |  |  | FINDING | [6 empty] | 143795
29795 | FINDING | "Overwrite duplicate files" not working properly, during importing ".ioc" file. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | &quot;Overwrite duplicate files&quot; comes irrespective of presence of &quot;.ioc&quot; file during import.<br>It imports the &quot;.ioc&quot; file even &quot;NO&quot; selected for &quot;Overwrite duplicate files&quot;, once file is not present. Please find attach for clarity. (Singh, Ghanshyam Jul 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works As Designed (WAD) - The Overwrite Duplicate Files Window is always displayed on an import of an audio file, bitmap file, or icon file. The studio has never check if the file was there or not to determine whether or not to display the message box. It always asks and uses the answer if necessary. This is the way it has always worked. (Augustine, Lisa Jul 30, 2012)<br><br>GS(08/14/2012)-If Overwrite Duplicate Files Window has no relation with presence of file, what is the purpose of the feature? It creates unnecessary confusion to the user. (Singh, Ghanshyam Aug 14, 2012)<br><br>Works As Designed (WAD) - I already explained this is how it is designed. We ask prior to the import operation in case it is encountered during the importing of the files so we will know what to do. This is the way it was designed and has always worked. It is not being changed. (Augustine, Lisa Aug 14, 2012)<br><br>GS: As per developer&quot;s comments above.The finding is closed. (Singh, Ghanshyam Oct 1, 2012) <br> |  | 35 | FINDING | 8675 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73703
29796 | FINDING | "$WDPF_HOME\mmi\config\icons directory" should be replaced by "Ovation\mmi\config\icons" directory | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | &quot;$WDPF_HOME\mmi\config\icons directory&quot; should be replaced by &quot;Ovation\mmi\config\icons&quot; directory in SVTP &quot;SDR18727_SVTP_rev1.1_GS.doc&quot; section 5.1.4 .Once we browes the &quot;Standard Application Icon&quot; or for ¿New Alarm Warning Icon¿ then it opensto the path &quot;Ovation\mmi\config\icons&quot; directory. (Singh, Ghanshyam Jul 26, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN OpCon (WOP)</p> <p><strong>Release Level:</strong> 3.5.0_U4 16-JUL-12</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2012-07-26T05:54:37-04:00</p> <p><strong>Modified Date:</strong> 2012-07-26T05:54:37-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8676 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73704
29797 | FINDING | Default value of CMAX for Distributor Algo is 1.5 in property summary | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | As per SRF1450_SVTP_rev1.2_JJ.doc , Test case:-&quot;5.2.2 Test: Distributor Algorithm&quot;s Parameters Default Values/Settings/Calculated values:&quot; CMAX=2.5 but in property summary diagram the default value comes as 1.5.<br><br>Please find the attached snapshot for details (Jayarajan, Jayakumari Jul 26, 2012) (Hutchison, Steven B. Jul 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The template has been changed to the following based on latest information from controller development group:<br><br> DEFAULT MIN MAX<br>CMAX 1.5 1.0 1.5<br>CMIN 0.5 0.5 1.0 (Hutchison, Steven B. Jul 26, 2012)<br><br>JJ(27July2012)<br><br>Then the test case SVTP should be modified . Please advise whether I can put finding against SVTP. (Jayarajan, Jayakumari Jul 27, 2012)<br><br><br>JJ(20Aug 2012)<br><br>closed (Jayarajan, Jayakumari Aug 20, 2012) <br> |  | 35 | FINDING | 8677 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73706
29798 | FINDING | FNUM exceeds the OUT pins then the Distributor algorithm willnot reset FNUM internally back to default | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps are done for testing<br><br>1. Add the algorithm to control sheet with an analog input(LA) and two outputs (out1 and out 2) are also connected .<br>3. FNUM first set to &quot;0&quot; and then 2 with default settings (all Base Gains =100% and Correction Gain =1.0),in both cases it is observed that o/p performs as per the equation<br>OUTx= IN*FNUM/Nc <br><br>4. But if FNUM greater than 2 it is also observed that the Distributor algorithm willnot reset FNUM internally back to default (equals OUT pins connected)<br><br>Please find the attached snapshot also for reference (Jayarajan, Jayakumari Jul 26, 2012)<br><br><br>This appears to be an algorithm operational issue. The validator believes the algorithm executing in the controller should reset the FNUM field if it exceeds the actual number defined outputs.<br>- (Hutchison, Steven B. Jul 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem recreated.<br>Algorithm didn&quot;t update FNUM field in LC record.<br>Problem is fixed (Plamowski, Sebastian Aug 2, 2012)<br>JJ_22Aug2012<br>FNUM exceeds the OUT pins then the Distributor algorithm reset FNUM internally back to default in U6 (Jayarajan, Jayakumari Aug 22, 2012) <br> |  | 35 | FINDING | 8678 |  | FINDING | Jankowiak, Michael AUTOSOL DX WRSW | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Kephart, Richard W EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [6 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73708
29799 | FINDING | More than three outputs are not getting correct value for distributor algo | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If we connect more than three ouputs with default settings (all Base Gains =100% and Correction Gain =1.0) the ouputs are not getting as per the eqn OUTx= IN*FNUM/Nc.<br><br>The value of 3rd, 4th, 6th,7th and 8th outputs are always appears in exponential form .<br><br>Please find the attached snapshots with various values FNUM and with Outputs. (Jayarajan, Jayakumari Jul 26, 2012)<br><br>This appears to be an operational issue. The outputs unreasonable values. <br>- (Hutchison, Steven B. Jul 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem recreated.<br>TRIN input signals were not initialized and the value was not corrected when signal was not connected. <br>FNUM was read as UINT but in algorithm it is used as a BYTE. Binary operation was added to read only low byte<br>rf_fnum = ((UINT32 *)ddbEntry.staticPtr)[LC_C0_OFFSET] &amp; 0xFF;<br>Problem is fixed. (Plamowski, Sebastian Aug 2, 2012)<br><br>JJ(31Aug2012)<br><br>All the o/p pins are getting correct value (Jayarajan, Jayakumari Aug 31, 2012) <br> |  | 35 | FINDING | 8679 |  | FINDING | Jankowiak, Michael AUTOSOL DX WRSW | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Kephart, Richard W EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [6 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73710
29800 | FINDING | OUTPUT pins of Image of distributor algo in signal diagram is not clear | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | After connecting three outputs with distributor algo and load the controller.<br>Then open the logic in signal diagram , it is observed that image of output section is not clear. <br><br>please find the attached snapshot for reference (Jayarajan, Jayakumari Jul 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it Works. The values for the points assigned to the unattached output pins are overlapping the pins and bottom of algorithms. Attach page connectors or downstream signals and the values will be placed on the signal lines (Hutchison, Steven B. Jul 26, 2012) <br> |  | 35 | FINDING | 8680 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73712
29801 | FINDING | Signal diagram Opened through context Manu Graphics if Prevent a User signal diagram from starting the program. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps followed--&gt;<br>I have removed signal diagram exe from Manage Group polices&quot;&gt; Select Operator (Locked down) under user polices --&gt; click on system --&gt; click run only allow window application and remove (cbviewer.exc) in Ovation Security Manager after that I am unable to open signal diagram through ovation application which is ok. But signal diagram would be opened through context Manu Graphics and point info.etc. (Kumar, Sudheer Jul 27, 2012) (Hutchison, Steven B. Oct 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19181 (Benzvi, Mati Oct 24, 2012) <br> |  | 35 | FINDING | 8681 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73714
29802 | FINDING | Accounts or Interactive logon state is not changed under Security Option . | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Accounts or Interactive logon state is not changed under Security Option in Ovation Security Manager <br><br>Steps followed--&gt;<br><br>Open Ovation Security Manager--&gt; select Manage Group polices&quot;&gt; Select any Polices under Computer polices --&gt; Select Security Options --&gt; click &quot;Accounts: Rename administrator account&quot; or &quot;Interactive logon :Massage title for users attempting to log on&quot; state is not change (Like not configured to enable or disable )<br>I changed the Accounts or Interactive logon state &quot;not configuration to enable or disable &quot; and apply after closed this window and check again the Accounts state under security options but state is not updated . (Kumar, Sudheer Jul 27, 2012) (Swartz, Mark E. Jul 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | For the two specific setting you described there is also a value field. If the value is not specified the setting does not change. If one enters a value then the setting is changed. (Burgoon, Frank J. Jul 27, 2012) <br> |  | 35 | FINDING | 8682 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73716
29803 | FINDING | Default values of record fields U1,B1 and B2(VER,COMAP and ACMAP) are not matching with the value given in Test case_Distributor algo | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In PI Default values of record fields U1,B1 and B2(VER,COMAP and ACMAP) are 1.12,3 and 3.<br>But as per SRF1450 and SVTP the default values for record fields are given as &quot;0&quot;<br><br>Please find the attached snapshots for reference. (Jayarajan, Jayakumari Jul 27, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Control Builder - Unified (CBU)</p> <p><strong>Subproduct:</strong> Algorithms (ALG)</p> <p><strong>Release Level:</strong> 3.5.0_U4 16-JUL-12</p> <p><strong>Originator:</strong> Jayarajan, Jayakumari</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Hutchison, Steven B. Jayarajan, Jayakumari</p> <p><strong>Entry Date:</strong> 2012-07-27T04:23:02-04:00</p> <p><strong>Modified Date:</strong> 2012-07-27T07:11:31-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8683 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73717
29804 | FINDING | (Y0,Y1,Y2,Y3,Y4,Y5)fields are not changing accordingly with packed point connected to "CMD" pin of distributor algo | Plamowski, Sebastian EMR SYSS PWS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Following steps were performed <br>Connected a 16 bit packed point to the cmd pin of distributor algo.<br>Given an an anlog value to Input pin<br>connected two outputs.<br>Loaded the logic sheet in controller <br>Thru PI , bits 1,3&amp;5 is set ,then the input pins (XSEL, PSEL,GAINx) are ON and accepts inputs from external application.<br><br>But the corresponing internal record fields (Y0, Y2 &amp; Y4 ) still have the default value &quot;0&quot;<br><br>Thru PI , bits 1,3&amp;5 is reset and 0,2&amp;4 are setthen the input pins (XSEL, PSEL,GAINx) are off and accepts inpus from internal application.<br>Then also the corresponing internal record fields (Y1, Y3 &amp; Y5 ) still have the default value &quot;0&quot;<br><br>Please find the attached snap shot for reference. (Jayarajan, Jayakumari Jul 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This appears to be operational issue in the algorithm. - (Hutchison, Steven B. Aug 16, 2012) <br> The fields Y0 ... to Y5 are independent of CMD pin.<br>These fields are used to control algorithm (select int/ext gains, priority... etc) from operator graphic. If somebody set Y0 to 1 algorithm reads this information, change the state and reset field Y0. CMD pin is used to control algorithm from the logic.<br><br>Information about CMD pin you can find in:<br>CMDVLG7VariableRequired0Information about CMD pin map-<br><br>Information about current state of algorithm (select int/ext gains, priority... etc) you can find in:<br>SPMAPB4Alg InitVariable0External GAIN, XSEL, PDB, TrackIfHigher<br><br>I verified reported problem with engineering and we don&quot;t see a problem in the algorithm.<br>Please, let me know if something is not clear in the documentation, we can update it. (Plamowski, Sebastian Aug 22, 2012)<br><br>jj(25feb2013)<br><br>As per the above information , the test case 5.2.4.2 &quot;Test: Internal &amp; External selection using &quot;Internal algorithm fields&quot;[Y0-Y5]: Verify the following&quot; sould be removed from SRF1450_SVTP_rev1.2.doc (Jayarajan, Jayakumari Feb 24, 2013) (Plamowski, Sebastian Aug 4, 2013) |  | 35 | FINDING | 8684 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73719
29805 | FINDING | Point Alias field of DU Record always asks to start with DROP | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | If we enter anything other than DROP in Point Alias field of DU Record point types then it gives error message [Drop Point names must start with &quot;DROP&quot;]. However, all other point type records accept any entries (except special characters) in Point Alias field. Please refer attached snapshot file SDR18167.jpg. (Gupta, Chandresh Jul 27, 2012) |  |  |  | The validation of point names will now check not only the point&quot;s record type, but also the attribute which is being checked. Therefore, the restriction that the &quot;name&quot; begins with &quot;DROP&quot; will only be applicable if the field belongs to a DROP point AND if the field is the Point Name attribute. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Currently, the validation of the Point Alias field is exactly the same as for the point name. Since Drop Point names are more restrictive, this inadvertantly caused the same validation of the Point Alias field to be performed on the Drop point. This will be corrected. (Swartz, Mark E. Jul 27, 2012)<br><br>cg (08/21/12) - Finding retested in 3.5.0_U6. Now, there is no restriction of DROP in Point Alias field. Hence this finding is closed. (Gupta, Chandresh Aug 20, 2012) <br> |  | 35 | FINDING | 8685 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73721
29806 | FINDING | Ovation Security Manager window closes upon clicking [x] of Help window | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps performed are as follows:<br>1. Opened Ovation Security Manager window from Developer Studio.<br>2. Selected &quot;Manage Database Users&quot; tab from Pick aa task option.<br>3. On right pane selected any Ovation user &amp; clicked on &quot;Reset Password&quot; button from menu bar. Password Editor subwindow opened.<br>4. Clicked on &quot;Help&quot; button of this window. It opened a warning subwindow saying &quot;The requested operation could not be performed......&quot;.<br>5. Upon clicking OK button it closes the Ovation Security Manager application which is fine as per the message in this subwindow.<br>However, upon clicking [x] located on the top right corner of this subwindow also closes the Ovation Security Manager window. Instead it should only close the warning subwindow.<br>Please refer attached snapshot file. Also attached is the remote login details to Net#7 DBS drop250. (Gupta, Chandresh Jul 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Change it to SDR. Will fix in the future 3.5.0 patch. (Thirunavukkarasu, Utthandi Oct 12, 2012)<br>---<br>msb - Closed. Converted to SDR 19133 (Benzvi, Mati Oct 13, 2012) <br> |  | 35 | FINDING | 8686 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73723
29810 | FINDING | OCR1100 Controller reports error if all the channels of SOE card are not assinged digital points | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On 3.5(WALT) network OCR1100 controller DROP35/DROP85, for SOE Contact Input module &quot;Event Tagging Enable&quot; is selected for all the 16 channels. If we assign digital points to all the 16 channels the controller loads without any error. But if any of the channels is not assingned a digital point, the controller will give following error after loading:<br>FC 66 Controller Fault<br>FK 08 H SOE Fault<br>FS 0001 H Could not find SID to match Event Error<br>The Ovation Error log is attached for reference. (Lal, Ramesh Jul 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This works as designed. If you configure a channel with Event Tagging, then the SOE module will scan that channel for events. If the channel has no point(SID) associated then the controller will post an alarm. It is not an error per se, it is only a notification that something is configured incorrectly. There is nothing the controller can do about this. <br>In addition, you state in the finding that this is an OCR1100 controller. You need to qualify that by stating OCR1100 controller only. If it was only the 1100, and not the 400, then this would be a valid finding. You should check both controller types. (Pingree, Douglas K. Jul 27, 2012)<br><br>9/20/12:RL - The same observation was made in OCR400 Controller. As noted by Dev, it is only a notification and not an error, I am closing this finding. (Lal, Ramesh Sep 20, 2012) <br> |  | 35 | FINDING | 8690 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73730
29812 | FINDING | Decription for Hide Internet Explorer option under "Manage Group Policies" need modifications. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation security manager under Manage Group Policies &gt; Computer Policies (any) &gt; Desktop &gt; Hide internet icon on desktop, the description of its mention as :- <br>&quot;Removes the Internet Explorer icon from the desktop and from the Quick Launch bar on the taskbar. This setting does not prevent the user from starting Internet Explorer by using other methods&quot; <br>However incase of WIN7 os, when this option is Enable then internet explorer icon does not hide from desktop (it do restrict to open ) also we cannot open the same from any other path.<br><br>Hence description of same should be modified for WIN7. (Sahay, Madhukar Jul 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Windows no longer supports this functionality. Create a 3.5 SDR requesting to remove this option from the security manager. (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: converted to SDR 19111 @ 08-Oct-2012 (Benzvi, Mati Oct 8, 2012) <br> |  | 35 | FINDING | 8692 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73734
29813 | FINDING | VC143 (with eDB sheets) can not be cleared or loaded | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | VC143 (with eDB sheets) can not be cleared or loaded in U4. <br>The controller was healthy in U3 and no siginficant changes were made to it in U4.<br><br>Load error:<br> *--------------------&gt; Error Stack Dump &lt;---------------------*<br> [External]: (DROP143 must be cleared before it is loaded)<br> [OvPtApi]: (No key found in object_hierarchy)<br><br>Clear Error in Studio after about 20 minutes:<br> *--------------------&gt; Error Stack Dump &lt;---------------------*<br> [External]: (error (11) from PEDITClear, OpStat = (0), ErrNum = (0)) (Benzvi, Mati Jul 28, 2012)<br>------<br>msb - 8/19 - Failed again in U6. Clear &amp; Load files attached (Benzvi, Mati Aug 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SSV task was faulting. The ssv.dat file may have been corrupted. Removing this file and rebooting stopped ssv task from faulting and then clear / load operation completed. Let&quot;s monitor this to see if it reoccurs in this drop or others. (Perdeus, Matthew Aug 15, 2012)<br>--- <br>Need to re-test with U8 after timing issues were addressed. (Boehmer, Robert W. Sep 14, 2012)<br>---<br>msb - 9/19 - In U8: 143 with 50 Sheets &amp; 13792 points.<br> a. Incremental Load<br> b. Clear and Load<br> c. All sheets are active in Signal Diagram (Benzvi, Mati Sep 19, 2012) <br> (Benzvi, Mati Sep 19, 2012) |  | 35 | FINDING | 8693 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73736
29814 | FINDING | Studio allows Remote Node name with 40 Chars, while spec requires 50 Chars. | Capani, Innocenzo AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | The Specs of SRF1632 - Expanded MultiNetworking states:<br> &quot;The maximum length for the Remote Node Name is 50 characters.&quot;<br>While in Studio when entered name with 50 Chars:<br> [Remote Nodes]<br> 50CHARS-10-234567-20-234567-30-234567-40-234567-50<br>recieved an error:<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br> [OvPtApi]: (Unable to insert into object hierarchy)<br> [API]:Database error (SQL exec insert on OBJECT_HIERARCHY)<br> [Driver]:ORA-12899: value too large for column &quot;PTADMIN&quot;.&quot;OBJECT_HIERARCHY&quot;.<br> &quot;OBJECT_NAME&quot; (actual: 50, maximum: 40) (4) (Benzvi, Mati Jul 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The 50 character length in the functional specification did not come from any specific requirement. This length conflicts with the maximum length of an object name in object_heirarchy. Therefore, the maximum will be changed to 40 and the spec will have to be updated. (Augustine, Lisa Jul 30, 2012)<br>---<br>msb - Changed Product to SVTP - Studio:<br> 3.5_SRF1632_300-Multinet_SVTP_Rev1.3 - Test 5.1.4: should be <br> Verify that Remote Node name or Nested Remote Nodes names can not exceed 40 characters.<br> a) Single Node name with 40 Characters<br> b) Nested Node name with 40 Characters<br> c) Node name with more than 40 Characters is not allowed (Benzvi, Mati Aug 8, 2012) <br> |  | 35 | FINDING | 8694 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73738
29816 | FINDING | Right Click Menu on Tree View of OSV could be seen on other applications also. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In OSV, when Right Clicked on Tree View, we have options of Collapse All / Expand All / Cancel. Now if we navigate from OSV to any other application on the desktop e.g. Dev.Studio / Alarms/ etc.. it is seen that the right click menu appears on all applications.<br><br>Kindly find attached OSV_rightclick.jpeg (Sachan, Pallavi Jul 30, 2012) |  |  |  | rerun the same test. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this is fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8696 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73741
29817 | FINDING | There is no option to refresh list of I/O Devices in OSV. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | There is no option in OSV to refresh the I/O Devices list.<br>When instance of OSV is opened and new Hardwares are configured in Studio, the newly configured devices does not show up in already opened OSV application, whereas open the same application on other drop we see all the configured devices.<br>The only way to see the devices is to Exit and Restart the OSV application. (Sachan, Pallavi Jul 30, 2012) |  |  |  | reload drops while the system viewer is running. You will see that the program will inform you that a reload is taking place within 60 seconds of the file being loaded on the operator&quot;s station. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this is fixed. Every time a drop is loaded, the new file is sent to the operator&quot;s stations.<br>When a file with a new time stamp is discovered, the system viewer will reload with in 60 seconds. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issue mentioned above is fixed. <br>But now, when the new files are loaded, system viewer collapses hierarchy and shows Drop Summary of Network level (Top Level). (Sachan, Pallavi Aug 28, 2012)<br><br>This is the expected display when a load occurs since<br>I do not know what was added, modified or deleted. (Wozniak, Diane M. Aug 29, 2012) <br> Found the issue to be fixed. Hence finding closed. (Sachan, Pallavi Aug 29, 2012) |  | 35 | FINDING | 8697 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73743
29819 | FINDING | OSV, Point Names are repeated under Point Attributes. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Point Names are repeated as Attribute &quot;Channel 1 Point&quot; and also as &quot;AHILK IO Module&quot; / &quot;DHILK IO Module&quot;. This is observed for Analog/Digital Points only.<br>Packed points assigned to Devices show Attribute Name as &quot;Channel 1 Point&quot; correctly for every Point name.<br>Kindly find attached OSV_attributename.jpeg. (Sachan, Pallavi Jul 31, 2012) |  |  |  | Run the same test again. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | There will not be duplicate point names on any of the point grids. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8699 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73747
29820 | FINDING | Columns under Drop Status cannot be customised by removing/ adding them. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In OSV,Columns under Drop Status cannot be customised by removing/ adding them.<br>Under Drop Status tab, the columns like &quot;Parameter&quot;, &quot;Primary Drop Value&quot;, &quot;Partner Drop Value&quot;, etc.. cannot be removed and added. <br>Like all other columns when we right click on the tabs the menu &quot;Remove This Column&quot; is greyed out. <br>Hence the above mentioned columns could not be removed/added (Sachan, Pallavi Jul 31, 2012) |  |  |  | try adding and removing columns. The drop summary grid should not allow columns to be removed. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | this is fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be still existing. Hence Finding Open (Failed Retest). (Sachan, Pallavi Aug 28, 2012) <br> My mistake! All of the other grids should have the option for removing the column. Not this grid.<br>This grid is not the same as the other grids. It has subsections. this grid is based on Point Information&quot;s grid. Point Information does not allow for the columns to be removed.<br>I am not planning on making any changes for this. (Wozniak, Diane M. Aug 28, 2012)<br><br>As per developer&quot;s comments above, Finding is Closed. (Sachan, Pallavi Aug 29, 2012) |  | 35 | FINDING | 8700 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73749
29821 | FINDING | When clicked on dynamic value in zoomed view, the Signal diagram changes to Full View. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | While working in signal diagram, Zoom the logic, when clicked on any Dynamic Values, the Screen comes to FULL View display. (Sachan, Pallavi Jul 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works as Designed - When the value is clicked, the originating algorithm is selected. The view is expanded to ensure the selected algorithm is visible.<br><br>- (Hutchison, Steven B. Aug 14, 2012)<br><br>Closed as per developer&quot;s comments above. (Sachan, Pallavi Aug 29, 2012) <br> |  | 35 | FINDING | 8701 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73751
29823 | FINDING | Forcing SIS Algorithms from Signal Diagram causes Error. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When attempting to force a value for SIS related points using a Signal Diagram an error is generated as indicated on the attached snapshot. This occurred on Database server (OS Server 2008, Service Pack 1 - 64 Bit) (Wood, Tom Aug 1, 2012) |  |  |  | Start Force application from Signal Diagram. It should not display error message. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem was caused by OvSisForceApp project settings. There was a compatibility issue between OvSisForceApp.exe and other Ovation .NET assemblies. (Czak, Jakub Aug 2, 2012) <br> |  | 35 | FINDING | 8703 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73754
29824 | FINDING | Time Period of Control Task 1 & 2 for Controller drop could be modified using Search option | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | User can modify Control Task 1 &amp; 2 time period configuration of Controller drop using &quot;Search&quot; option. Steps are as follows:<br>1. Thru right click Search option the Control Task is selected. Column &quot;Period (msec)&quot; is added.<br>2. Changed the Control Task 1 or 2&quot;s time to something other than the default.<br>3. When observed that parameter thru Developer Studio hierarchy for that Control Task it does not reflect the change. This is ok since CT 1 &amp; 2 have fixed time period of 100msec &amp; 1000mse resp.<br>4. Again did &quot;Search&quot; (as done in step 1 above) for the same Control Task. In this window it shows the changed value instead of default value.<br>Instead, these attributes for CT1 &amp; 2 could be prevented from being changed via the Search window. It could be made Read-only for viewing purpose. (Gupta, Chandresh Aug 3, 2012) (Swartz, Mark E. Aug 3, 2012) |  |  |  | The affected area is in the definition of the properties of the &quot;Period (msec)&quot; attribute of Control Task configuration objects. Specifically, this attribute will have the internal property &quot;no global change&quot; -- which means that it will be shown as read-only and grayed-out when displayed in the Ovation Developer Studio search results UI. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | What was observed in step 3 of this Finding&quot;s Description is that the Control Task edit UI is driving the value back to its intended value of 100ms. Simply opening it up has not changed the value in the database &quot; only the displayed widget shows the value. If the Ok or Apply buttons where pressed at that time, the value would have changed back to the original default value of 100ms. The subsequent &quot;Search&quot; in step 4 would then show the default value of 100ms again.<br><br>As we know, CT 1 and CT 2 Periods are not intended to be changed by the user. As pointed out in this Finding, the Search operation currently permits the user to modify those values. (I&quot;m not sure that anyone ever noticed that before &quot; or if they did, it was never reported.)<br><br>With the Search results UI, we cannot conditionally set different rows of a particular column to different properties. Given that, the only course of action is to prevent that attribute from being changed via the Search window. The &quot;Period (msec)&quot; value would be read-only when viewed in the &quot;Search&quot; window regardless of what control task it is associated with.<br><br>-----<br>The properties of the &quot;Period (msec)&quot; attribute of Control Task configuration objects will be changed such that it cannot be modified via the Search results in the Ovation Developer Studio. (Swartz, Mark E. Aug 3, 2012) (Swartz, Mark E. Aug 15, 2012) <br> cg (08/21/12) - Finding retested in 3.5.0_U6. Now, Period (msec) column for all the 5 Tasks in Search window are appearing as greyed out. User cannot modify this field. So the behavior is matching with the developers comments. Hence this finding is closed. (Gupta, Chandresh Aug 20, 2012) |  | 35 | FINDING | 8704 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73756
29825 | FINDING | SIS controller fails due to vxworks task timeout. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In PGH lab drop2/52 which is SIS controller constantly fails after loading controller.<br>Both Controllers now has Processor module -G02 and IOIC mudule as G02.<br>Controller is configured for 6000 points and has 3242 actual points.<br>Kuba from Poland is investigating this problem and according to him there is problem with sis_xdb task. (Kumar, Shailendra Aug 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | sis_xdb task was corrupting stack. (Czak, Jakub Aug 4, 2012)<br>SK:ok in U7 hence closed. (Kumar, Shailendra Sep 6, 2012) <br> |  | 35 | FINDING | 8705 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73758
29826 | FINDING | In OSV, the Drop Status is not updated for the drops configured in any UNIT other than UNIT0. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | For the Drops configured under UNIT1 ( we have a VC drop3 and a SIM Controller drop99 in UNIT1 on NET#8), the Drop Summary window does not show any update. This is shown as ??? for all the parameters, whereas Drop Status shows all the details of the drop properly.<br><br>Kindly refer to attached OSV_DropSummary.jpeg (Sachan, Pallavi Aug 6, 2012) |  |  |  | Be sure to make a system that has 2 or more units on it. Be sure there are hardware points on all the drops on all the units. Be sure to check the Status Point Window and Point Attributes Window. Be sure to try to call up point information from them, make sure the values are updating, etc. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a serious finding. It is more that just the drops on the Drop Summary window.<br>All of the points on the non default units would not have displayed properly. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8706 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73760
29827 | FINDING | OSV-&gt Print Preview, when Print command is given Print Window opens 3 times. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OSV, Print -&gt;Preview &amp; Print Window -&gt; Select available windows to be printed -&gt; Print. This calls Print Window 3 times, when pressed ok or cancel, it is followed by &quot; on not valuecolorobj HWY1Ext&quot; message already mentioned in F#8665. (Sachan, Pallavi Aug 6, 2012) |  |  |  | retry the same test. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Both of the problems listed have been fixed. (Wozniak, Diane M. Aug 27, 2012)<br><br>Found the issues to be fixed. Hence Finding closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8707 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73762
29828 | FINDING | OSV -&gtPrint Preview -&gtToolbar -&gt Customise option is greyedout. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OSV -&gt;Print Preview -&gt;Toolbar -&gt; Customise option is greyedout. (Sachan, Pallavi Aug 6, 2012) |  |  |  | This matches Point Information. I am not planning on making a change. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is the same as Point Information. Since this matches Point Information, no change is being made. (Wozniak, Diane M. Aug 27, 2012)<br><br>As per developer&quot;s comments, Finding is closed. (Sachan, Pallavi Aug 28, 2012) <br> |  | 35 | FINDING | 8708 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73764
29830 | FINDING | Developer"s studio crashes when it is tried to commisioned any new device in segment. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When it is tried to commissioned a new device in a segment (which does not have any commisioned device earlier ) then developer&quot;s studio crashes.<br><br>Workaround given by steve by adding function block in it. (Sahay, Madhukar Aug 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. Aug 8, 2012)<br><br>MS : Following steps are performed in 3.5_U9:-<br> 1. Segment 1 has 2 commissioned device (848T).<br> 2. Decommissioned both the device so that this segment does not have any commissioned device.<br> 3. Now commissioned each device one by one successfully. <br> <br> I am closing this finding. (Sahay, Madhukar Sep 25, 2012) <br> |  | 35 | FINDING | 8710 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73768
29831 | FINDING | Discrepancies in 3.5_WIN_OPCON_SVTP_rev2.H_xxx.doc | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | 1) Test case 5.1.2d : Please include LC record type in the tests.<br>2) Test case 5.1.4.1i : auto cutout on/off ( The buttons have been revised to auto cutout enabled/disabled) The same correction needs to be done in all the other test cases as well.<br>3) Test Case 5.2a : Trend Configuration test case in the SVTP is not updated as per the current release. The complete test needs to be revised. (Khanna, Anant Aug 7, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN OpCon (WOP)</p> <p><strong>Release Level:</strong> 3.5.0_U5 03-AUG-12</p> <p><strong>Originator:</strong> Khanna, Anant</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Khanna, Anant</p> <p><strong>Entry Date:</strong> 2012-08-07T02:45:01-04:00</p> <p><strong>Modified Date:</strong> 2012-08-07T02:45:01-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8711 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73769
29832 | FINDING | HEARTBEAT algorithm Functional Symbol in control builder is not similar with the help file. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0, the Functional Symbol of HEARTBEAT algorithm in the Control Builder is not matching as per the Help file. At the left of the functional diagram of HEARTBEAT at control builder IN2,IN4,IN5 is not as per the position shown in help file. At the right side HTBT is also not in the same position as shown in the help file.<br>For reference, please find the attached snapshots. (Mitra, Sambuddha Aug 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works as designed - No Plans to Fix - (Hutchison, Steven B. Aug 8, 2012) <br> |  | 35 | FINDING | 8712 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73771
29834 | FINDING | Single-attached OCR400s sometimes show Channel 0 as Available rather than Active. | Ritenbaugh, David PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Single-attached OCR400s sometimes show K0 as Available (4), rather than Active (8). This does not always occur, and it is not know what causes it. (Brown, Sean Aug 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | May be related to finding 8381. Please re-test in U6. (Pingree, Douglas K. Aug 7, 2012) <br> |  | 35 | FINDING | 8714 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73774
29835 | FINDING | Unable to select Historian drop in Historical Review | Contento, James AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | It is clear from the screen shots &quot;Unable to select Historian .jpg&quot; that there is no option to select Historain drop from drop down option.But as per validator point of view, option should be there to select an historian drop.<br><br>Note: Manually validator are able to enter historian drop name. (Agarwal, Gaurav Aug 7, 2012) |  |  |  | See finding description. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8715 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | OVA350_Patch. OPH340 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73776
29836 | FINDING | HSE server is not configured in AMS server plus station. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | HSE server is not configured in AMS server plus station.<br>Steve has given the workaround of this by coping it. (Sahay, Madhukar Aug 7, 2012)<br><br>IC 3/10/14 &gt; also seen on 3.5.1 when installing AMS 12.5. 3.5.1 DIR will note the workaround provided by Steve (below). (Capani, Nooch Mar 10, 2014) | During testing it was observed that the HSE server was not configured in the AMS Server plus station (F#8716). The following was done to fix this: Type the following lines in a command prompt: CD /D %WDPF_HOME%\OvationBase InstallHseServer -i Note the -i must be lower case. It is expected that AMS will document the preferred configuration and registration procedure for the HSE Server. |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Hse Server is now available on all Ovation Stations.<br><br>AMS will document the preferred configuration and registration procedure for the HSE Server.<br><br>For the time being type the following lines in a command prompt:<br><br> CD /D %WDPF_HOME%\OvationBase<br> InstallHseServer -i<br><br>Note the -i must be lower case.<br><br>- (Hutchison, Steven B. Aug 13, 2012) <br> IC 9/13/12 - DIR. (Capani, Nooch Sep 13, 2012)<br><br>IC 9/27/12, added to DIR, closed finding. (Capani, Nooch Sep 27, 2012) |  | 35 | FINDING | 8716 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73778
29837 | FINDING | FFAI_RMT causes the lock of field bus map file. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | FFAI_RMT causes the lock of field bus map file. Due to this function block in <br>signal diagram is not operational.<br>Steve has given workaround of this. (Sahay, Madhukar Aug 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | After removal of pathch by steve I have tested in U6 , working fine. (Sahay, Madhukar Aug 24, 2012) <br> |  | 35 | FINDING | 8717 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73780
29838 | FINDING | FFAI_RMT causes the lock of field bus map file. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | FFAI_RMT causes the lock of field bus map file. Due to this function block in <br>signal diagram is not operational.<br>Steve has given workaround of this. (Sahay, Madhukar Aug 7, 2012)<br><br>Duplicate finding entered as 8717. I am closing this (Sahay, Madhukar Aug 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8718 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73782
29839 | FINDING | Historical review could not be opened once it is closed from right click[close window] of task bar. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps can recreate this:<br>1)Open Historical Review window, <br>2)Minmize it then <br>3)Right click the taskbar use [close window] to close the Historical review.<br><br>If User tries to Open Historical Review again on this station it will not open.<br>Shown this problem to Shyam. (Kumar, Shailendra Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. Next build should have this. (Matreja Shyam Aug 8, 2012)<br><br>SK:Ok in U9 hence closed. (Kumar, Shailendra Oct 23, 2012) <br> |  | 35 | FINDING | 8719 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73784
29840 | FINDING | The execution time can be non-sequentional in FFDEV script. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The execution time can be non-sequentional in FFDEV script based on execution order of the script. (Sahay, Madhukar Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed - (Hutchison, Steven B. Aug 8, 2012)<br><br>Tested in U6 , working fine. (Sahay, Madhukar Aug 24, 2012) <br> |  | 35 | FINDING | 8720 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73786
29841 | FINDING | Modifying SIS logics and then loading SLS hangs the studio and gives PEDIT error. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Its observed that on drop2/52 (SIS controller) :<br>1)While loading SDS01-SDS04 it hanged studio and after while it gave Pedit error for one of the NON SECURE point. <br>2)If SIS logics is modified/saved/compiled and then loading of SLS hanged studio.In this case it gave PEDIT error(11) for drop52(which is in control).Error says &quot;unable to update target sequence number&quot;<br>For reference attached is the error.<br>Kuba from Poland is investigating this problem.Rebooting the controller solves the problem for while.<br>SIS system has U4 + patch for SIS (Kumar, Shailendra Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Tasks pedittsk and gni3_admd were stuck on sending to the same socket. Since gni3_admd was also responsible for reading from that socket deadlock occured. Fix in shc lib implemented by Ben Christy was tested in Warsaw lab and it solves the issue. (Czak, Jakub Sep 12, 2012)<br><br>Tested in IEC lab and found loading of SLS OK after modification of SIS sheet. (Kumar, Shailendra Dec 5, 2012) <br> |  | 35 | FINDING | 8721 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73788
29842 | FINDING | The Redundant Modbus task stops when the driver is enabled. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR1100 Controller 32/82 (EMILY) is configured with a Redundant Modbus device. When and IP address (other than 255.255.255.255) is configured, the task stops. Ovation Error Log entries are attached. (Brown, Sean Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected behavior when tt field is empty (Christy, Benjamin Sep 18, 2012)<br>---<br>msb - Closed: Converted to SDR 19143 (Benzvi, Mati Oct 16, 2012) <br> |  | 35 | FINDING | 8722 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73790
29843 | FINDING | ELC config tool gives error while opening on 64 bit WIN7 system. | Plymire, Alvan AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps are performed.<br>1. ELC 1.1 has been istalled in drop126 (WIn7 OS- Emily system).<br>2. ELC module has been configured on 1.1.3 at drop40/90.<br>3. When ELC config tool was opened it gives an error &quot;Caught exception in <br> HighwayCollection--- ( Please refer attached snapshot ELC_config_Error.jpg) <br> On clicking the OK button Highway error appeared (Please find attached Details_tab.txt <br> file message of its details tab) (Sahay, Madhukar Aug 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/19/12 - per Al P. this is fixed. Please retest with U8 and latest ELC 1.2. (Capani, Nooch Sep 19, 2012)<br><br><br>MS : Checked in U8 &amp; ELC1.2_U7 , found fixed. I am closing this finding. (Sahay, Madhukar Sep 20, 2012) <br> |  | 35 | FINDING | 8723 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U8 ELC.1.2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73792
29845 | FINDING | Operator Digram Group Display is crashing while Adding Snapshot on Win07(64-bit OS) & Win08. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduces:<br>1.Opened the Operator Digram Group Display window from the following path.<br>Go to Start button-&gt;All Programs-&gt;Ovation-&gt;Ovation Utility-&gt;Digram Group Display.<br>2.Click on &quot;Add Snapshot&quot; Button then Snapshot Description pop-up window is opened.<br>3.write &quot;group&quot;or &quot;any text&quot; on Enter Snapshot Description then Press apply button.<br>4.The Operator Diagram Group Display becomes Crashed.<br>Please find attached Snapshot &amp; Text file of Error Description as &quot;Error occured while Add Snapshot.jpg&quot; &amp; &quot;Error occured while Add Snapshot.txt&quot;. <br>Note:The Operator Diagram Group Display is working fine on Win07(32-bit OS). (Prasad, Parmatma Aug 10, 2012)<br>PP:Issue is reported in Finding#8726. (Prasad, Parmatma Aug 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8725 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73796
29846 | FINDING | Operator Diagram Group Display is crashing while Adding Snapshot on Win07(64-bit OS) & Win08. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduces:<br>1.Opened the Operator Digram Group Display window from the following path.<br>Go to Start button-&gt;All Programs-&gt;Ovation-&gt;Ovation Utility-&gt;Digram Group Display.<br>2.Click on &quot;Add Snapshot&quot; Button then Snapshot Description pop-up window is opened.<br>3.write &quot;group&quot;or &quot;any text&quot; on Enter Snapshot Description then Press apply button.<br>4.The Operator Diagram Group Display becomes Crashed.<br>Please find attached Snapshot &amp; Text file of Error Description as &quot;Error occured while Add Snapshot.jpg&quot; &amp; &quot;Error occured while Add Snapshot.txt&quot;. <br>Note:The Operator Diagram Group Display is working fine on Win07(32-bit OS). (Prasad, Parmatma Aug 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Rebuild the Diagram Group program as a 32bit program. (Spillane, Donal A. Aug 24, 2012)<br>Retested in Ov3.5.0_U7 release,the issue has been resolved. (Prasad, Parmatma Aug 27, 2012) <br> |  | 35 | FINDING | 8726 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73798
29847 | FINDING | FFISEL algorithm shows Unkown mode in signal diagram viewer. | Pratley, Bob EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | FFISEL algorithm shows Unknown state in cb viewer. <br>steve has checked it &amp; confirmed that function block is working fine but in cb viewer the bock mode is unknown. (Sahay, Madhukar Aug 10, 2012)<br><br>The block Y0 and/or AMODE point do not correctly reflect the actual mode of the block in the device. The problem appears to be in the controller.<br>- (Hutchison, Steven B. Aug 13, 2012)<br><br>Reassigning to Ben. (Boehmer, Robert W. Dec 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19449 (Benzvi, Mati Mar 4, 2013) <br> |  | 35 | FINDING | 8727 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73800
29848 | FINDING | Amode of FFMAI algorithm shows 0 when block is in auto mode. | Pratley, Bob EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 848T has beem commissioned at 1.1.1 in drop40/90 in emily system. <br>FFMAI algorithm has been used &amp; found that when it is in auto mode then Y0 field (AMODE) of its LC record is 0 instead of 4 (please refer attached snapshot FFMAI_Amode.jpg)<br>However Amode of FFAI is working fine. (Sahay, Madhukar Aug 10, 2012)<br><br>Reassigning to Ben (Boehmer, Robert W. Dec 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A test configuration with an 848T, FFMAI, and FFISEL, has been created in the Embdedded lab. The Y0 field of the LC record is 4 as expected. The AMODE point D40-848T-01-MAI-AMODE also has value 4. Please refer to attached snapshot. (Pratley, Bob Mar 8, 2013) File is FFMAI_Amode_ok.jpg. (Pratley, Bob Mar 8, 2013) <br> |  | 35 | FINDING | 8728 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73802
29849 | FINDING | Update Backup from controller diagnostics gives error. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On drop17/67 which has control synchronization as dedicated cable.<br>When Update backup is done through controller diagnostics it gives error&quot;update failed:Error 0x131d9a0 Recieving Dynamic data from partner&quot;(for reference attached is snapshot)<br>Controller is OCR400 on WALT network. (Kumar, Shailendra Aug 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Potential issues with update backup. (Ciccozzi, Anthony Sep 10, 2012)<br><br>A bug was found (accessing uninitialized ddb table)and will be addressed in a patch. (Ciccozzi, Anthony Dec 11, 2012)<br><br>This has been released in OVA35005. (Ciccozzi, Anthony Feb 20, 2013)<br><br>This is not in OVA350005. Target is OVA350011. Changing state to SDR. Changing RE to Mark Zaremsky. (Boehmer, Robert W. Feb 22, 2013)<br>---<br>msb - Closed; Converted to SDR 19425 @ 22-Feb-2013 (Benzvi, Mati Feb 22, 2013) <br> |  | 35 | FINDING | 8729 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73804
29853 | FINDING | Function block upload & download cause the entire device to fail. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps are performed :-<br>1. Foundation fieldbus module has been configured in 1.1.1 on drop40/90.<br>2. 848T device has been commissioned on its segment1.<br>3. FFMAI algorithm has been used &amp; control sheet is working fine.<br>4. In Developer&quot;s studio gone to 1.1.1 &gt;P01 &gt; 848T device &gt; Function blocks<br>5. Selected FFMAI (Right click) &amp; performed upload then download operation. <br><br>then all the channel value on all the blocks went to BAD quality in signal diagram.<br><br>According to AMS, the device had a NV Memory error.<br>Workaround of this is :--<br>a. Reset the device to factory setting.<br>b. Hard boot of module.<br>c. Set the tunning parameter for function block (e.g FFMAI).<br>d. Clear &amp; download the port. <br><br>- Sahay, Madhukar Aug 13, 2012) (Hutchison, Steven B. Aug 13, 2012) |  |  |  | Test upload/download on several different function blocks to ensure issue is resolved. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Oct 17, 2012)<br><br>MS : Performed upload &amp; download of FFMAI,FFPID &amp; FFAI block.<br> All the function blocks &amp; associated signal diagram was running after this operation.<br> I am closing this finding. (Sahay, Madhukar Nov 29, 2012) <br> |  | 35 | FINDING | 8733 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73813
29854 | FINDING | VXSim Virtual Controller doesn"t come up on the highway if I/O Device Type/Driver is External Ovation Network | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Created a new VC DROP144 on 3.5 (WALT) network with following configurations:<br>I/O Device Number:5<br>I/O Device Type: External Ovation Network<br>I/O Driver Type: External Ovation Network<br>The VIrtual Controller was downloaded successfully. But on reboot it could on come up on the Highway. It remains in white state(in System Status Diagram)with following error:<br>FC 66 Controller Fault<br>FK 01 H Coordinator task fault<br>FS 0005 H Point Edit Error<br>F0 0002 H<br>The snapshot of Ovation Error log is attached for reference. (Lal, Ramesh Aug 13, 2012) |  |  |  | Configure virtual controller with External Ovation Network driver. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem corrected with allowing EON configuration with virtual controller. (Perdeus, Matthew Oct 29, 2012) <br> |  | 35 | FINDING | 8734 |  | FINDING | [10 empty] | Implementation | OVA350005 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
29855 | FINDING | More than 32 Networks cannot be imported or configured in Studio | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Installing Remote networks in a Remote Node by import file aborts on the 33 network,<br>with import error:<br>----<br> [OvPtImport]: Importing Nets_300.imp, all objects<br> [OvPtApi]: (Remote Network Alias Id Value must be between 1 and 32)<br> [OvPtImport]: Required attribute REMOTE_NET_NUMBER_ALIAS at line 319 failed validation<br> [OvPtImport]: &lt;V2Object.cpp:640&gt; Unable to add object NTWRK033 at line 319<br> [OvPtImport]: &lt;V2Object.cpp:641&gt; Any children of this object will be ignored<br> [OvPtImport]: Unable to continue processing Nets_300.imp<br>-----<br>If the 33 network is added manually in Studio under a node, it fails with error:<br> [OvPtApi]: (Field Validation Error) <br> [OvPtApi]: (Remote Network Alias Id Value must be between 1 and 32) (Benzvi, Mati Aug 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK in 3.5.0_U7 @ 25-Aug-2012: Imported 100 networks (Benzvi, Mati Aug 25, 2012) <br> |  | 35 | FINDING | 8735 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73817
29856 | FINDING | ¿Get SMART¿ is incorrectly used in the WHART and CONTROLLER SVTPs | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | The Rosemount tool that is used to communicate with the 1420 Wireless Gateway is named &quot;Smart Wireless Gateway&quot; not &quot;Get Smart&quot;. This should be corrected in the WHART and CONTROLLER SVTPs. (Capani, Nooch Aug 14, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U5 03-AUG-12</p> <p><strong>Originator:</strong> Capani, Nooch</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Capani, Nooch</p> <p><strong>Entry Date:</strong> 2012-08-14T07:42:20-04:00</p> <p><strong>Modified Date:</strong> 2012-08-14T07:42:20-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8736 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73818
29857 | FINDING | RESTORE operation for Ovation Windows drop is giving error | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | RESTORE operation is not working on Ovation Windows drop. This option is available in Dev. Studio right click context menu of Operator Station drops.<br>Steps performed are as follows:<br>1. Initially drop253 (EWS-Net#7) was in fully loaded state.<br>2. Enabled Restore Mode option to &quot;Restore Mode enabled for all drops&quot; from Dev. Studio System level.<br>3. Added few points (Analog &amp; Digital) to drop253.<br>4. Did right click on drop253 &amp; selected &quot;Restore&quot; option.<br>However, it gave error message &quot;Unable to select newly created referenced objects&quot; as seen in attached snapshot file EWS-restore01.jpg. (Gupta, Chandresh Aug 14, 2012) |  |  |  | The affected area is in the internal query identified in the Resolution. The Restore operation should no longer produce this error condition. An additional (and applicable) test is as follows: Initial condition: Drop253 is fully loaded. Add a new digital point to drop253 and modify a point in some other drop such that it now references this new point as an alarm cutout. If the user were to now perform a Restore operation on drop253, the digital point which had been added will now be removed. Note, however, that the point is the other drop which had been referencing this digital point as an alarm cutout should now show-up as an unresolved reference (e.g., warning) if an consistency check were performed on that other drop (or at some higher level of the hierarchy). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The particular query being performed (in this case) is a preliminary step which identifies objects (external to the drop being restored) which reference objects IN this drop and are not in the undo image. The internal execution of this query is different in this version of Oracle than in previous versions. As a result, the query will be modified slightly. (Swartz, Mark E. Aug 14, 2012)<br><br>cg (08/21/12) - Finding retested in 3.5.0_U6. RESTORE operation was checked on EWS, Ctlr &amp; VC drops per steps mentioned in the description field above. The operations were successful. Also, as mentioned in &quot;Affected Areas and Test Recommendations&quot; field below, performed operation where point referencing was involved. The drop got restored finally &amp; consistency check of the reference drop showed unresolved reference (please see the attached screenshot file Restore-ref.jpg). This is ok hence finding closed. (Gupta, Chandresh Aug 21, 2012) <br> |  | 35 | FINDING | 8737 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U6 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73820
29858 | FINDING | Advanced Virtual controller could not be configured | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On 3.5 (WALT Network) created a new VxSim Controller Drop Type:Advanced Vitual Controller.While download to this drop was successful, on reboot it did not come up on the <br>highway. Thee is no error message in the Ovation Error log. (Lal, Ramesh Aug 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This looks like a duplicate of finding 8900. (Boehmer, Robert W. Oct 29, 2012)<br>---<br>msb - Closed; Converted to SDR 19148 (Benzvi, Mati Oct 29, 2012) <br> |  | 35 | FINDING | 8738 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73822
29859 | FINDING | All the Virtual Controllers do not go off highway when Ovation Virtual Host Service is stopped. | Perdeus, Matthew AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 5 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | There are 5 Virtual Controllers configured on 3.5 (WALT) Network e.g. DROP141, DROP142, DROP143,DROP144,DROP145. When Ovation Virtual Host Service is stopped it is seen that not all the Virtual Controllers go off highway. Few of them are still on the highway in Failed mode as seen in the System Status Diagram. Please refer the attached snapshot. (Lal, Ramesh Aug 14, 2012) |  |  |  | Shutdown of vcoordinator service should stop all virtual controllers on that host. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | An issue was corrected the stopping of virtual controllers. (Perdeus, Matthew Aug 17, 2012)<br><br>8/31/12:RL - Tested in 3.5_U7. All Virtual Controller still do not stop when Ovation Virtual Host Service is stopped. Filding Failed Retest. Please refer the attached snapshot. (Lal, Ramesh Aug 31, 2012) <br> This should be fixed in U8. Please re-test. (Boehmer, Robert W. Oct 29, 2012)<br><br>1/03/2013:RL -Retested on VCH Drop182 on Net#8 in IEC which has 12 VCs (including 2 backup VCs). When Vcoordinator.exe was stopped through Task Manager none of the VCs stopped. There were 12 instances of vxsim.exe still running as seen in Task Manager.Hence, Finding is failed retest. (Lal, Ramesh Jan 3, 2013)<br><br>This should be tested by stopping the service properly. Killing the process from task manager will not stop the virtual controllers. (Perdeus, Matthew Jan 3, 2013)<br>1/04/2013:RL - Stopping Ovation Virtual Host service from Administrative Tool stops all the Virtual controllers (whereas Vcoordinator service from Task Mnager will not).But it doesn&quot;t happen always.It was noticed twice that 2 (and 3)VCs out of 12 did not stop.Please refer the attached snapshot. (Lal, Ramesh Jan 4, 2013)<br><br>Please stop service and ensure all virtuals are stopped. If not, kill them via Windows task manager. Edit the file c:\ovation\vcoord\config\config.log file so that the LevelFile options are <br>all set to 8. Restart the service and retest. Please send the \Ovation\vcoord\log\emulog00x.txt files after seeing this occur. (Perdeus, Matthew Jan 7, 2013)<br>1/18/13:RL - Emulog00 files are attached for scenario i. when 1 out of 15 VCs did not stop, ii.when 2 out of 15 VCs did not stop. (Lal, Ramesh Jan 18, 2013) |  | 35 | FINDING | 8739 |  | FINDING | Staab, Randy AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Lal, Ramesh External | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
29861 | FINDING | Digital points are not display with the correct textual set or reset in Historical review. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Historical Review will not display the correct textual or currect value with associated description.If I am change the digital value zero to one after that Operater event showing entered value in historical reviews display . (Kumar, Sudheer Aug 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | It is believed that this issue exists with the origination of the operator event that is sent to the OPH. (Contento, James L. Sep 13, 2012)<br><br>IC 9/27/12 - moved Product &amp; Release from OPH to Ov 3.5 Win Opcon. (Capani, Nooch Sep 27, 2012)<br><br>Create an SDR. (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: converted to SDR 19112 @ 08-Oct-2012 (Benzvi, Mati Oct 8, 2012) <br> |  | 35 | FINDING | 8741 |  | FINDING | Contento, James AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73829
29862 | FINDING | VxSim Virtual Controllers enter into alarm even though no operation is performed on them | Perdeus, Matthew AUTOSOL PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | We have configured 6 Virtual Controllers (Drop141-Drop146)on 3.5 WALT network. It is observed that many of these VCs enter into alarm even though no operation has been performed on them. In the System Status diagram we see following message:<br>FC: 66 Controller Fault<br>FK: 01 H Coordinator Task Fault<br>FS: 000C H Monitor Task Warning<br>F0: 0013 H<br>After Acknowledging and Clearing Drop alarm, these alarm go off but appear again after some time. (Lal, Ramesh Aug 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is on drop244 and believed to be related to F 8866 (drop244 high CPU usage). (Perdeus, Matthew Oct 31, 2012) <br> |  | 35 | FINDING | 8742 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
29863 | FINDING | Few changes required in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | There are few changes required in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc. They are:<br>1. Test case 5.1.18 says &quot;Start Symbol Builder&quot; from Studio. However, Symbol Builder could only be opened from Control Builder &amp; not from the Developer Studio directly.<br>2. &quot;Allow Modification of Ancilliary Data&quot; test needs to be included under Security Functions Test cases 5.8.6 (Local) &amp; 5.8.6 (Remote). This is the new feature in the current release. (Gupta, Chandresh Aug 17, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U4 16-JUL-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-08-17T07:35:44-04:00</p> <p><strong>Modified Date:</strong> 2012-08-17T07:35:44-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8743 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73832
29864 | FINDING | sisio1 error and Hardware point showing BAD quality on SIS 1100 controller. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | After changing SIS controller(drop2/52,PGH lab) from OCR400 to OCR1100 following is the observation:<br><br>1)Error is seen in error log:<br>FRI AUG 17 19:02:17 2012 : 0x2277fe0 (sisio1): task 0x2277fe0 has had a failure and has been stopped.<br>FRI AUG 17 19:02:17 2012 : 0x2277fe0 (sisio1): fatal kernel task-level exception!<br><br>2)Hardware point assigned to SIS I/O channel and used in LSAI/LSDI algo are showing as BAD quality.<br><br>Status diagram shows controller &quot;s Fault code as:66,b,6,8029 H<br><br>For detail attached is the error log and snapshot.System is loaded with U6. (Kumar, Shailendra Aug 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed handling of SIS interface for OCR1100 (Czak, Jakub Oct 31, 2012) <br> |  | 35 | FINDING | 8744 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73834
29865 | FINDING | For points which are not Trendable message is incorrect in Trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | For LC,RM,RN,DU and PD point if opened in Trend shows &quot;Point not Found&quot; which is incorrect since point exists on system.Older Trend showed these point as &quot;Specified Point is not trendable&quot;. (Kumar, Shailendra Aug 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest in 3.5.0_U8<br><br>New Trend App will allow the addition of such points, but will set the description to &quot;Point not trenadble&quot;. Apparently OPH can collect data for such points. (Bargaje Prashant Sep 12, 2012)<br><br>SK:Tested in U9 its OK for all except LC points hence failed retest. (Kumar, Shailendra Oct 23, 2012) <br> |  | 35 | FINDING | 8745 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Piolo, Jean-Frederic EMR SYSS PSS SPRI | [6 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73836
29866 | FINDING | ELC module does not communicates with controller diagnostic window. | Plymire, Alvan AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps are performed in Emily system :-<br><br>1. A new ELC module has been configured in 1.1.3 at drop40/90.<br>2. Drop40/90 has been loaded.<br>3. In controller diagnostic when firmware download was tried for ELC module then blank <br> window appeared (please refer attached snapshot Module Firmware_ELC.jpg).<br> <br> Further it is observed : At 1.1.1 Field bus module was configured &amp; working fine<br> when step 3 has been performed then field bus module also stop communicating with <br> controller diagnostic but control sheet containing ff algorithms keep updating the <br> values. (Sahay, Madhukar Aug 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/19/12 - per Al P. this is fixed. Please retest with U8 and latest ELC 1.2. (Capani, Nooch Sep 19, 2012)<br><br>MS : Checked in U8 &amp; ELC1.2_U7 , found fixed. I am closing this finding. (Sahay, Madhukar Sep 20, 2012) <br> |  | 35 | FINDING | 8746 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U8 ELC.1.2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73838
29867 | FINDING | Network Configuration Tool -&gt Properties on VCH does not exit after required change during upgrade | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Steps for upgrading a VCH, in the Network Configuration Tool, <br>a. Right click the Network bridge connection and select Properties<br>b. In the Adapters box, get both NIC of WRTAP &amp; 1st Ovation NIC checked.<br>c. Select the DDB Protocol for the bridge (Ovation NIC)<br>d. Click [OK].<br>At that point, on some W7 drops, the selections are saved but the Network Configuration UI <br>is not closed (display a &quot;In use&quot; clock). <br>The drop has to be be hard rebooted to recover. (Benzvi, Mati Aug 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Proper procedure will be addressed in user manual. If upgrading an existing 3.5 VCH, this requires deleting the existing bridge and recreating new bridge. (Perdeus, Matthew Nov 14, 2012)<br><br>This was addressed in user manual. (Perdeus, Matthew Feb 21, 2013) <br> |  | 35 | FINDING | 8747 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73840
29868 | FINDING | Error message is not displayed in Consistency check on System level | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Consistency check on system level flags on top: <br> Error: 1, Warnings: 12, Info: 54814.<br>In the canvas area it only shows:<br> 3 Warnings on the Top, 1 Warning on the bottom, All or some Info in the middle<br>but the Error message is not displayed. (Benzvi, Mati Aug 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK if you click on the column header to resort all entries,<br>we can see the - Error: 1, Warnings: 12 and all Info messages. (Benzvi, Mati Aug 20, 2012) <br> |  | 35 | FINDING | 8748 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73842
29869 | FINDING | Real limit of points number on Controller defined for 32000 is 31999. | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Controller defined to use 32000 loaded with maximum point number fails due to maximum points exceeded. It was verified that configuration with 31999 points can be loaded to the controller. Similar problem appears on controller configuration of 16000 and 6000 points. Real limit is one point lower than configuration (15999 and 5999). (Zochowski, Piotr Aug 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Will update documentation.<br>Although we publish 32000/16000/6000 points, due to the way this is indexed the actual number is that -1. So the actual maximums are 31999/15999/5999. We recommend leaving at least 25% spare capacity, so in theory the user should never see this limitation, but I want to ensure it is documented. (Pingree, Douglas K. Sep 4, 2012) <br> The Controller documents will be updated with the following information:<br><br>For Maximum Point Limit:<br>This radio button selects the maximum number of points that the Controller can be configured to monitor.<br>Due to the way points are indexed, the actual point number is the maximum point count minus 1.<br>Normal handles up to 6000 points. (Actual limit = 5,999)<br>Expanded handles up to 16,000 points. (Actual limit = 15,999)<br>32000 handles up to 32,000 points. (Actual limit = 31,999) <br>Note: Additional shared memory may be required to accommodate additional points. (Skena, Ronald E Sep 12, 2012) |  | 35 | FINDING | 8749 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Ritenbaugh, David PROCESS PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73844
29870 | FINDING | SOE timestamps do not have 1 ms precision | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | We prepared a test environment with 2 redundant pairs of controller. Each controller pair have SOE module. We configure it in that way, we have got the same event to both SOE modules, so we should receive event message from both cards with the same timestamp. All controllers have been synchronized directly with reliable time source (Symmetricon GPS time server).<br>During our test we observed time difference between timestamps in range from 0ms to 26 ms. That difference is unacceptable, because we do not have 1ms precision in SOE timestamps.<br><br>We have also executed the same test on Ovation 3.3.1 and here time differences between SOE timestamps were in acceptable range: from 0ms to 2ms. (Kossowski, Grzegorz Aug 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The IOIC was not being synced properly. Now the IOIC is being synced with the SNTP time more accurately. This can be tested by triggering two SOEs on separate controllers using a single source. It is important that this scenario be tested with a dedicated time server as a windows domain controller does not provide an accurate time source. (Pingree, Douglas K. Aug 22, 2012) <br> |  | 35 | FINDING | 8750 |  | FINDING | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW | Perdeus, Matthew AUTOSOL PWS PITT |  |  | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73846
29871 | FINDING | Loading first time (control sheet) in every Virtual Controller thru the alert message. | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1. Open Virtual Controller <br>2. Add control task-&gt;control sheet-&gt;Add Algorithms-&gt;compile-&gt;Load<br>3. While loading the control sheet developer studio thru the alert message <br> says &quot;Load operation to Drop XYZ has been aborted and must be reinitiated&quot; <br><br>Please find the attachment this is happing only in first time loading, <br>But it occurs every time in every virtual drop.<br>Press &quot;OK&quot; button in this message and loading again it&quot;s getting load the drop. (K, SendhilKumar Aug 20, 2012) (Pingree, Douglas K. Aug 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is an error from dev studio, not the controller. I believe this is fixed in U7, but I am transferring this to Kim Costlow for confirmation. (Pingree, Douglas K. Aug 22, 2012)<br><br>Please retest. (Costlow, Kimberly A. Sep 24, 2012) <br> |  | 35 | FINDING | 8751 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73848
29872 | FINDING | In the Help file "30ms" should be replaced with "30000ms". | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0 Help file for both OCR400 &amp; OCR1100, five control areas, each with selectable speeds will be 10ms-30000ms. So, in the Help file, &quot;30ms&quot; should be replaced with &quot;30000ms&quot;.<br>Please find the attached JPEG files &quot;Finding_U6_Help1&quot; and &quot;Finding_U6_Help2&quot; for the issue marked. (Mitra, Sambuddha Aug 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The following correction will be made to the OCR400 manual OW350_54 and the OCR1100 manual (OW350_58).<br><br>OCR1100<br>Five control areas, each with selectable speeds (10ms - 30 seconds). (Skena, Ronald E Sep 12, 2012)<br><br>Verified this in OV.3.5.0_U8 and the issue is resolved. Hence closing the finding. (Mitra, Sambuddha Sep 20, 2012) <br> |  | 35 | FINDING | 8752 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73850
29873 | FINDING | Controller Diagnostics shows Ethers address for VxSim Virtual Controller which is incorrect | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | VxSim Virtual Controllers do not have Ethers address defined in Ovation Developer Studio. But Controller Diagnostics shows an arbitrary number for them. For excample Virtual Controller Drop145 dosn&quot;t have Ethers address but In controller Diagnostics its Ethers address is /a:/a:ac:10:2a:91. (Lal, Ramesh Aug 20, 2012)<br><br>9/24/12:RL - O.K. in 3.5_U8 (Lal, Ramesh Sep 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8753 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73852
29874 | FINDING | Installation of Ov-3.5.0_U6 from a DVD stalls and force to abort with OvSisEvant.Service error | Budzynski, Piotr EMR SYSS RS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Installation of Ov-3.5.0_U6 from a DVD on a new Server or upgrade of older update stalls and forces the installer to abort with &quot;OvSisEvents.Service.exe -install&quot; error.<br>Duplicated in Austin &amp; Pgh with the same results.<br>--<br>Piotr manually added missing files to the Austin server. <br>Error attached. (Benzvi, Mati Aug 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - OK in Ov-3.5.0_U7 @ 25-Aug-2012 (Benzvi, Mati Aug 25, 2012) <br> |  | 35 | FINDING | 8754 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Maxwell, Jeffrey C EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73854
29875 | FINDING | PWSIT - Unable to launch control builder for newly created control sheet | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Attemp to create a control sheet for Fieldbus algorithm control but control builder window doesn&quot;t launch. An IE window popup but never completely launch.<br><br>Steps to reproduce:<br>- Right click on &quot;Control Sheets&quot; under controller drop system tree in Developer studio and select &quot;Insert New&quot;<br>- Fill in required information for sheet then click OK<br>- IE window popup with blank screen and remain there indefinitely. (Phan, Quang Aug 20, 2012)<br>(see attachement for detail) (Phan, Quang Aug 20, 2012) | In certain scenarios, the control builder window may not open. A blank Internet Explorer pops up and remains indefinitely (F#8755). This may be caused by certain Microsoft patches resetting the file association between the Control Builder Editor and the Scalar Vector Graphics (SVG) file extension. The following link expains how to reset the assocation: http://windows.microsoft.com/en-US/windows-vista/Change-which-programs-Windows-uses-by-default You will want to open the link &quot;If a program does not show up in the Programs list&quot; for step 3 you want to select the record with &quot;.svg&quot; for &quot;Name&quot; Select the cbEditor.exe. It should be in the short list. If you have to browse, it is in c:\Ovation\CtrlBldr |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Certain MS patches reset the file association between the Control Builder Editor and the Scalar Vector Graphics (SVG) file extension.<br><br>The following link expains how to reset the assocation:<br><br> http://windows.microsoft.com/en-US/windows-vista/Change-which-programs-Windows-uses-by-default<br><br>You will want to open the link &quot;If a program does not show up in the Programs list&quot;<br><br>for step 3 you want to select the record with &quot;.svg&quot; for &quot;Name&quot;<br><br>Select the cbEditor.exe. It should be in the short list. If you have to browse, it is in c:\Ovation\CtrlBldr (Hutchison, Steven B. Aug 21, 2012) <br> This is a work around. Initial installation of Ovation should set this automatically w/o requirement for user to set this manually. (Phan, Quang Aug 21, 2012)<br><br>It does some of the microsoft patches occationally reset the ovation install.<br>- (Hutchison, Steven B. Aug 22, 2012)<br><br>IC 8/29/12 - per Val+Dev mtg, document in DIR. Also changed to CAT 3 since work-around exists. (Capani, Nooch Aug 29, 2012)<br><br>IC 9/27/12 - added info to DIR, closed finding. (Capani, Nooch Sep 27, 2012) |  | 35 | FINDING | 8755 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73856
29876 | FINDING | Poke7/23/9:-.pdf file should give pop up if path name is incorrect. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce: <br><br>1 Create a poke (poke7/9/23) in GBNT and assign a path of a pdf file(which do not exist in system e.g. &quot;xyz.pdf&quot;). save and download the diagram, open the graphic application and click on the poke to open the pdf file.<br>Observation:a pop up appears showing the &quot;The file can not be found&quot;. Which is ok. Please find the attached screen shot. The same pop up is coming for other applications also (.xls, .doc, .txt).<br>2. Repeat the above step by giving a file name (which actually exist in the system) but with wrong path .<br>Observation: No pop up came (though file is not opening which is ok). In other application (.xls, .doc, .txt) the pop up is coming. <br>A pop up should come in case2 also for pdf file.<br>please find attached remote login details. (Joshi, Parmesh Aug 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A message is being displayed in the status bar of the graphic window indicating that the file does not exist. (Spillane, Donal A. Aug 24, 2012)<br><br>I was assuming that for case2 the pop up will come as it comes for .xls and .doc applications.<br>Closed . (Joshi, Parmesh Aug 31, 2012) <br> |  | 35 | FINDING | 8756 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73858
29877 | FINDING | SimControl.exe and Simapi.exe do not work in VxSim Virtual Controller | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In VxSim Virtual Controller simulation functions e.g. Run,Freeze,Save,Load Snapshot,Start,Stop do not work as Sim Control.exe and simapi.exe could not be run.<br>Please refer the attached snapshot. (Lal, Ramesh Aug 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added missing dlls to the build. (Pingree, Douglas K. Aug 28, 2012)<br><br>8/30/2012:RL - SimControl.exe and Simapi.exe are working in 3.5_U7. Finding closed. (Lal, Ramesh Aug 30, 2012) <br> |  | 35 | FINDING | 8757 |  | FINDING | [10 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73860
29878 | FINDING | Fieldbus tuning dialog missing values in enumerated parameter combo-boxes | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 11:22 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 11:22 |  |  |  | 2019-07-02 11:22 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Parameters with enumerated combo-box values are missing an entry from the list within standards template. (Christoforetti, Matthew M. Aug 21, 2012) |  |  |  | Open tuning dialog for a function block. Select a sample of tuning boxes for parameters that have an enumerated drop-down list. Verify entry list shows all values. Can verify against values in template: OvPtSvr/FoundationFieldbusDevices/Standards/&lt;Function Block Name&gt;.xml | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | mmc - Fixed iterator - 8/21/2012 (Christoforetti, Matthew M. Aug 21, 2012) <br> |  | 35 | FINDING | 8758 |  | FINDING | Pratley, Bob EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | USPITTFSService | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U9 |  |  | FINDING | [6 empty] | 143807
29881 | FINDING | Simcontrol.exe not supported in Ov3.5.0 machines.SDR-18575 failed. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | SDR-18575 failed. <br>We could not open Simcontrol.exe in 3.5.0 machines (VCH &amp; EWS).But it is showing task manager for some seconds &amp; it disappeared.<br>Please find the attachment. (K, SendhilKumar Aug 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added missing dlls into the build. (Pingree, Douglas K. Aug 28, 2012) <br> |  | 35 | FINDING | 8761 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U7 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73868
29882 | FINDING | Control task of VxSim controller go into Suspended state sometimes | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | VxSim Virtual Controllers (Drop141 - Drop146)are defined on 3.5 WALT network. It is observed that sometimes Control Task of these controllers go into Suspended state (instead of Enabled) as viewed in Controller Diagnostics Control Task Info tab. It happens more frequently for Control Task 1. A reboot of the controller will solve the problem but it will reappear after some time. Please refer the attached snapshot. (Lal, Ramesh Aug 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is on drop244 and believed to be related to F. 8866 (drop244 high CPU usage). (Perdeus, Matthew Oct 31, 2012)<br><br>1/03/2013:RL - This was happening due to avp.exe consuming most of the CPU time <br> This problem was not seen in IEC. Hence, finding is closed. (Lal, Ramesh Jan 3, 2013) <br> |  | 35 | FINDING | 8762 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73870
29883 | FINDING | VxSim Controller enter into "RESERVED ERROR" often on their own | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | On 3.5 Walt network 6 VxSim Controller drops (Drop141 - Drop146) were rebooted so that they do not have any alarm/error and kept under observation. After about an hour 3 out of 6 Controllers went into &quot;Reserved Error&quot; as seen in the System Status Diagram.The fault codes are:<br>FC = 66 Controller Fault<br>FK = 01 H Coordinator Task Fault<br>FS = 000E H Reserved Error<br>f0 = 000 H<br>A reboot of the controller will remove the error but will appear again. Please refer the attached error log for your reference (Lal, Ramesh Aug 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is on drop244 and believed to be related to F. 8866 (drop244 high CPU usage). (Perdeus, Matthew Oct 31, 2012)<br><br>1/03/2013:RL - This was happening due to avp.exe consuming most of the CPU time which was a local issue. This problem was not seen is IEC. Hence finding is closed. (Lal, Ramesh Jan 3, 2013) <br> |  | 35 | FINDING | 8763 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73872
29885 | FINDING | PROFIBUS points go to Bad Quality when a controller failover is performed. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OCR400 Controller 39/89 (EMILY) is configured with PROFIBUS modules, devices and points. When a soft reboot of the controller in Control is performed, all of the process points assigned to signals go to Bad Quality for about 10 seconds. All of the modules were downloaded and rebooted prior to this occurring. (Brown, Sean Aug 22, 2012)<br><br>OCR400 Controller 38/88 (EMILY) is configured with DeviceNet and demonstrates the same behavior. (Brown, Sean Aug 22, 2012)<br><br>The same behavior was observed with both sets of above controllers converted to OCR1100s. (Brown, Sean Sep 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The driver thinks the dbm files on the module need to be updated (as if there was a different DBM file on the primary and backup controller). If there is a mismatch between the dbm files on the primary and backup, when the failover occurs the driver will download the dbm file (which involves setting the points to bad quality and alarming the node records). So the behavior would be expected. However, in this case the files appear to be matched between the primary and backup. Will need to investigate. (Ciccozzi, Anthony Sep 6, 2012)<br><br>There was a change in the filesystems between VxWorks5.4 and VxWorks6.8. In 5.4 capitalization did not matter. In 6.8 it does. There was code that identified the dbm files by device type (&quot;PB&quot; or &quot;DN&quot;) additional logic was added to account for lower case &quot;pb&quot; or &quot;dn&quot;. The driver was not processing the dbm files b/c it thought they were invalid. (Ciccozzi, Anthony Sep 6, 2012)<br><br>Appears to be resolved in U8; closing. (Brown, Sean Sep 20, 2012) <br> |  | 35 | FINDING | 8765 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Plymire, Alvan AUTOSOL PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73876
29886 | FINDING | PWSIT - Unable to commission Fieldbus device from "Mismatch" state | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Fieldbus device was previously commissioned on older Ovation. Verified using DeltaV host and confirm device is in &quot;Mismatch&quot; state.<br>When try to commisison it on new fieldbus segment, transition to Standby process hang and unable to move on. (see attached screenshot)<br><br>Tested using 3 different devices, all in &quot;Mismatch&quot; state, and all encounter the same issue:<br>Rosemount 3244 Rev 3<br>Rosemount 644 Rev 1<br>Fisher Control DVC6000 Rev 1<br><br>Step to reproduce:<br>- On FF segment, connect &quot;Mismatch&quot; device<br>- On Studio Hardware tree, browse to the same FF port, create new device and points as needed<br>- Download port<br>- Load controller<br>- Right click on newly created device and select Commission<br>- Window popup stating that no device available, select &quot;Acclimate Non-Commissioned Devices&quot; to put device in Standby state<br>- Observed that process is hang while device transition to Standby.<br><br>Work around:<br>- Move device to other host and decommission device to Spare or Standby state (Phan, Quang Aug 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This issue was caused by two issues.<br><br>1) Mismatched devices on working segment can be set to off-line via the live list context menu.<br>2) When the segment is uninitialized the live list will contain one entry in an unknown state. In this case, download the segment to initialize the segment.<br><br>- (Hutchison, Steven B. Sep 4, 2012) <br> Follow Steve&quot;s instruction to put device in offline stage from live list menu. Continue with commission process. &quot;Acclimate Non-Commissioned Devices&quot; process was able to complete within 10 minutes and did place offline device into standby mode. Was able to select device and complete commission process. Validated in 3.5 build U9. (Phan, Quang Oct 23, 2012) |  | 35 | FINDING | 8766 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73878
29887 | FINDING | Bit 2 & 3 details in PI of 1W Status Word for LD, LP, DD & DP needs to be added | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Bit 2 &amp; 3 details in PI of 1W Status Word for LD, LP, DD &amp; DP are presently appearing as &quot;Not Applicable&quot;. These bits are getting active during Alarm Cutout operation. Hence description of these bits need to be added.<br>Please see the attached snapshot file. (Gupta, Chandresh Aug 23, 2012) |  |  |  | The bit descriptions for bits 2 and 3 of 1W for LD, LD, LP, DP, RM, and RN points have been updated. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | cg (09/19/12) - Finding retested in Ov3.5.0_U8. Bit details for 2 &amp; 3 are available. Hence this finding is closed. (Gupta, Chandresh Sep 19, 2012) <br> |  | 35 | FINDING | 8767 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73880
29888 | FINDING | Fieldbus Migration did not migrate some attributes | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:47 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:47 |  |  |  | 2019-07-02 10:47 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Migration missed port attribute for Max inter chan Skew <br>Migration missed function block paramters <br>for EU0, EU100 , IO_OPTS , STATUS_OPTS ENUMS (Shiferaw,Tedla Aug 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Missed port attribute . Fixed<br>all function block parameters are captured. The only parameter left is SUBSTITUTE_IN (Shiferaw,Tedla Sep 10, 2012) <br> |  | 35 | FINDING | 8768 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | Pratley, Bob EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | Shiferaw, Tedla AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U9 |  |  | FINDING | [6 empty] | 143796
29891 | FINDING | SVTP "SRF1524_SVTP_rev1.1_PJ" need modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | SVTP &quot;SRF1524_SVTP_rev1.1_PJ&quot; need modification as follows:<br>1. Test case 5.2.1 &amp; 5.2.2: Step 1: Verify that Test 5.1.2 is done and Poke windows is inserted. should be modified as &quot;Verify that Test 5.1.2 &amp;5.1.3 is done and Poke windows is inserted.<br>2. Test case 5.2.2: Case2:Step 3: &quot;Case 2) of Test 5.2.3 should be repeated ....&quot; should be change as &quot;Case 2) of Test 5.2.2 should be repeated .....&quot; (Joshi, Parmesh Aug 24, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Optional SW (OSW)</p> <p><strong>Release Level:</strong> 3.5.0_U6 17-AUG-12</p> <p><strong>Originator:</strong> Joshi, Parmesh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Joshi, Parmesh</p> <p><strong>Entry Date:</strong> 2012-08-24T04:05:17-04:00</p> <p><strong>Modified Date:</strong> 2012-08-24T04:05:17-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8771 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73886
29892 | FINDING | Print operation for SIS sheets hangs the cbeditor window. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps were done on SIS network :<br>1)Right click SIS controller drop2/52 &lt;Control Option&gt;----&gt;Print Operation---&gt;Title sheet and selected 2 SIS sheets.1st selection is Sheet nos 111 and 2nd is sheet nos 121 in print opertion sub window(for reference attached is the exported sheet).<br>2)On clicking next it hangs the cbeditor.Error in background shows error for OCBDComApi.dll(attached is the error).<br><br>Shown above issue to Matt. (Kumar, Shailendra Aug 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is an unlikely scenario. The first sheet in every drop is typically selected when generating title sheets. Generate a cat 4 SDR. This is really a nuisance crash. Persistent data is not effected and no functionality is lost.<br>- (Hutchison, Steven B. Sep 11, 2012)<br>---<br>msb - Closed: converted to SDR 19049 (Benzvi, Mati Sep 25, 2012) <br> |  | 35 | FINDING | 8772 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73888
29894 | FINDING | Fielbus device alert is not functional. | Morris, Gilbert L AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | 848T has been commissioned in 1.1.1 at drop40/90.<br>Plant web alert has been configured for the same.<br>it is observed that any of the device alert (failed, communication etc) is not appearing.<br>e.g When 848T is removed from the bus then Ccommunication alert does not appeared. (Sahay, Madhukar Aug 24, 2012) |  |  |  | Retest Plant Web Alerts on several different types of Rosemount devices. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | At the time this finding was written, it appeared that the Plant Web Alerts on the effected system weren&quot;t working, but they were on a different system. It was also noticed during testing, that a Plant Web Alert was being broadcast on a different bit. The necessary change was implemented in U9. (Morris, Gilbert L. Oct 15, 2012) <br> |  | 35 | FINDING | 8774 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73892
29895 | FINDING | While Adding Multi-Network points stops buffering of points which are already in trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Its observed that Trend is running local point and making sine wave, in this running trend if we browse point and add point from different network(which are added for first time on this drop&quot;s trend)its observed that for few seconds buffering stops for already running point i.e Sine wave becomes straight line for few seconds.<br>Shown this issue to Prashant (Kumar, Shailendra Aug 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest in 3.5.0_U8 (Bargaje Prashant Sep 12, 2012)<br>SK:ok in U9 hence closed. (Kumar, Shailendra Oct 23, 2012) <br> |  | 35 | FINDING | 8775 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73894
29896 | FINDING | Firmware Download fails for HART High Performance Analog Output module | Durbin, Michael EMR SYSS PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 3 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | While testing High Performance HART I/O module it was noticed that Firmware Download can&quot;t be<br>performed on HART High Performance Analog Output module. It shows &quot;FAILED&quot; status at the end of the download. However, for HART High Performance Analog Input module The Firmware Download is successful. Please refer the attached snapshot. (Lal, Ramesh Aug 24, 2012) |  |  |  | Re-test firmware download with a different High Performance HART AO module. Refresh controller diagnostics or restart the application entirely before testing with a different module. Troubleshoot per the instructions in the Resolution section. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | It is possible this was a faulty module or had experienced a failure during another firmware download. Downloads were successful when trying to reproduce the issue. The only time the downloads failed were when the module was &quot;bricked&quot;. 1) Open a console to the controller, 2) Type ld &lt; /ata0/controller/io_tools 3) Type io_tools 4) Select Menu Option 3 (i/o) -&gt; 14 (module firmware: read module version) -&gt; select device number 0 -&gt; Enter hw address for reg b (i.e. if 0x4800 enter 0x480b - address can be obtained from controller diagnostics or hardware tab of module record) -&gt; Select 2 (high performance HART A0). 5) Check the status that prints - if it failed (i.e. cycle status = 0x4000) then the module most likely needs reflashed). (Ciccozzi, Anthony Mar 5, 2013)<br><br>4/16/2013:RL - 1.Retested.The Firmware download failed again. Please refer the attached snapshot. <br>2. The console session with OCR400 Controller Drop32/82 (hardware address as seen in Controller Diagnostics:48a0)is attached. At the end of the session the Module Firware Version shown is 7 (same as Controller Version).We have only one High Performance Analog Output module in IEC. (Lal, Ramesh Apr 16, 2013) <br> |  | 35 | FINDING | 8776 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
29897 | FINDING | VCH (32b) freezes during upgrade and requires hard reboot. VCH 244 is unusable. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | VCH (32b) freezes during upgrade when selecting:<br>f(2). Within the Network Configuration tool, Right click the Network bridge connection.<br> a. Select Properties.<br> b. In the Adapters box, get both NIC of TAP-Win32 &amp; 1st Ovation NIC checked.<br>A forced hard reboot is required to continue.<br>On drop244 (WALT) upon every hard reboot the drop freezes again and networking is diconnected.<br>On drop127 (EMILY) the drop recovers and operate after the hard reboot.<br>On VCH (64b) - drop139 (SIS) upgrade goes smoothly with no problems. (Benzvi, Mati Aug 25, 2012)<br>---<br>msb - 8/28 - drop244 no longer freezes after the weekend. Will keep Monitoring. (Benzvi, Mati Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8777 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73898
29898 | FINDING | Cannot import or insert the 130th Remote network: No License Available | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Importing Remote networks fails on the 130th netork because of License error:<br><br>[OvPtImport]: Importing Nets_200.imp, all objects<br>[0] ¦&lt;OvPtSystemValidate.cpp:9042&gt;¦ [OvPtApi]: (There are not enough Remote Network licenses available)<br>[OvPtImport]: &lt;V2Object.cpp:1769&gt; Failure in CheckLicensing for object NTWRK130 at line 420<br>[OvPtImport]: &lt;OvPtImport.cpp:644&gt; Unrecoverable error encountered, terminating...<br>----<br><br>In Studio inserting the 130th Remote Network fails with error:<br>*--------------------&gt; Error Information &lt;--------------------*<br>Unable to complete the requested operation <br>Code : 0x80004005 Source : Ovation Developer Studio<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br>&lt;OvPtObject.cpp:1637&gt; [OvPtApi]: (System Validation Failure)<br>&lt;OvPtSystemValidate.cpp:9042&gt; [OvPtApi]: (There are not enough Remote Network licenses available)<br>------<br><br>The License tool Max Remote numbers is 126 (see F# 8224) (Benzvi, Mati Aug 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Ok in Ov-3.5.0 - Both Import &amp; Insert of &gt; 130 Remote Networks (Benzvi, Mati May 23, 2013) <br> |  | 35 | FINDING | 8778 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73900
29899 | FINDING | Can not deselect the Toolbars option in Ovation System Viewer. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0 following steps are performed: Open Ovation System Viewer---&gt;Right click on Active Instance Indicator---&gt;click on Customize... Here we can not deselect the Toolbars option &quot;bar2&quot;.<br><br>Please see the attached snapshot for details. (Mitra, Sambuddha Aug 27, 2012) |  |  |  | Please run this same test over other sections of the display. I have fixed all of the occurences I could find. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This will be fixed in the next update. There was a problem with the main status bar, the search results bar and hierarchy bar. (Wozniak, Diane M. Sep 10, 2012)<br><br>Verified this finding in OV.3.5.0_U8 and seen that the issue is resolved. Hence closing the finding. (Mitra, Sambuddha Sep 19, 2012) <br> |  | 35 | FINDING | 8779 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73902
29901 | FINDING | "Diagrams" should be replaced with "Diagram". | Swartz, Mark EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0 following steps are performed: Open Ovation developer studio--&gt;Select a drop(EWS)--&gt;Configuration--&gt;Alarm--&gt;Iconic--&gt;Groups--&gt;Insert New Diagrams Wizard. Here &quot;To Insert A New Diagrams...&quot; should be replaced with &quot;To Insert A New Diagram...&quot;.<br><br>Please see the attached snapshot for details. (Mitra, Sambuddha Aug 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The dialog text &quot;To Insert A New Diagrams. Fill in the fields below&quot; is generated automatically based on the type of item. Specifically, the word &quot;Diagrams&quot; is exactly the same as that shown in the hierarchy. This behavior is not specific to this particular object. Please note that one would observe the same if one were to insert an Analog point (which is identified in the hierarchy as &quot;Analog Points&quot;). (Swartz, Mark E. Aug 27, 2012)<br><br>Modification of the text shown in this type of dialog window will be considered in the next release. (Swartz, Mark E. Aug 28, 2012) <br> |  | 35 | FINDING | 8781 |  | FINDING | [10 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73906
29902 | FINDING | HART Devices connected to High Performance AI and High Performance AO module do not communicate with AMS 11.5 | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | High Performance Hart Analog Input and High Performance Hart Analog Output modules are configured on 3.5 WALT network.Following are the Version Numbers:<br>High Performance Hart Analog Input: Version = 8 <br>OCR1100 Controller: Version=8<br>High Performance Hart Analog Output: Version = 7 <br>OCR1100 Controller: Version = 7<br>Hart Devices connected to these modules are working fine and process points are updating as seen in the Point Information. But these Devices are not able to communicate with AMS 11.5. Please refer the attached snapshot.<br>Please note that these Devices were coomunicating properly with AMS 11.5 in 3.5_U5 build. But after doing Firware Download in 3.5_U7 the communication has stopped. Earlier Versions were: High Performance Hart Analog Input: Version = 6 <br>OCR1100 Controller: Version = 6<br>High Performance Hart Analog Output: Version = 6 <br>OCR1100 Controller: Version = 6 (Lal, Ramesh Aug 27, 2012) (Lal, Ramesh Aug 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 10/01/12:RL - Retested in 3.5_U9 with OCR400 and OCR1100 controllers. HART devices were able to communicate with AMS Device Manager 11.5. Hence, finding is closed. (Lal, Ramesh Oct 1, 2012) <br> |  | 35 | FINDING | 8782 |  | FINDING | [10 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73908
29903 | FINDING | ELC module does not communicate to controller after firmware download. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Following steps are performed :-<br>1. ELC1.2 software has been loaded in drop126 (WIN7-SP1,64 bit in Emily system)<br>2. New ELC module has been configured at 1.1.3 in drop40/90 (Emily system) <br>3. Firmware download to this module has been performed successfully <br> through controller diagnostic.<br>4. Reseated this module.<br>5. It is observed that now module is not communicating with controller.<br> Please refer the attached snapshot (ELC module_Error.jpg) for your reference (Sahay, Madhukar Aug 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected downloadable files. Please check in an OCR1100 and OCR400. (Pingree, Douglas K. Aug 28, 2012)<br><br>MS : Checked in U8 &amp; ELC1.2_U7 , this issue is fixed for OCR400, However incase of OCR1100 <br> diagnostic doesnot show all the files, I have entered a saperate F#8943 to track OCR1100 <br> issue. I am closing this finding. (Sahay, Madhukar Sep 20, 2012) <br> |  | 35 | FINDING | 8783 |  | FINDING | Plymire, Alvan AUTOSOL PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73910
29904 | FINDING | Trend is not working with multi trend on a same graphics. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I am created a graphics with trend and multi trend. In online graphics, trend is not working properly but multi trend is working properly and updating point values. <br>I have created graphics with only trend, In online graphics,trend is working properly. (Kumar, Sudheer Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please attach the graphic source file so that we can try to duplicate (McMaster, James Aug 31, 2012)<br><br><br>I am sending Graphics 011.src file with attachment for your reference . (Kumar, Sudheer Sep 3, 2012)<br><br>In the graphic that you sent the single trend has an interval of 1000 seconds. That means it updates every 1000 seconds. Is that what you mean to do? (McMaster, James Sep 3, 2012)<br><br>I was change the interval time is 60 sec after that both trend are working fine . (Kumar, Sudheer Sep 24, 2012) <br> |  | 35 | FINDING | 8784 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73912
29905 | FINDING | Multi trend points colors are not updated in the online graphics. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | I have created a graphics with multi trend ---&gt;select properties ---&gt;added more than one points and select different colors for different point. In online graphics shows only one color for every added points. (Kumar, Sudheer Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please attach the graphic source file so that we can try to duplicate. (McMaster, James Aug 31, 2012)<br><br>I am sending Graphics 011.src file with attachment for your reference (Kumar, Sudheer Sep 3, <br><br>Note there are 2 multitrends in this graphic, one is the size of a dot and below the other trend.<br>Is this what you intended. Also, the multitrend that is visible has an interval of 1000 seconds. When i change the interval to something smaller I see the blue and red trend lines (McMaster, James Sep 3, 2012)<br><br>I changed the interval time 60 sec and samples 10, after that run time graphics is not showing correct Colors .please refer to snapshot. (Kumar, Sudheer Sep 3, 2012) <br> Are the points you are trending &quot;OFF SCAN&quot;, if so the trend color will be cyan (default FG color for fair quality). Can you try to trend points that have good quality, the trend color for these points should follow the defined trend color. (Spillane, Donal A. Sep 4, 2012) |  | 35 | FINDING | 8785 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73914
29906 | FINDING | Cut and Paste operation is not working in Audit Viewer. | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0, open Ovation Audit Viewer. There,for a specific time period,search is done and details comes at AuditView window. Now any row from the details is selected--&gt;Edit. Here Cut operation is not working. There is no clipboard comes to Paste it as per Help file.<br>Please find the attached snapshot for reference. (Mitra, Sambuddha Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Cut and Paste operations/functions are not applicable when viewing Audit results and will be disabled. (Swartz, Mark E. Aug 28, 2012)<br><br>Verified in Ov.3.5.0_U8. The problem is solved. Hence closing the finding. (Mitra, Sambuddha Sep 18, 2012) <br> |  | 35 | FINDING | 8786 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73916
29907 | FINDING | SDR 18616 failed. The Online Ref_1100 is not updated for certain algorithms. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Note written in Online REF_1100 against SUM, MULTIPLY, SQUAREROOT and FUNCTION algorithms is &quot;The gain on the input should never be initialized to zero; if it is, the drop is placed into alarm. &quot;, while it must be updated in U7 build of Ovation 3.5.0 as per SDR 18616. (Goel, Chetna Aug 28, 2012) | LC 08/29/2012: Updated the SUM, MULTIPLY, SQUAREROOT, and FUNCTION algorithms so that there is no confusion on when a drop is placed in alarm. |  |  | LC 8/29/2012: Check the SUM, MULTIPLY, SQUAREROOT, and FUNCTION algorithms for removal of the note. Also check the Algorithm tables, the parameter dealing with gain on input. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 08/29/2012: Per manager in Product Development, the note was removed from the SUM, MULTIPLY, SQUAREROOT, and FUNCTION algorithms about the drop being placed in alarm. This should be available in U8 build. (Casteel, Linda Aug 29, 2012)<br><br>LC 08/29/2012: Update to above: the Gain parameter in algorithm table already says, &quot;The gain on the input should never be initialized to zero; if it is, the drop is placed into alarm.&quot; It is there for the SUM, MULTIPLY, SQUAREROOT, and FUNCTION algorithms. (Casteel, Linda Aug 29, 2012)<br><br>CHG 28 Feb 13: Found fixed in OVA350010 patch. Hence closed. (Goel, Chetna Feb 28, 2013) <br> |  | 35 | FINDING | 8787 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73918
29908 | FINDING | OCR400 processor type information is different in two places. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In Ovation 3.5.0, Controller Diagnostics is opened--&gt;Select any (or both primary/partner) controller drops(OCR400). Here in Controller Overview, Processor is shown &quot;PentiumPro&quot;, but in the Help file, &quot;Celeron&quot; processor is mentioned. Correct and same information should be given in both places.<br>Please find the two attachments for reference. (Mitra, Sambuddha Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed wording (Christy, Benjamin Sep 10, 2012)<br><br>Verified in Ov.3.5.0_U8. Now, correct and same information is showing in both places. The issue has been solved. Hence, closing the finding. (Mitra, Sambuddha Sep 18, 2012) <br> |  | 35 | FINDING | 8788 |  | FINDING | Spillane, Donal AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73920
29909 | FINDING | Fieldbus Statistics | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 11:21 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 11:21 |  |  |  | 2019-07-02 11:21 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | 1. Statistics shows empty dialog box when hse server is not running.<br>2. Lock row heights for all display grid.<br>3. Refresh grayout during automatic refresh.<br>4. Timer may not be accurate after character was input in edit box. (Shiferaw,Tedla Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1.Statistics now shows error dialog box if hsserver is not running<br>2.row heights is locked . Not allowed to change.<br>3.refresh is grayed out if auto refreshing is on.<br>4. time is accurate. (Shiferaw,Tedla Sep 25, 2012) <br> This was released in U9 (Costlow, Kimberly A. Oct 17, 2012) |  | 35 | FINDING | 8789 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | Pratley, Bob EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | Shiferaw, Tedla AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U7 |  |  | FINDING | [6 empty] | 143806
29910 | FINDING | Incomplete busmap in controller | Benzvi, Mati EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | When a valid busmap from the database is sent to the controller, only part of the file reaches the controller. The end is truncated (approx 80% of the file is there). The module cannot communicate. (Buzza, Sheri Aug 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed In Controller - Part of Copying files to back up. - (Hutchison, Steven B. Sep 4, 2012)<br><br>Can We Get this closed? (Hutchison, Steven B. Aug 30, 2013) <br> |  | 35 | FINDING | 8790 |  | FINDING | Buzza, Sheri AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Buzza, Sheri AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73924
29911 | FINDING | Scrollbar are function block tuning remains after resize. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | The tuning window is displayed for a function block.<br>When it is resized using the expand button to fill the developer studio window,<br>the old scrollbar remains. It is not functional and goes away with a refresh. (Buzza, Sheri Aug 28, 2012) |  |  |  | Open tuning dialog for a function block. Resize dialog using expand button. Verify scroll bars are handled correctly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Sep 5, 2012) <br> |  | 35 | FINDING | 8791 |  | FINDING | Buzza, Sheri AUTOSOL PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Buzza, Sheri AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73926
29913 | FINDING | Export documents from the Print preview of OSV doesnot show watermarks for formats other than pdf. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | OSV-&gt; Print Preview -&gt;Toolbar -&gt; Watermark. When Text Watermark/ Picture watermark are applied and the transperancy is set high so that the visibility of preview document is good.<br><br>Now export the document :<br>1&gt; to pdf format, the pdf document is seen with the watermark overlaped on the preview report. <br>2&gt; to html format, watermark doesnot exists.<br>3&gt; to MHT format, watermark doesnot exists.<br>4&gt; to RTF format, watermark doesnot exists. <br>5&gt; to XLSX format, watermark doesnot exists.<br>6&gt; to CSV format, watermark doesnot exists.<br>7&gt; to TXT format, watermark doesnot exists.<br>8&gt; to JPG format, watermark doesnot exists. (Sachan, Pallavi Aug 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | If you run the same tests on Point Information, you will see the same thing.<br>This is the way it works. I have no plans on fixing this. (Wozniak, Diane M. Aug 29, 2012)<br><br>Closed as per developer&quot;s comments above. (Sachan, Pallavi Aug 29, 2012) <br> |  | 35 | FINDING | 8793 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73930
29914 | FINDING | In OSV, General attributes for SIS shows many details which are not easy to understand. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | In OSV, General attributes for SIS shows many details which are not easy to understand like mentioned below:<br>1&gt; Under SDS: (a) Ovation Point name key, (b) Revision number<br>2&gt; Under SLS: (a) Type:5359 Undefined, there are many such Types which refer to Non-Secure Parameters. <br>3&gt; Under SIS IO Channel: (a) CRC for individual I/O channel, (b) Type:5482 Undefined, etc...<br>4&gt; Under Control Modules: (a) Ovation Point name key, (b) Candidate Module Rev<br>where as for <br>5&gt; SIS Secure Parameters: all the features shown in OSV are same as seen in Studio. (Sachan, Pallavi Aug 29, 2012) |  |  |  | Please check the sis grid displays against the Ovation developer&quot;s Studio. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please send a screen capture. (Costlow, Kimberly A. Aug 29, 2012)<br><br>Kindly find XMLfiles-SIS.zip for xml files of Drop23/73 and SIS-details.zip for screen captures. (Sachan, Pallavi Aug 29, 2012)<br><br>please check the new grid displays with the Ovation Developer&quot;s Studio. Things should be much better. (Wozniak, Diane M. Sep 10, 2012)<br><br>This should be fixed in the Nov 1 patch. (Wozniak, Diane M. Oct 29, 2012) <br> msb - Closed: converted to SDR 19221 (Benzvi, Mati Oct 31, 2012) |  | 35 | FINDING | 8794 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73932
29915 | FINDING | Import SIS sheet to logic solver could not be performed and cause error inconsistently. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | Performed steps are:<br>1. Export SIS sheet from a logic solver [SLS01] to directory say D:\XYZ.<br>2. Import SIS sheet from D:\XYZ to SLS02/SLS01. During import operation&quot;Unable to get SheetDb Record&quot; error appeared. For reference screenshot &quot;SIS sheet Import operation error.jpg&quot;.<br>3. After Import operaton, in studio imported sheet are without name and number. Refer &quot;SIS SHEET IMPORT ERROR-Stdio.jpg&quot; Screenshot (Pandey, Vijay Aug 29, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Control Builder - Unified (CBU)</p> <p><strong>Subproduct:</strong> Safety Instrumented System (SIS)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Hutchison, Steven B. Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2012-08-29T08:20:01-04:00</p> <p><strong>Modified Date:</strong> 2012-08-29T08:20:01-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8795 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73933
29916 | FINDING | In 3.5_CONTROLLER_SVTP_rev5.1_SK.docx some tests are not Applicable and needs modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In 3.5_CONTROLLER_SVTP_rev5.1_SK.docx following tests are not Applicable:<br>1)5.21.1[ b,c,d] ,5.21.4 [a,b,c] and 5.21.7 [a,b,c]refers to Ovation Ethernet IO which can be modified to Ethernet Remote Interface which is applicable for NumaLogic only in Ov3.5.0.<br><br>2)5.21.1 (d),5.21.2(d),5.21.4 [c,j] and 5.21.7 (h) has test of 100 Mbps Auto Negotiate but in drop down selection option available is of auto-negotiate only. <br><br>3)5.21.3 (g) can be marked as N/A since On removing N2 cable controller goes off highway but in test its written to check the drop fault.<br><br>4)5.24.6 test for deluxe point can be marked as N/A.Input and Output point referred in this test can also be removed. <br><br>5)5.21.4 (k,l)N2 can be replaced with N3 (Kumar, Shailendra Sep 6, 2012) (Kumar, Shailendra Sep 12, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Kumar, Shailendra</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Kumar, Shailendra</p> <p><strong>Entry Date:</strong> 2012-08-29T09:10:35-04:00</p> <p><strong>Modified Date:</strong> 2012-09-12T06:34:42-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8796 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73934
29918 | FINDING | All the Virtual controllers failed after changing one snapshot to another in Simcontrol. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1.Open Dvp.studio-&gt;Goto Configuration-&gt;Click &quot;Simulation Drop Config&quot;-&gt;Mention all virtual controller&amp; Host names in &quot;drops.cfg&quot; file.<br>2.Configure simulation logic using &quot;2Xselect&quot; algo as shown in attached snapshot(Simcontrol.JPEG)<br>3.Open &quot;Simcontrol.exe&quot; from C:\Ovation\OvationBase\Simcontrol.exe<br>4.Give the value to 2Xselect algo (Eg:Mode-4,Trasmitter-A-50,Trasmitter-B-70) Freeze the control &amp; save the snapshot.<br>5.Take another snapshot with mode value:5 &amp; save. Run the Simcontrol.<br>6.Now Freeze the Simcontrol and change the previous snapshot(Eg:Mode-4,Trasmitter-A-50,Trasmitter-B-70).and RUN the simcontrol.<br>7.Observe the control more than 5min,It will fail all the Virtual controller drops.<br>8.The fail may occur after 5minites.<br>9.After rebooting the VC&quot;s getting online.<br><br>I have done the Experiment in VCH drop.<br>Please refer the attached Ovationerrorlog &amp; Simcontrol-Log. (K, SendhilKumar Aug 29, 2012) (K, SendhilKumar Aug 30, 2012) |  |  |  | Save a simulator snapshot and reload. Ensure virtual controller stays functional. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem corrected in simulator save routine (localmem). (Perdeus, Matthew Sep 17, 2012) <br> |  | 35 | FINDING | 8798 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73938
29919 | FINDING | PWSIT - Unable to see FF devices on non-DBS drops in AMS Device Manager | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 09:05 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 09:05 |  |  |  | 2019-07-02 09:05 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Fix on finding 8716 doesn&quot;t fix this issue.<br><br>When configure Ovation network on AMS DM from a non-DBS drop, AMS DM unable to see any live device from Fieldbus segments.<br><br>When configure network on DBS drop, AMS was able to see live Fieldbus devices.<br><br>Attemp to use the fix on Finding # 8716 doesn&quot;t solve the problem.<br><br>Steps to reproduce:<br>Terminate all AMS service on all drops<br>Delete existing Ovation network configured on DBS if present.<br>From a non-DBS drop (this included drop with AMS Server Plus installed), run the AMS Network Configuration and configure an Ovation Network.<br>When done, start AMS, perform rebuild heiarchy on Ovation network<br>Browse to Fieldbus segment and try to identify a device<br>Warning message will state &quot;No device found at xxxxx&quot; (see screenshot attached) (Phan, Quang Aug 29, 2012)<br><br>Still see issue after upgrade to Ovation 3.5 build U7 with AMS 12.0 Build 466 (Phan, Quang Aug 30, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8799 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Pratley, Bob EMR SYSS PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  | Follow the &quot;note&quot; at the beginning of Section 6 &quot;Installing and configuring AMS Device Manager software&quot; of OW350_30 &quot;Foundation Fieldbus User Guide for Ovation 3.5&quot; recommending the execution of InstallHSEServer.bat. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U7 |  |  | FINDING | [6 empty] | 143789
29920 | FINDING | PWSIT - Discripancy on Rosemount 644 R1 AI Function block |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Rosemount 644 R1 device is commissioned in Ovation. 2 AI function block is available from device. Device show in AMS with good status and no error.<br><br>Issue 1:<br>When try to tunne these function blocks using Tunning option, permitted mode on these block are different:<br>1st block shows OOS as only option<br>While other block shows 3 different modes user can select from<br><br>Issue 2:<br>In Tunning windows, these block shows actual mode as OOS for both while in Signal Diagram it show one in Local mode and other as Unknown mode.<br><br>See attached screenshots for detail (Phan, Quang Aug 29, 2012) | Validated using 3.5 build U9. All 3 permitted modes (Auto, Manual, OOS) are available in FFAI tuning. Was able to place FFAI in Auto mode. Check Signal Diagram and verified block is in good status with correct value compare to device in AMS UI. |  |  | Please retest; verifying correct mode handling in tuning box. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Oct 17, 2012) <br> |  | 35 | FINDING | 8800 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73941
29921 | FINDING | Redundant Drops did not have all of the fieldbus information updated. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Changes made to the drop in control were not updated in the partner on a load for the <br>fieldbus ports.<br>Information for the port on the control drop did not exist for the port in the partner drop. (Buzza, Sheri Aug 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed In Controller - Porting Issue. - (Hutchison, Steven B. Sep 4, 2012) <br> |  | 35 | FINDING | 8801 |  | FINDING | Buzza, Sheri AUTOSOL PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Buzza, Sheri AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73943
29922 | FINDING | PWSIT - Failure to change fieldbus function block tag description |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Error message occurred when attemp to change Tag Description on fieldbus function block (AI in this case) in Tunning window. (See attached for error screenshot).<br><br>Devices tested: (all AI blocks)<br>Rosemount 3244 Rev 3<br>Rosemount 644 Rev 1<br>Rosemount 848T Rev 5<br><br>Steps to reproduce:<br>In Developer Studio, right click on an AI function block and select Tuning<br>Place block in OOS <br>Make change to Tag Description<br>Click Commit (Phan, Quang Aug 29, 2012) | Validated using 3.5 build U9. Was able to place device OOS and made change to Tag Description. Process went thru without error. Place block back in service. Tag Description retain. |  |  | Steps to reproduce: In Developer Studio, right click on an AI function block and select Tuning Place block in OOS Make change to Tag Description Click Commit | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Sep 5, 2012) <br> |  | 35 | FINDING | 8802 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73945
29923 | FINDING | When the graph line is very close to vertical, mouse hover window does not always pop-up. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | When the graph line is very close to vertical point value, mouse hover window does not always pop-up.<br>When graph line is horizontal straight line moving cursor on this line always shows hover window but if graph line is zig zag and graph lines are close, mouse hover window does not always pop-up.<br>Shown this to Prashant. (Kumar, Shailendra Aug 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19204 (Benzvi, Mati Oct 29, 2012) <br> |  | 35 | FINDING | 8803 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73947
29924 | FINDING | Test case 5.1.4/c & 5.1.10/c, in SVTP "3.5_SDR18728_SVTP_rev1.5_PP.doc"need to modify. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In Test case 5.1.4/c, in SVTP &quot;3.5_SDR18728_SVTP_rev1.5_PP.doc &quot;, there should be removed colon (:) between ¿settings &amp; System¿ from command line of ¿review /settings: System file name.rvt¿. <br>Same modification also for Test case 5.1.10/c, between ¿f &amp; System¿ from command line of ¿request_alarm_list ¿f: System: filename.alm¿<br>Hence the SVTP should modify accordingly. (Prasad, Parmatma Aug 30, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN OpCon (WOP)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Prasad, Parmatma</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Prasad, Parmatma</p> <p><strong>Entry Date:</strong> 2012-08-30T00:24:39-04:00</p> <p><strong>Modified Date:</strong> 2012-08-30T00:24:39-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8804 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73948
29926 | FINDING | Default value of "Maximum Password Age" needs to be changed | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Under [Manage Ovation Security --&gt; Manage Domain Policies --&gt; Default Domain Policies --&gt; Password Policies] there is an option &quot;Maximum Password Age&quot;. By default its State is set as &quot;Passwords Do Not Expire&quot;. When the user change this State to &quot;Enabled&quot;, the &quot;Value&quot; field shows &quot;-1&quot; as the entry. However, -1 days is not relistic because the rule says that Value can be between 0 to 999 days. <br>So this default value needs to be changed to something else, preferrably &quot;0&quot;.<br>Please refer the attached snapshot file. (Gupta, Chandresh Aug 30, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | When user is changing state to enabled they can also set the number of days in the same screen. This will not be changed at this time. (Burgoon, Frank J. Oct 1, 2012)<br><br>cg (10/03/12) - Developer mentioned that &quot;This will not be changed at this time&quot;. So I believe this issue will be fixed in future Ovation release &amp; I feel that it could be fixed. Hence this finding could be marked as SDR to track for future Ovation release. Presently, I am changing the Action field to &quot;DRR&quot;. Thanks!! (Gupta, Chandresh Oct 3, 2012)<br><br>IC 10/26/12 - closing as WIW (No plan to fix). Dev always has discretion to fix this iin the future if they chosse to. (Capani, Nooch Oct 26, 2012) <br> |  | 35 | FINDING | 8806 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73952
29927 | FINDING | Default values of [Domain - Password] need to be changed in TR "3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc" | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | In TR &quot;3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc&quot; test case 5.7.2 &quot;Domain - Password&quot; the default values of the following needs to be changed:<br>1. Maximum Password Age : from [Enabled=42] to [Passwords Do Not Expire]<br>2. Minimum Password Length : from [Enabled=0] to [Enabled=7]<br>3. Password must meet complexity requirements : from [Disabled] to [Enabled] (Gupta, Chandresh Aug 30, 2012) (Gupta, Chandresh Sep 14, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Securtiy (WSEC)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-08-30T05:59:11-04:00</p> <p><strong>Modified Date:</strong> 2012-09-14T01:30:13-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8807 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73953
29928 | FINDING | Backup VxSim Virtual Controller goes off highway and comes back few times after failover is done. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Redundant VxSim Virtual Controller are configured on 3.5 WALT system (Primary-Drop144, Partner-Drop147). When Failover is performed it is observed that the VC which is in backup mode fluctuates between white , gray and yellow state as seen in the SSD graphics for sometimes.<br>In general, it is observed that Virtual Controllers go off highway occasionally, if observed for prolonged time. (Lal, Ramesh Aug 30, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This appears to be related to finding 8866. If agreed, please close this finding. (Perdeus, Matthew Oct 26, 2012)<br><br>3/01/2013: RL - Monitored redundant Virtual Controllers operation on VCH Drop182 on Net#8 in IEC. On this machine avp.exe is consuming ~5% CPU time. The failover to backup VC takes place as desired and backup VC doesn&quot;t go off highway.Hence finding is closed. (Lal, Ramesh Jan 3, 2013) <br> |  | 35 | FINDING | 8808 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73955
29929 | FINDING | Advanced Virtual Controller License not mentioned in the Ovation License Manager | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 | [7 empty] | USPITTFSService | 2015-06-12 04:03 |  | As per the SVTP-3.5_VxSIM_VC_SVTPRev2.0_SKK,Testcase-5.6<br><br>Step:-5.6.3 Test: Licensing Updates:<br><br>a) The Ovation License Manager will need to support the additional drop type of Advanced Virtual Controller. Software Licensing will need to have the capability to enter this drop type into the license. All associated licensing forms will need to be updated to include this new drop type Get the license for Advanced Virtual Controller from Software Licensing and verify that it works fine.<br><br>But,Advanced Virtual Controller License not mentioned in the Ovation License Manager.<br><br>we have option to add Advanced Virtual Controller in Developer studio(refer snapshot)after all configuration we could not Download the drop it&quot;s thru error message. (K, SendhilKumar Aug 31, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Virtual Controller (OVC)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> K, SendhilKumar</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Perdeus, Matthew K, SendhilKumar</p> <p><strong>Entry Date:</strong> 2012-08-31T02:01:25-04:00</p> <p><strong>Modified Date:</strong> 2012-10-12T16:30:09-04:00</p> | 0 |  | Ovation for Windows/General/Software | RWB: This is not a Virtual Controller issue. (Boehmer, Robert W. Oct 12, 2012) <br> |  | 35 | FINDING | 8809 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | Perdeus, Matthew AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73956
29930 | FINDING | There is no action taken place on Click the left mouse button over the button if trigger function used. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:03 | [11 empty] | USPITTFSService | 2015-06-12 04:03 |  |  |  | 2015-06-12 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:03 |  | Step to reproduce:<br>1. Open the Ovation developer Studio (OVA3.5.0_U7).<br>2. Go to process diagram config. Window through (drop 232-&gt;configuration-&gt;process diagrams-&gt;process diagram config. window) the path.<br>3. Check the radio button of Execute Action On release is false on process diagram config. Window.<br>4. Trigger function used in button on GBNT.<br>5. Downloaded the drop232 &amp; restarted the graphics.<br>6. Open graphics window but no actions taken place for click the left mouse button over the Button.<br>Note: - I have checked above behavior for OL button, OL choice &amp; OL checkbox. (Prasad, Parmatma Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This action is correct. SRF 1652 required us to change the action of the pokes and buttons that executed on the depression of the left mouse button, OL buttons with trigger functionality were not one of these. OL buttons triggers have always worked on the release of the mouse button and therefore no change was required. (Spillane, Donal A. Sep 4, 2012)<br>Closed as per developer&quot;s comments above. (Prasad, Parmatma Sep 10, 2012) <br> |  | 35 | FINDING | 8810 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73958
29931 | FINDING | There is no action taken place on Click the left mouse button over the Poke-8. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Step to reproduce:<br>1. Open the Ovation developer Studio (OVA3.5.0_U7).<br>2. Go to process diagram config. Window through (drop 232-&gt;configuration-&gt;process diagrams-&gt;process diagram config. window) the path.<br>3. Check the radio button of Execute Action On release is false on process diagram config. Window.<br>4. Poke-8 used in GBNT.<br>5. Downloaded the drop232 &amp; restarted the graphics.<br>6. Open graphics window but no actions taken place for click the left mouse button over the Poke-8. (Prasad, Parmatma Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This action is correct. SRF 1652 required us to change the action of the pokes that executed on the depression of the left mouse button, poke type 8 was not one of these. Poke type 8 has always worked on the release of the mouse button and therefore no change was required. (Spillane, Donal A. Sep 4, 2012)<br>Closed as per developer&quot;s comments above. (Prasad, Parmatma Sep 10, 2012) <br> |  | 35 | FINDING | 8811 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73960
29932 | FINDING | GBNT crashes eveeytime in a drop & other drops occasionally. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | While working in the drop #203 in net8 of 3.5.0 workstation, GBNT crashes everytime with meter selected. This system is of OS Window 7 with 32 bit. While I observed in other workstations with 32 bit, it happens occasionally with Meter, Bmp Image and also with OL slider. Please find enclosed is the snapshot. (N, Thamaraiselvi Aug 31, 2012).<br><br>Aso observed the OnLine graphics containing Meter, Bmp Image and also with OL slider crashes, after changing the conditions of color everytime while opening on both 32 bit &amp; 64 bit window 7 systems. (N, Thamaraiselvi Sep 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please provide details as to what you were doing in GBNT prior to the crash. For instance, did you select a meter and then do a Properties functions on it and then GBNT crashed, or did you select a meter and then press OK/Apply on the meter dialog to apply changes to the meter and then GBNT crashed, or did GBNT crash after just selecting the meter and doing nothing to it? Also, the snapshot image you sent showed a BUTTON selected and the GBNT:Button dialog, so is the problem specific to the meter or the button or the bmp_image or the ol_slider - or all of these items? Note that the bmp_image item does not have color or color conditionals associated with it, so I don&quot;t understand what you mean when you say GBNT crashes every time you change the color on a bmp_image. <br><br>Please provide exact details of the steps you take to make GBNT crash AND also provide the graphic .src file (and the .src files for any macros used on the graphic), for the graphic which causes GBNT to crash. (Johnson, Kathy Sep 10, 2012) <br> I was doing test cases of Enhanced Entry field, Meter, Bmp_Image &amp; OlSlider all drawn in a single sheet in the drop #203 of OS having Win 7 with 32 bit. It was working fine, both with GBNT &amp; graphics.<br>The GbNT started crashing after I selected the meter, right clicked,selected drawing attributes and filled with color, filled pattern in it. I did download &amp; load the drop.Also restarted the drop.But the GBNT crashes everytime whenever I open the particular sheet and not with any of the application properties selected. And then I created a new sheet with meter. After pasting the meter, the new sheet also crashes without properties selected.Then I observed drawing Meter, BMp_Image, &amp; then OL_Slider in other 32 bit OS Machines which does crash occasionally.<br>The gbnt crashing snapshot is one of the snapshot I took doing testing cases.<br>I am sorry that Iam on medical leave, &amp; so the delay in providing the appropriate info.<br>I will send all the snapshots on Monday when I go to Office.<br><br> The crashing of graphics I observed after changing the color conditions of button which I also observed in other drop #234 of 62 bit. <br>Please find attached the zip files of src files of drop #203 of 32 bit.<br>Hope I answered your questions. Please revert me for furhur clarification. (N, Thamaraiselvi Sep 13, 2012)<br><br>I am sorry for the late info, as I didn&quot;t come to Office on Monday &amp; came today only.<br>Observed about the findings of both GBNT &amp; Graphics of the above said drops. Seems it is resolved with the installation of U_8. Still I will observe more &amp; then close the finding. (N, Thamaraiselvi Sep 20, 2012) (N, Thamaraiselvi Sep 20, 2012).<br><br>After the observation, found out that the finding is resolved.Now no more crashing happens in any of the drop with the meter, Bmp_image &amp; OL_slider as well. (N, Thamaraiselvi Sep 28, 2012) |  | 35 | FINDING | 8812 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73962
29933 | FINDING | In distributor algo FPEA is ON with FPEX set to 0x05 to exclude the OUT pins 1 and 3 are not working | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following steps were performed in ctrl 32/82 <br><br>Connected the input and three outputs in distributor algo set the FPEA ON and set the FPEX to 0x05 , but it is observed that Out pins 1 and 3 are not excluded.<br><br>Attached the logic sheet and snap shot of signal diagram (Jayarajan, Jayakumari Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | FPEA parameter is used only during FIRST_PASS_STARTUP - when algorithm is added to the sheet or after restart both controllers. This parameter defines that XSEL pin will be ON or OFF after first pass startup (thi parameter defines initial state).<br>Please repeat test.<br>1. Create the new sheet with distributor algorithm and set in control builder FPEA ON and set FPEX to 0x05. Then load the sheet and check that out 1 and 3 are excluded.<br>2. For the same settings Restart both controllers and check that out 1 and 3 are excluded. (Plamowski, Sebastian Sep 11, 2012)<br><br>JJ(14Sep2012)<br><br>Vwerified by restarting the ctrls. but in point information it was difficult to observe.<br>So I put the o/p of out1 and out2 pins in trend and observed during the startup tere was an exclusion that is for approximately.<br><br>So the status of finding is changing to close. (Jayarajan, Jayakumari Sep 13, 2012) <br> |  | 35 | FINDING | 8813 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73964
29934 | FINDING | FPPA (PSEL is ON/OFF )for distributor algo is not working | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Attached the logic sheet and snapshot of signal diagram (Jayarajan, Jayakumari Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | FPPA parameter is used only during FIRST_PASS_STARTUP - when algorithm is added to the sheet or after restart both controllers. This parameter defines that PSEL pin will be ON or OFF after first pass startup (this parameter defines initial state).<br>Please repeat test.<br>1. Create the new sheet with distributor algorithm and set in control builder FPPA ON and set PSEL to 0x05. Then load the sheet and check that out 1 and 3 are set as priority.<br>2. For the same settings Restart both controllers and check that out 1 and 3 are excluded. (Plamowski, Sebastian Sep 11, 2012)<br><br><br>JJ(14Sep2012)<br><br>Verified by restarting the ctrls. <br>So the status of finding is changing to close. (Jayarajan, Jayakumari Sep 13, 2012) <br> |  | 35 | FINDING | 8814 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73966
29935 | FINDING | Need to update page "To add a new Ovation Virtual Controller" | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It is clear from the screen shot (In correct controller type.jpg) that In description field of Controller Type that OCT161 is one of the option of controller type but OV 3.5.0 does not support it &amp; that option is unavaliable in Developer studio. As shown in screen shots (OCR 161 unavaliable.jpg)<br><br>All screen shots are attached. (Agarwal, Gaurav Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Thanks Gaurav. I added a new screen shot for the Virtual Controller manual (3.5 release). (Skena, Ronald E Oct 24, 2012) <br> |  | 35 | FINDING | 8815 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73968
29936 | FINDING | Set start time and End Time not wroking properly. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Steps are performed:<br>Historical Review open.Click on set time button.<br>1.Change default start time and end time. Refer Screenshot &quot;hist rev set time1.jpg&quot;. Click [OK], desire result not obtained, in result start time and end time same. Refer screenshot&quot;hist rev set time1-1.jpg&quot;.<br>2. Change default start time and end time. Refer Screenshot &quot;hist rev set time2.jpg&quot;. Click [Begin], desire result btained, in result start time and end time are appeared as they configured. Refer screenshot&quot;hist rev set time2-2.jpg&quot;. (Pandey, Vijay Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. Will be available in next build. (Matreja Shyam Aug 31, 2012)<br>VP-09/28- Retested with 3.5.0_U9, found fixed. Hence, finding is closed. (Pandey, Vijay Sep 28, 2012) <br> |  | 35 | FINDING | 8816 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73970
29937 | FINDING | Description of "Simulator Driver Type" is not correct on "To set Ovation device number parameters" page. | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Description of &quot;Simulator Driver Type&quot; is not correct on &quot;To set Ovation device number parameters&quot; page.<br><br>For more details please find the attached screen shots &quot;Incorrect description.jpg&quot; (Agarwal, Gaurav Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The description for the Simulator Driver Type will be corrected for the 3.5 Ovation release. The Affected manuals are OW350_54, OW350_57, and OW350_58. The description for the Simulator Driver Type is shown below:<br><br>Selects the Simulator Driver for the selected device.<br>Fake<br>Ovation<br>For SimControllers and Virtual Controllers, this should be set to Ovation. (Skena, Ronald E Sep 12, 2012) (Skena, Ronald E Sep 9, 2013) <br> |  | 35 | FINDING | 8817 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73972
29938 | FINDING | Help file is not openning in "New custom Networking Interface, New point processing etc." windows. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | 1:- Open the Developer studio.<br>2:- GO to following path &amp; Press right click.<br>System&gt;Network&gt;Unit&gt;Drop&gt;Point Processing<br><br>3:- New point processing window is opened.<br>4:- Press the help button. Following message is appearing.<br><br>&quot;[OvPtApi]: (No such object)&quot;<br>Note:- Same issue observed with &quot; New custom networking Interface, New sim controller&quot; windows.<br>For more information please find the attach screenshot &quot;Help file not openning .jpg&quot; (Agarwal, Gaurav Aug 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 09/05/2012: This is a known problem in the Developer Studio. The Help buttons on the windows that are marked as &quot;New&quot; do not work. Product Development is aware of the problem, but cannot fix it at this time. (Casteel, Linda Sep 5, 2012)<br><br>As per developer comment, finding is closed. (Agarwal, Gaurav Oct 17, 2012) <br> |  | 35 | FINDING | 8818 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [7 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73974
29939 | FINDING | VC fails to send error messages to Server when multiple remote SHC (networks) are configured | Perdeus, Matthew AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | VC fails to send error messages to designated Server when multiple remote SHC (networks)<br>are configured to start.<br>Emily-Drop145 is configured with 11 external Networks connections and Send messages to drop125.<br>When the drop starts only 3 [Init_SHC : Initializing SHC #] are reported in drop125 Error log.<br>and on drop145 printErrorBuffer shows:<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 0<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 1<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 2<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 3<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 4<br>FRI AUG 31 17:00:33 2012 : failed sending error to host: drop125: S_errno_EHOSTUNREACH<br>FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC 5 (Benzvi, Mati Aug 31, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Virtual Controller (OVC)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Perdeus, Matthew</p> <p><strong>Notify List:</strong> Perdeus, Matthew Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2012-08-31T16:12:16-04:00</p> <p><strong>Modified Date:</strong> 2012-10-29T10:17:45-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8819 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73975
29940 | FINDING | implicit Consistency check is required on each controller when more than 31 Remote networks are defined. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | If a network is configured with more than 31 Remote networks and a controller has no<br>[External Networks Connections - External Networks] defined, the controller will atempt<br>to start as many SHCs as the number of ENCs on the network:<br> FRI AUG 31 17:00:33 2012 : &lt;134&gt; Init_SHC : Initializing SHC #<br>The current consistency check on the controller checks the number of defined ENCs only if <br>the controller has a [device: I/O Device # ExternalOvationNetwork] defined. (Explicit Check).<br>The Consistency Check should also do an implicit check, when no ENCs are not defined at all, <br>to verify that the controller does not exceed the 31 SHCs limit.<br>to avoid error:<br> Local Memory Manager : Error allocating local memory : errno = 0xc (0x1) (Benzvi, Mati Aug 31, 2012) |  |  |  | The consistency check functionality of the Ovation Developer Studio has been affected. The Ovation developer Studio performs a consistency check to prevent this situation. However, the check was only performed when the External Ovation IO Device was added to the drop under the [I/O Devices] location. The Studio had been updated to always perform this consistency check, even when the External Ovation I/O Device is not configured. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Ovation developer Studio performs a consistency check to prevent this situation. However, the check was only performed when the External Ovation IO Device was added to the drop under the [I/O Devices] location. The Stusio will be updated to always perform this consistency check, even when the External Ovation I/O Device is not configured. (Augustine, Lisa Sep 7, 2012)<br>---<br>msb - OK in Ov-3.5.0_U8 @ 18-Sep-2012<br> 2 Controllers with no External networks displayed error on Download after the upgrade to U8 (Benzvi, Mati Sep 18, 2012) <br> |  | 35 | FINDING | 8820 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73977
29941 | FINDING | VC Displays Fatal error when configured with more than 18 [External Network Connections] | Perdeus, Matthew AUTOSOL PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | VC Displays Fatal error when configured with more than 18 [External Network Connections]:<br>Drop145 (Emily Network - VCH drop127 - W7(32b)) when configured with 18,19 or 20 <br>Remote networks: Comes up OK with 18 <br>and displays &quot;fatal kernel task-level exception&quot; error when configured with 19 External Networks.<br>-----<br>PrintErrorBuffer of VC drop145 with 18,19 &amp; 20 ENCs is attached (Benzvi, Mati Sep 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | How many can be configured without failure in a hardware controller? (Perdeus, Matthew Oct 29, 2012)<br>---<br>msb - As stated in the Description: Remote networks: Comes up OK with 18 (Benzvi, Mati Oct 29, 2012)<br><br>The previous query was for a hardware controller (not a virtual). How many can be configured in a hardware controller without error? (Perdeus, Matthew Oct 31, 2012) <br> |  | 35 | FINDING | 8821 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73979
29942 | FINDING | The Historical Ascii Review drop selection request filter is not functional and entries in the drop column are blank | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In the Historical Ascii Review tab, the entries in the drop column are blank.<br>Also, if a user opts to filter by drop, the filter does not function in accordance with the actual result. (Khanna, Anant Sep 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8822 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73981
29944 | FINDING | DRPI1A Algo Help button is not linked correctly | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:26 | [11 empty] | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:26 | 3.6.0_U1 |  |  | 2017-06-15 04:26 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | If a user right clicks on the &quot;DRPI1A&quot; algorithm and selects the &quot;help&quot; option, the previously opened algorithm&quot;s help is opened instead of DRPI1A algorithm help. The button&quot;s linking is incorrect. (Khanna, Anant Sep 3, 2012) | <p>AA 12/01/2015: The particular finding was fixed by Linda. </p> |  |  | <p>LC 11/22/2013: See if the online help for the DRPI1A algorithm accesses the proper help.</p><p>AA 12/01/2015: The issue related to the&nbsp;DRPI1A algorithm has been resolved by Linda. The same will be visible in the latest online help.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>LC 11/22/2013: Added a new help ID for the DRPI1A algorithm. Should bring up the correct online help now. This fix will be available in the Ovation 3.5.1 U3 build and in OW351_R1100.pdf on Q:\Communication\Tech\Comm\Share\Validation. (Casteel, Linda Nov 22, 2013) </p><p>AA 12/01/2015: The issue related to the&nbsp;DRPI1A algorithm has been resolved by Linda. The latest updated manual is kept at: Q:\Communication\TechComm\Share\Abhinav_Ovation 3.6.0 manuals\Ovation Algorithms Reference Manual (OW360_R1100). This is visible in 3.6.0_U1 build.</p><p><br></p> |  | 35 | FINDING | 8824 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Bush, Kirt T EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | USPITTFSService | Validation |  | <p>LC 11/22/2013: Fixed a problem with access the online help for the DRPI1A algorithm.</p><p>AA 12/01/2015: The issue related to the DRPI1A algorithm has been resolved by Linda. Hence, closing the finding.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 114323
29945 | FINDING | Toolbar is not working in Sensor Calibration. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ov.3.5.0, open Sensor Calibrate--&gt;go to View at menu--&gt;click on Toolbar. Here Toolbar is not doing any function.<br>Please see the attached snapshot for reference. (Mitra, Sambuddha Sep 3, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | No plans to change to remove the Toolbar choice. There is no toolbar so this is a cosmetic problem not a loss of any functionality. This has been like this since beginning. (McMaster, James Sep 17, 2012)<br><br>Understand this,hence closing the finding. (Mitra, Sambuddha Sep 18, 2012) <br> |  | 35 | FINDING | 8825 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73987
29946 | FINDING | SVTP-3.5_SRF1630_SVTP_rev1.1_SKK-SVTP need to be modified | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | SVTP-3.5_SRF1630_SVTP_rev1.1_SKK,Testcase-5.1,<br>Step-5.1.1<br>Verify the availability of Snapshot files it can be found in Ovation VCH/Simulator drop at location C:\Ovation\dropxxx\dpu\sim.<br>The path Specified for &quot;sim&quot; folder need to be modified as C:\Ovation\dropxxx\ata0\wdpf\dpu\sim. (K, SendhilKumar Sep 3, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Virtual Controller Emulation (VCE)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> K, SendhilKumar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch K, SendhilKumar</p> <p><strong>Entry Date:</strong> 2012-09-03T06:33:42-04:00</p> <p><strong>Modified Date:</strong> 2012-09-03T06:33:42-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8826 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73988
29948 | FINDING | Ovation does not show any error when wrong Ethers Address is given in the Developer Studio. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following procedures done:<br>a)Open Controller Diagnostics--&gt;Select controller DROP13--&gt;Note down the Ethernet Address (MAC ID) of it.<br>b)Open Ovation System Viewer--&gt;Select DROP13--&gt;Note down the MAC Address of it.<br>For the above a) &amp; b) procedure, MAC address of DROP13 is found same:00:20:AB:39:01:AA.<br>Now c)Open Ovation Developer Studio--&gt;Select and open DROP13--&gt;Change the Ovation Network Ethers Address to 00:00:00:00:00:00--&gt;Apply and Ok--&gt;Download DROP13--&gt;Load DROP13.<br><br>In the procedure c), No error is shown as wrong MAC address has been given. Even the controller successfully downloaded and loaded in spite of giving wrong MAC ID. The controller is functioning fine. Now in Ovation System Viewer, MAC address of DROP13 shows 00:00:00:00:00:00 which is wrong. Only Controller Diagnostics shows the correct MAC ID.<br><br>Please find the attached snapshots for reference. (Mitra, Sambuddha Sep 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This works per design. The user is responsible for entering the correct MAC address. (Swartz, Mark E. Sep 4, 2012)<br><br>Understand this. So, closing the finding. (Mitra, Sambuddha Sep 5, 2012) <br> |  | 35 | FINDING | 8828 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73992
29949 | FINDING | Error message during "Override Default Unit" needs to be modified | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | While testing &quot;Override Default Unit&quot; security configuration, if this configuration is Disabled &amp; when we access points of any UNIT other than the default then an error message pops-up. In this message the first word needs to be modified to &quot;Unable&quot; instead of &quot;Unabled&quot;. Please see the attached snapshot file Override-Default-Unit-message.jpg. (Gupta, Chandresh Sep 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Change to SDR. (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19113 @ 08-Oct-2012 (Benzvi, Mati Oct 8, 2012) <br> |  | 35 | FINDING | 8829 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73994
29950 | FINDING | Point Filter buttons on the common tab of Historical Review open outside the screen window | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In the common tab of Historical Review, once a user clicks on the point filter option present in the &quot;Operator Event&quot; or &quot;SOE&quot; column, the point filter window opens outside the screen window, User is not able to access the buttons(OK/CANCEL/BROWSE) and hence cannot filter by point name for Operator Event and SOE. (Khanna, Anant Sep 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please demonstrate or provide a screen image capture of the problem. (Contento, James L. Sep 4, 2012)<br><br>(ANK- Sep 5, 2012)- The buttons which i am referring to are circled in red. (Refer to 1.jpg)<br>On pressing the button, the window partially opens outside the screen and a user is not able to set a point filter as the buttons are not visible on the screen. (Refer to 2.jpg) (Khanna, Anant Sep 4, 2012) <br> smatreja: Fixed. Check it in next update (Matreja Shyam Sep 5, 2012)<br><br>ANK:The finding has been fixed in U8 build. (Khanna, Anant Sep 19, 2012) |  | 35 | FINDING | 8830 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73996
29951 | FINDING | Exceptions thrown on filtering excessive data in Historical Review | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Historical Review, if a user sets a filter which gives a large number of data entries, an exception message is thrown.<br>For eg: Setting a time range of 6 months and filtering the alarms/points.<br>Two types of Exceptions have been faced so far:<br>1)Exception of type &quot;System.OutOfMemory Exception&quot; (Snapshot 1.jpg)<br>2)External component has thrown an exception (Snapshot 2.jpg) (Khanna, Anant Sep 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Improved. User have to make sure that it has enough system memory. (Matreja Shyam Sep 10, 2012) <br> The finding has been fixed in U8 build. (Khanna, Anant Sep 19, 2012) |  | 35 | FINDING | 8831 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 73998
29952 | FINDING | Function Block tuning commit operation processes even if nothing has been changed. | McMaster, James External Artech | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Commit processing executes when pressing &quot;Commit&quot; button even if no tuning changes have been made. (Christoforetti, Matthew M. Sep 4, 2012) |  |  |  | Open tuning dialog for any function block. Press &quot;Commit&quot; button. Verify nothing happens. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Sep 4, 2012) <br> |  | 35 | FINDING | 8832 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | ? |  |  | FINDING | [6 empty] | 89600
29953 | FINDING | VCoordinator Manager does not work correctly for Redundant VxSim Controller | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On 3.5 WALT network we have configured Redundant VxSim Virtual Controllers (Primary-Drop144 &amp; Backup-Drop147). Using VCoordManager.exe (Ovation Virtual Controller Manager GUI):<br>1. If we try to stop Primary VxSim Drop144, it will stop Backup VxSim Drop147 as well. <br>2. If we try to stop Backup Vxsim Drop147, it will not. <br>Please note that it is possible to start Primary and Backup Drops individually (Lal, Ramesh Sep 4, 2012) |  |  |  | Test by sending stop command to redundant virtual controller currently in backup mode. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected issue in receiving commands in backup mode. (Perdeus, Matthew Sep 28, 2012)<br>---<br>msb - Closed: Converted to SDR 19144 (Benzvi, Mati Oct 16, 2012) <br> |  | 35 | FINDING | 8833 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74002
29954 | FINDING | Control builder string file is unable to locate automatically by NLS Dev kit utility 3.5.0. | Burgoon, Frank AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Control builder string file cannot find the path by itself in resource directory of NLS, so doesn&quot;t allow the Ovation NLS Development kit utility to build satellite assemblies. Firstly we need to create a new &quot;.ts&quot; file with the similar name appeared in warning window at below mentioned path:<br>C:\Programe files\Emerson Process Management\Ovation NLS Development Kit for Ovation 3.5.0\resources\CtrlBldr\cb_hi-IN.ts <br>Please refer the attached. (Jain, Yukta Sep 5, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> National Language Resource Utility (NLSU)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> NLSU.3.5.0_U0 29-AUG-12</p> <p><strong>Originator:</strong> Jain, Yukta</p> <p><strong>Responsible:</strong> Burgoon, Frank J.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jain, Yukta</p> <p><strong>Entry Date:</strong> 2012-09-05T05:34:05-04:00</p> <p><strong>Modified Date:</strong> 2012-09-06T03:11:30-04:00</p> | 0 |  | Ovation for Windows/General/Software | Yes, create the file needed, then follow instructions how to localize the file and then<br>create the localization (McMaster, James Sep 5, 2012)<br><br>How do user will get to know about the file name &amp; path for various languages other then English need to create. Either it should be mentioned in manual or system must generate the file by itself.<br>Manual needs modification first. (Jain, Yukta Sep 6, 2012) <br> |  | 35 | FINDING | 8834 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74003
29956 | FINDING | OCR1100 controller takes more time in Database Distribution compared to OCR400 after reboot. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Its observed after reboot of OCR1100 controller, It takes approx 1 minute to update E5 field(of DU point) from 65535 to 100.<br>However OC400 controller takes approx 1-3 secs for same. (Kumar, Shailendra Sep 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Which drop or drops does this occur on. Is it all 1100&quot;s in the validation lab or just some? (Christy, Benjamin Nov 16, 2012)<br><br>Mark Z corrected issue in DbXmit to resolve this issue. (Christy, Benjamin Dec 17, 2012)<br><br>SDR 19350 created (Ritenbaugh, David W. Jan 16, 2013) <br> |  | 35 | FINDING | 8836 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74007
29957 | FINDING | Controller(Drop34/84) FAILS when ENBL & TMOD signals are high for MASTER SEQUENCER ALGO. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Step to reproduce:<br>1.Create a control sheet using MASTER SEQUENCER ALGO.<br>2.Assign input signals ENBL,OVRD,PRCD,RSET,TMOD &amp; TKIN &amp; also assign Step Number as say 15.<br>3.Load the drop &amp; open the sheet in signal diagram.<br>4.SET the ENBL(Enable Flag) pin, the step becomes 15.<br>5.Now SET the TMOD (Track Flag) signal.<br><br>Observation:The controller goes into fail mode.<br><br>NOTE: The above scenerio happens consistently 8 out of 10 times. <br>Also, some times the corresponding task becomes Freezed with the same operation if the controller does not fail.<br>The above behavior occurs in both redundant &amp; NON redundant controllers.<br>Please find attached snapshots for the above behavior. Also attached is Remote login details to Net#7 DBS drop250. (Prasad, Parmatma Sep 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Call to updateDeviceStat() with a step of zero resulted in a page fault of the calling controll task. Corrected error checking to resolve issue. (Christy, Benjamin Sep 17, 2012)<br>Retested in Ov3.5.0_U9 release,the issue has been resolved. (Prasad, Parmatma Sep 28, 2012) <br> |  | 35 | FINDING | 8837 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74009
29960 | FINDING | Point filter is set to -1 on cancelling the Point Group filter in Historical Review | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Point filter is set to -1 on cancelling the Point Group filter in Historical Review <br>Steps to recreate the problem:<br>1) Click on Point Filter<br>2) Without selecting any point filter, press the cancel button<br>The point filter would be set to a value of &quot;-1&quot; instead of the default value &quot;0&quot;<br>Refer to the attached snapshot. (Snapshot.jpg) (Khanna, Anant Sep 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. Check in next build i.e U8 (Matreja Shyam Sep 10, 2012) <br> The finding has been fixed in U8 build. (Khanna, Anant Sep 19, 2012) |  | 35 | FINDING | 8840 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74015
29962 | FINDING | Controllers Drop35/Drop85 Failed when they were converrted from OCR1100 to OCR400. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller Drop35/Drop85 on 3.5 WALT network is configured for 32k points. It was working normally till June 18 (probably 3.5_U3) . Thenafter it was converted into OCR1100 Controller and it has worked fine till date. However, today when an attempt was made to convert it back into OCR400 Controller, both the controller came into Failed mode. We removed references of &quot;External Ovation Network&quot; but it did not solve the problem. Then we changed 64 MB RAM TO 128 MB RAM in the controller but to no avail. Both the controllers are lying in Failed mode for investigation by Dev. The snapshot of Error log and printErrorBuffer is enclosed for reference. (Lal, Ramesh Sep 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Ben cleared the flashes and the controllers came up. This should be duplicated to see if it happens every time this is done. (Pingree, Douglas K. Sep 7, 2012) <br> Moved to cat 3. User should explicitly clear flash. Pleas re-test. (Boehmer, Robert W. Sep 14, 2012)<br><br>10/01/12:RL - Current drop type of Drop35/Drop85 (OCR400) was changed to OCR1100, Controllers were Downloaded/rebooted, cleared and loaded.The conversion process was successful without any issue. Drop35/Drop85 were converted back to OCR400 and again no issue was noticed.It may be noted that flash disks were not changed. Hence,the finding is closed. (Lal, Ramesh Oct 1, 2012) |  | 35 | FINDING | 8842 |  | FINDING | Ritenbaugh, David PROCESS PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74019
29963 | FINDING | Scroll bar is not coming at Ovation Point Review and System Viewer Options. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation 3.5.0, following steps are performed:<br>1)Open Ovation Point Review--&gt;at top left click to Ovation Point Review Button--&gt;click to Point Review Options.<br>2)Open Ovation System Viewer--&gt;at top left click to Ovation System Viewer Button--&gt;click to System Viewer Options.<br>In both the said conditions, scroll bar is not coming if the windows screen size is made smaller by mouse. For this reason, &quot;OK&quot; and &quot;Cancel&quot; buttons are not coming.<br><br>Please see the attached snapshots for reference. (Mitra, Sambuddha Sep 7, 2012) (Mitra, Sambuddha Sep 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Point Review options dialog has been made non-sizeable. (Burgoon, Frank J. Sep 7, 2012)<br><br>SystemViewer options dialog has been made non-sizeable. (Wozniak, Diane M. Sep 10, 2012)<br><br>Verified in Ov.3.5.0_U8 and seen that the issue is resolved. Hence closing the finding. (Mitra, Sambuddha Sep 18, 2012) <br> |  | 35 | FINDING | 8843 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74021
29964 | FINDING | Some of the test cases of 3.5_SRF1421_SVTP_rev1.2_TN can be removed. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In test cases of 3.5_SRF1421_SVTP_rev1.2_TN the following test cases doesn&quot;t apply &amp; can be removed.<br><br>a)5.16.5-Support for enhanced entry field (iv-vi,xv -xvii) regarding the line width, line pattern &amp; fill pattern.<br>b)5.17.5-Support for Rounded buttons (v-vi,xv -xvii, xviagain ) regarding the line width, line pattern &amp; fill pattern.<br>c)5.18.6-Support for Meter(v-vi,xvi -xvii) regarding the line width, line pattern &amp; fill pattern.<br>d)5.19.6-Support for BMP_IMAGE enhancement(v-vi,xvi -xvii) regarding the line width, line pattern &amp; fill pattern.<br>e)5.20.12-Support for enhanced entry field (v-vi,xvi -xvii) regarding the line width, line pattern &amp; fill pattern.<br>f)5.16.5-Support for Ol Sliders (v-vi,xvi -xvii) regarding the line width, line pattern &amp; fill pattern. (N, Thamaraiselvi Sep 7, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Control Builder - Unified (CBU)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Hutchison, Steven B. N, Thamaraiselvi</p> <p><strong>Entry Date:</strong> 2012-09-07T03:28:15-04:00</p> <p><strong>Modified Date:</strong> 2012-09-10T11:25:55-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8844 |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | N, Thamaraiselvi AUTOSOL PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74022
29965 | FINDING | OSR Report doesnot identify the Operating System Service Pack for 64-bit machines. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OSR Report doesnot identify the Operating System Service Pack for 64-bit machines. <br><br>For 32-bits machines, Operating System Service Pack is seen as Service Pack1/ whichever applicable, while for 64-bit machines, OS Service Pack version is seen as (blank). (Sachan, Pallavi Sep 7, 2012)<br><br>I need access to your machine with this issue. Kindly email the remote login details and the drop name. (Quintos, Ronaldo M. Oct 31, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012)<br><br>Kindly create a SDR for tracking purposes. I will reference the SDR number when creating the patch. (Quintos, Ronaldo M. Jan 4, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The 64-bit machine Drop231 can be logged in using the attached Remote_Login_Details.doc (Sachan, Pallavi Nov 1, 2012) <br> Finding Closed as SDR19306. (Sachan, Pallavi Jan 4, 2013) |  | 35 | FINDING | 8845 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74024
29966 | FINDING | SimControl GUI reports errors where are misleading | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In SimControl GUI Freeze,Save, Load, Run commands are working fine but its error log shows &quot;Error receiving reply, ret=7&quot; for all the commands. It gives the impression as if the commands were not executed successfully. Please refer the attached snapshot. (Lal, Ramesh Sep 7, 2012) |  |  |  | Use simcontrol gui to send simulator commands and ensure that if the commands are actually performed, that they return success (not always reporting an error). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected problem in receiving simulator command replies. (Perdeus, Matthew Sep 21, 2012)<br>---<br>msb - Closed: Converted to SDR 19146 (Benzvi, Mati Oct 17, 2012) <br> |  | 35 | FINDING | 8846 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74026
29967 | FINDING | OSR doesnot display 32b/64b type and Installed RAM info | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | The OSR report on Ov-3.5.0 doesnot display following Information:<br> System Type: {32-Bit,64-Bit} Operating System<br> Install Memory (RAM): #.## GB<br><br>Both are important to report (Benzvi, Mati Sep 7, 2012)<br>---<br>msb - 10/31: WIW is not good.<br>It is impotant to know if an Ovation client is running - Ex. on W7(32b) or W7(64b)<br>It is imprtant to know how much RAM is on the client.<br>Both pieces of information are readily available in the System UI. (Benzvi, Mati Oct 31, 2012)<br><br>Added. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012)<br><br>Kindly create a SDR for tracking purposes. I will reference the SDR number when creating the patch. (Quintos, Ronaldo M. Jan 4, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | On SIS network, OSR reports:<br>drop135: <br>Operator System Name: Microsoft Windows Server 2008 R2 Standard (64-bit)<br>Computer Model: PowerEdge T300 (1.99 GB)<br><br>drop137: <br>Operator System Name: Microsoft Windows 7 Professional (32-bit)<br>Computer Model: OptiPlex 960 (3.25 GB)<br><br>drop139: <br>Operator System Name: Microsoft Windows 7 Professional (64-bit)<br>Computer Model: OptiPlex 990 (3.96 GB) (Benzvi, Mati May 23, 2013) <br> |  | 35 | FINDING | 8847 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74028
29968 | FINDING | There are discripancies in DSR of VCH/VC vi-a-vis MMI/ Controller | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Each Virtual Controller is supposed to originate Drop Status Record (DSR)similar to Standard Controller Drop and Virtual Host will originate DSR similar to Ovation MMI. There exists following dicripancies in DSR:<br>Interface Vendor(VE)=10 For VC, OHI For Controller<br>Interface Vendor(VE)=Unknown For VCH, OHI For MMI (Lal, Ramesh Sep 7, 2012) |  |  |  | Use Point Info to check VE field in DU record of a virtual controller and ensure it reads &quot;Wind River&quot; and not &quot;10&quot;. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The VCH should be operating the same as any MMI not configured with OHI. <br>The 10 for the vxsim is for the WindRiver simnet driver. The text for PI should be updated for this. (Perdeus, Matthew Oct 26, 2012)<br><br>11/14/2012:RL - Dev may like to change the text in PI as viewed by Matt.Hence, this finding is <br> being referred to Dev resposible for PI. (Lal, Ramesh Nov 14, 2012)<br><br>PI updated by Lisa A. to use &quot;Wind River&quot; text for VE=10. (Perdeus, Matthew Nov 15, 2012)<br>---<br>msb - in DU record of VC: VE = Wind River (Benzvi, Mati May 23, 2013) <br> |  | 35 | FINDING | 8848 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74030
29969 | FINDING | SimControl GUI requires some changes | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Sim Control GUI the text &quot;Full Snapshot&quot; should be changed to &quot;Partial Snapshot&quot; when the button is disabled.Presently it is always &quot;Full Snapshot&quot; irrespective of whether the button is Enabled or Disabled. (Lal, Ramesh Sep 7, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This was done to act according to Microsoft&quot;s guidelines for Ribbons and their controls.<br><br>The button is acting like a checkbox with &quot;Full snapshot&quot; being enabled or disabled. (Perdeus, Matthew Sep 21, 2012)<br><br>9/25/12: RL - Finding closed based on Dev&quot;s comment (Lal, Ramesh Sep 25, 2012) <br> |  | 35 | FINDING | 8849 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74032
29970 | FINDING | 3.5_Controller_SVTP_Rev5.1 - Test 5.23.2: has items g) & h) twice | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | 3.5_Controller_SVTP_Rev5.1 - Test 5.23.2: has items g) &amp; h) twice.<br>should be fixed to { a) to q) } instead of { a) to o) }. (Benzvi, Mati Sep 8, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2012-09-08T17:54:39-04:00</p> <p><strong>Modified Date:</strong> 2012-09-08T17:54:39-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8850 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74033
29971 | FINDING | 3.5_Controller_SVTP_Rev5.1 - Test 5.23.2: items {k - q} are incorrect according to SRF 1379 | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | 3.5_Controller_SVTP_Rev5.1 - Test 5.23.2: items {k - q} are incorrect.<br>SRF # 1379 -OCR1100 FS stats in:<br> 3.3 Controller Functionality<br> The OCR1100 will detect at boot what version it is (G01 and G02). If G02, the OCR1100 <br> will be able to detect the SFP type (speed and media). The controller will log this <br> information. This information will also be made available to Controller Diagnostics <br> and the Sysytem Registration Utility.<br><br>No where in the FS it states that this info [OCR type {400,1100} and { G0x}] will also be <br>displayed in the Ovation Errorlogs as stated in the SVTP. (Benzvi, Mati Sep 8, 2012)<br>----<br>The specs and implementaion is for OCR1100 only.<br>Therefore, 3.5_Controller_SVTP_Rev5.1 - Test 5.23.4: items {a, b} are incorrect:<br> Diagnostics does not show G0x of OCR400 controllers. (Benzvi, Mati Sep 19, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2012-09-08T18:46:56-04:00</p> <p><strong>Modified Date:</strong> 2012-09-19T18:55:13-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8851 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74034
29974 | FINDING | AMS Device Manager test cases in "3.5_CONTROLLER_SVTP_rev4.5_VP.docx" SVTP need to be modified. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Below test cases in &quot;3.5_CONTROLLER_SVTP_rev4.5_VP.docx&quot;SVTP need to be modified.<br>1. Test 5.6.1.4(b) and 5.6.3.4(b) statement &quot;Right click on a Temperature device and select configure from the pull down list.Verify that live data is being displayed for the device&quot; needs to be replaced with &quot;Right click on a Temperature device and select Process Variable from the pull down list. Verify that live data is being displayed for the device&quot;.<br>2. Test case 5.6.1.4(c) and 5.6.3.4(c) statement &quot;Right click on a Temperature device and select Sensor Config. From the pull down menu select Display Sensor Connections and verify that the proper sensor types are displayed for the device¿s sensors.&quot; needs to be replaced with &quot;Right click on a Temperature device and select Configure/Setup. Select Variable Configuration option.Verify that the proper sensor types are displayed for the device¿s sensors. &quot; (Pandey, Vijay Sep 10, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2012-09-10T04:41:26-04:00</p> <p><strong>Modified Date:</strong> 2012-09-10T04:41:26-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8854 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74039
29975 | FINDING | OSR doesnot report installed Lumension software on 64-bit machines. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In a 32-bits machine when Lumension software is installed it is seen as below.<br>Under Other Installed Software:<br>&lt;a&gt; LM Agent<br>&lt;b&gt; Lumension Patch Agent for Windows.<br><br>This is not seen for 64-bit machines. (Sachan, Pallavi Sep 10, 2012)<br><br>I need access to your machine with this issue. Kindly attach the remote login details and the drop name. (Quintos, Ronaldo M. Nov 13, 2012)<br><br>Changed action from DDR to MIR. (Quintos, Ronaldo M. Sep 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013)<br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 8855 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74041
29976 | FINDING | Cannot configure Advanced Virtual Controller with 32000 points in Developer Studio. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | During configuring drop of type &quot;Advanced Virtual Controller&quot; there is possibility to configure Maximum Point Limit as &quot;Normal (6000)&quot; and &quot;Expanded (16000)&quot;. There is missing &quot;32000&quot; option. (Kossowski, Grzegorz Sep 10, 2012) |  |  |  | The affected area is in the software responsible for generating the set of applicable configuration selections for Maximum Point Limit (based on drop type). The software has been changed to treat the Advanced Virtual Controller the same as the Virtual Controller. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The software which generates the list of configuration options for &quot;Maximum Point Limit&quot; (based on drop type) is incorrect in the case of Advanced Virtual Controller. This error was introduced when the Advanced Virtual Controller drop type was introduced in this release. The software will be corrected. (Swartz, Mark E. Sep 10, 2012) <br> |  | 35 | FINDING | 8856 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW |  |  | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kossowski, Grzegorz PROCESS PWS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74043
29977 | FINDING | Numa-Logic OCR400 is experiencing Ran Late errors after being upgraded to Ovation 3.5.0. | Christy, Benjamin A PROCESS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 43/93 was copied from the NUMALOG1 3.4.0 system to the EMILY 3.5.0 system (i.e., identical database and control). The controller ran on the 3.4.0 system with Numa-Logic I/O for several months without experiencing Ran Late errors. The Worst Cycle times for Tasks 2 and 3 on the 3.5.0 system are substantially higher than those from the 3.4.0 system. Images of Controller Diagnostics are attached. (Brown, Sean Sep 10, 2012)<br><br>Reassigning to Ben. (Boehmer, Robert W. Dec 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This seems to have gone away at some point. Can we retest to verify? (Christy, Benjamin Jan 28, 2013)<br><br>This should have been fixed in U8 refer to SDR 18548 (Christy, Benjamin Feb 20, 2013) <br> |  | 35 | FINDING | 8857 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74045
29978 | FINDING | XY plot-X axis settings with 4 quadrant layout .if we changing XY plot setting it will reflect in all quadrant | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In property pain window if user changes any setting in display setting it will only effect in the seleted point quadrant but if we select XY plot -X axis setting it will affet all 4 quadrant . (Sharma, Vaibhav Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The XY-Plot option in point properties panel, is meant to mark that POINT as x-axis for XY-Plot.<br>Once checked, XY-Plot mode is then applied to all quadrants.<br><br>If no points are marked as XY_Plot, then x-axis shows DATE_TIME.<br><br>As per current design, each quadrant does not have independent XY-Plot mode. (Bargaje Prashant Sep 10, 2012)<br><br>As per developer comment closing this finding . (Sharma, Vaibhav Jul 22, 2013) <br> |  | 35 | FINDING | 8858 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sharma, Vaibhav PROCESS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74047
29979 | FINDING | Trend application crash if we using zoom option with 4 quad display. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When we using Quad view for trend view in layout option .trends application got crash .i am mentioning step done for this <br><br>Steps performed<br>1. Open any previous created group have 4- 5 point <br>2. Select quad view in layout <br>3. Select any of the point use display setting option area bar &amp; select marker for same point.<br>4. use xy-Axis option now <br>5. Some all four quad rant point xy axis plot changes and some of point scale looks like over lapped .<br>6 use Zoom option for any above mention type point immediately trend application fails.<br><br><br>It seems problem is with scale range as if we use small scale range or defined scale range for any point. This scenario can be avoided. (Sharma, Vaibhav Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please retest in 3.5.0_U8. (Bargaje Prashant Sep 12, 2012)<br><br>Failed in Retest in OV 3.5.0_U8 (it seem now scale is not over lapping but still when use zoom option trend application stop responding. (Sharma, Vaibhav Sep 18, 2012)<br>---<br>msb - Closed: Converted to SDR 19201 (Benzvi, Mati Oct 26, 2012) <br> |  | 35 | FINDING | 8859 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Contento, James AUTOSOL PWS PITT | Sharma, Vaibhav PROCESS PWS NOIDA | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74049
29980 | FINDING | 3.5_CONTROLLER_SVTP_rev4.5_VP.docx, test cases 5.6.2.2, 5.6.4.2, 5.6.2.4(c)and 5.6.2.4(c) are NA. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Below test cases with following reason needs to be marked NA.<br>1.HART High Performance Analog Output module (5X00167G01/1X00188H01A) contains only 4 channels. However, in TR 3.4_CONTROLLER_SVTP_rev4.5_VP.docx, test case 5.6.2.2 and 5.6.4.2<br>says to check the devices on Channels 5, 6, 7 &amp; 8 also. So these are NA.<br>2.In TR 3.4_CONTROLLER_SVTP_rev4.5_VP.docx, test case 5.6.2.4 (c)and 5.6.4.4 (c) says &quot;Verify that the proper sensor types are displayed for the device&quot;s sensors&quot; connected with<br>High Performance AO module. However, there are no sensors displayed for output<br>devices. Hence these test cases are NA. (Pandey, Vijay Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/28/12 - fixed in CONTROLLER_SVTP_rev4.6 and in CONTROLLER_SVTP_rev5.3. (Capani, Nooch Sep 28, 2012) <br> |  | 35 | FINDING | 8860 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74051
29981 | FINDING | First point of the RESET tab in Alarm system can"t be selected for reset. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In the RESET tab of Alarm system the first point (top most entry) in the list can&quot;t be selected to reset the point as cursor doesn&quot;t stay there. This will happen if there are other points toggling in and out of alarm. (Lal, Ramesh Sep 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. Will be available in next build. U8 (Matreja Shyam Sep 10, 2012)<br><br>9/21/12:RL - Testes in 3.5_U9. The cursor now stays on the first point (top most entry) but if <br> the point is selected it can not be deselected. Finding failed retest. (Lal, Ramesh Sep 21, 2012)<br><br>smatreja: For deselection, User need to hold Ctrl-key and use Mouse Left key. Same behavior exists in other application i.e. Point Review. (Matreja Shyam Sep 24, 2012)<br><br>9/21/12:RL - As there is an alternate way to perform the function and also same behaviour exists in other Ovation Application, the finding is closed. (Lal, Ramesh Sep 24, 2012) <br> |  | 35 | FINDING | 8861 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74053
29982 | FINDING | MAC address field is not disabled as per the Task 5.1.2. C documented in 3.5_SRF1583_SVTP_rev1.1. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation version 3.5, while adding Virtual Data Server in Dev studio under SIS network, if Virtual Data Server checkbox is selected then it should not disabled the Data Server Ethers Address field.<br>As per the Task 5.1.2 C, it suppose to disable the Data Server Ethers Address filed if Virtual Data Server checkbox is selected. (Bhanegaonkar, Sukhanand Sep 11, 2012) |  |  |  | The affected area is in the handling of the Data Server Ether Address field shown when editing a SIS Data Server in the Ovation Developer Studio. The field should be shown as read-only if the SIS Data Server is configured to be Virtual. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Data Server Ether Address field (primary-side) will be enabled/disabled based on the configuration of the Virtual data server checkbox. This had been previously overlooked. (Swartz, Mark E. Sep 11, 2012) <br> |  | 35 | FINDING | 8862 |  | FINDING | Bhanegaonkar, Sukhanand EMR SYSS PSS NASK | Ratnaparkhi, Shirish EMR SYSS PSS NASK | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Bhanegaonkar, Sukhanand EMR SYSS PSS NASK | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74055
29983 | FINDING | OSR, Advanced Virtual Controller is reported as Security Server. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In OSR Report, The Drop configured as Advanced Virtual Controller is reported as Security Server. (Sachan, Pallavi Sep 11, 2012)<br><br>I need access to your machine with this issue. Kindly email the remote login details and the drop name. (Quintos, Ronaldo M. Oct 31, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Kindly find attached Remote_Login_Details.doc file. <br><br>You will be logged into DBS Drop176. On this network you will find Drop14 which is configured as OCR1100 (kindly note that this controller drop is not present physically, just for OSR report purpose I have done the configuration).<br><br>Whereas in Pittsburgh lab we have real OCR1100 controllers. (Sachan, Pallavi Nov 1, 2012) <br> |  | 35 | FINDING | 8863 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74057
29984 | FINDING | MAC ID is required to create Virtual SIS controller. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | MAC ID is required to create Virtual SIS controller.In case of virtual SDS Dev Studio should be disable or not required. (Sharma, Vaibhav Sep 11, 2012)<br><br>closing this finding (Duplicate finding) (Sharma, Vaibhav Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8864 |  | FINDING | Sharma, Vaibhav PROCESS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74059
29986 | FINDING | Redundant VxSim Controller gives "Detected both drops in control" message in the Error log | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On 3.5 WALT network we have configured Drop144 as Primary VxSim Controller and Drop147 as Partner VxSim Controller. When Drop144 (in Control) is rebooted Partner Drop147 takes the control only for few seconds and reverts back to Back up mode. In the Ovation error log we get the message &quot;Detected both drops in control(from partner DU):DROP Reboot&quot; <br>Please refer the attached Error log. (Lal, Ramesh Sep 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Are these on the same host or separate host? (Perdeus, Matthew Sep 24, 2012)<br><br>9/24/12:RL - Both Primary Virtual Controller Drop144 and Partner Virtual Controller Drop147 are on the same Virtual Controller Host Drop244 on 3.5 WALT network. (Lal, Ramesh Sep 24, 2012)<br><br>Drop244 is running at ~ 70%, spiking higher at times. This is without the vcoordinator or WindRiver network service running. ~50% being used by avp.exe. Adding in the virtual services and the vxsims, the vxsims are not getting enough time to run consistently and messages are being missed. It should be determined why the avp.exe is consuming most of the CPU. (Perdeus, Matthew Oct 26, 2012) <br> 1/03/13:RL - Monitored redundant Virtual Controllers operation on VCH Drop182 on Net#8 in IEC. On this machine avp.exe is consuming ~5% CPU time. The failover to partner VC is taking place as desired and we don&quot;t get above message in Ovation Error log.Hence finding is closed. (Lal, Ramesh Jan 3, 2013) |  | 35 | FINDING | 8866 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74063
29987 | FINDING | Test case 5.1.2 & 5.3.3, in SVTP "3.5_SRF1652_SVTP_rev1.1_XX.doc"(XX=PP, SA) need to modify. | Prasad, Parmatma EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Test case 5.1.2, in SVTP &quot;3.5_SRF1652_SVTP_rev1.1_XX.doc&quot;(XX=PP,SA),there should be removed test case 5.1.2/d because &quot;there is no action taken place on Click the left mouse button over the Poke-8&quot;. <br>Same modification also for Test case 5.3.3, there should be removed test case 5.3.3/d because &quot;there is no action taken place on Click the left mouse button over the Poke-8&quot;. <br>Hence the SVTP should modify accordingly. (Prasad, Parmatma Sep 12, 2012) (Capani, Nooch Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - Parmatma: please update Val\Tests\3.5.0\SVTPs-Future\SRF1652_SVTP_rev1.2.doc with your requested changes. Close this finding when you are done. Thanks. (Capani, Nooch Sep 27, 2012)<br>pp 9/28/12:changed the SVTP(SRF1652_SVTP_rev1.2.doc ) as per above comment. (Prasad, Parmatma Sep 28, 2012) <br> |  | 35 | FINDING | 8867 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74065
29988 | FINDING | Test case 5.1.3(4, 5, 6) & 5.3.3(4, 5, 6), in SVTP "3.5_SRF1652_SVTP_rev1.1_XX.doc"(XX=PP, SA) need to modify. | Prasad, Parmatma EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2015-07-13 03:53 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2015-07-13 03:53 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Test case 5.1.3(4, 5, 6), in SVTP &quot;3.5_SRF1652_SVTP_rev1.1_XX.doc&quot;(XX=PP, SA), there should be removed test case 5.1.3/b,5.1.4/b,5.1.5/b &amp; 5.1.6/b because &quot;There is no action taken place on Click the left mouse button over the button if trigger function used&quot;. <br>Same modification also for Test case 5.3.3(4, 5, 6) there should be removed test case 5.3.3/b,5.3.4/b,5.3.5/b&amp;5.3.6/b because &quot;There is no action taken place on Click the left mouse button over the button if trigger function used&quot;. <br>Hence the SVTP should modify accordingly. (Prasad, Parmatma Sep 12, 2012) (Capani, Nooch Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - Parmatma: please update Val\Tests\3.5.0\SVTPs-Future\SRF1652_SVTP_rev1.2.doc with your requested changes. Close this finding when you are done. Thanks. (Capani, Nooch Sep 27, 2012)<br>pp 9/28/12:changed the SVTP(SRF1652_SVTP_rev1.2.doc ) as per above comment. (Prasad, Parmatma Sep 28, 2012) <br> |  | 35 | FINDING | 8868 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | u4 |  |  | FINDING | [6 empty] | 82448
29989 | FINDING | OSR, OCR1100 is reported as Unknown. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | If Controller is OCR1100, Model in OSR report is shown as UNKNOWN. (Sachan, Pallavi Sep 12, 2012)<br><br>Changed category to CAT5 since this is a new feature. (Quintos, Ronaldo M. Sep 12, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012)<br><br>Kindly create a SDR for tracking purposes. I will reference the SDR number when creating the patch. (Quintos, Ronaldo M. Jan 4, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Finding Closed as SDR 19305. (Sachan, Pallavi Jan 4, 2013) <br> |  | 35 | FINDING | 8869 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74069
29990 | FINDING | OSR, Licensing does not show SIS Configuration Tools license details. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In developer studio, Ovation License Manager has License details for feature: SIS Configuration Tools, but this is not repoeted under licensing in the SureService Ovation system Registration Report. (Sachan, Pallavi Sep 12, 2012)<br><br>Changed Category to CAT5 since this is a new feature. This is not available in previous version. (Quintos, Ronaldo M. Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8870 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74071
29991 | FINDING | OSR, MAC address and IP address are not available for Controllers. | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | MAC address and IP address of the Controllers are not reported in OSR report. (Sachan, Pallavi Sep 12, 2012)<br><br>The IP and MAC addresses have been removed in this release to comply with NERC. I need to lookup the SRF/SDR number. (Quintos, Ronaldo M. Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Kindly provide the SRF/SDR number, so that I can close the finding. (Sachan, Pallavi Sep 14, 2012) <br> |  | 35 | FINDING | 8871 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74073
29992 | FINDING | OSR: Software Revision is not available for advanced controller | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Software Revision is not available for advanced controller type. (Singh, Ghanshyam Sep 12, 2012)<br><br>Kindly specify what is being displayed in the report (NA, (blank))? (Quintos, Ronaldo M. Sep 12, 2012)<br><br>If this is a new controller, this is not yet supported. Kindly change the category to CAT5. (Quintos, Ronaldo M. Sep 12, 2012)<br><br>This is OCR400 controller only. Kindly find attached html file for clarity .(OSR report from pgh lab and check 14/64 controller ) (Singh, Ghanshyam Sep 13, 2012)<br><br>Changed Action field to DWI. (Quintos, Ronaldo M. Oct 24, 2012)<br><br>Software revision is available only in OCR1100. (Quintos, Ronaldo M. Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Finding closed as per developer&quot;s comment. (Singh, Ghanshyam Nov 27, 2012) <br> |  | 35 | FINDING | 8872 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74075
29993 | FINDING | OSR: Hardware revision and serial are shown as NA for controllers | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Hardware revision and serial are shown as NA for controllers in the OSR reports (Singh, Ghanshyam Sep 12, 2012)<br><br>What type of controller is this? Kindly verify if the information is collected on previous OSRU version, if not, NA is a valid value for these entries. (Quintos, Ronaldo M. Sep 12, 2012)<br><br>My controller type is OCR400 but it is observed for the hardware modules. But it is necessary to display until controller itself provides NA for Hardware revision and serial(some hardware modules does not show Hardware revision and serial perhaps Hardware revision and serial are not present).If you could provide old version OSR report, it would help to compare. (Singh, Ghanshyam Sep 13, 2012)<br><br>Changed Action field to DWI. (Quintos, Ronaldo M. Oct 24, 2012)<br><br>Controller does not return these info as of the moment. (Quintos, Ronaldo M. Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | If this is planned to be fixed in future release then it would be better to change the Action field from WIW to MNR. (Singh, Ghanshyam Nov 14, 2012)<br><br>changing state of Action Field from MNR to WIW. OCR400s doesn&quot;t have the capability to show its serial and mfg index information. (Benig, Ronaldo B. Apr 1, 2014) <br> |  | 35 | FINDING | 8873 |  | FINDING | Jimenez, William PROCESS PWS MNL | Layug, Leslie PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Singh, Ghanshyam EMR SYSS PWS LEIC | [6 empty] | Implementation | 3.5.1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74077
29994 | FINDING | OSR:MAC address and IP address of the Server and Workstation are not reported in OSR report. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | MAC address and IP address of the Server and Workstation are not reported in OSR report. (Singh, Ghanshyam Sep 12, 2012)<br><br>The IP and MAC addresses have been removed in this release to comply with NERC. I need to lookup the SRF/SDR number. (Quintos, Ronaldo M. Sep 12, 2012)<br><br><br>Closed as per developer&quot;s comment. (Singh, Ghanshyam Sep 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8874 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74079
29995 | FINDING | During Timeout state of any point trend colour remain same as it default good colour. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | During Timeout state of any point trend colour remains same as it default good colour. For long term monitoring of trend graph it their is any Time out state of any point due to system failure. User unable to know that point goes in bad status. This state only reflects in Table form or in real time monitoring of point detail pane. (Sharma, Vaibhav Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This application behavior is consistent with the previous Trend version. (Contento, James L. Sep 12, 2012) <br> |  | 35 | FINDING | 8875 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sharma, Vaibhav PROCESS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74081
29996 | FINDING | OSR, Microsoft AntiXSS v4.2.1, software entry is seen DBS drop only. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Microsoft AntiXSS v4.2.1, software is found installed on all the drops in the network, but OSR reports this for DBS drop only. (Sachan, Pallavi Sep 12, 2012)<br><br>Changed Action field to DWI. (Quintos, Ronaldo M. Oct 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013)<br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 8876 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74083
29997 | FINDING | OSR: Few installed software are not reported under other installed software. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Few installed software are not reported under other installed software:<br>1.Inter(R) network connection drivers<br>2.java(TM)6 Update33(64 Bit)<br>3.Kaspersky lab Network agent <br>4.Microsoft Visual C++ some installed patches are missing.(observed in Server 2008) (Singh, Ghanshyam Sep 12, 2012)<br><br>Changed Action field to DWI. (Quintos, Ronaldo M. Oct 24, 2012)<br><br>I need access to your machine with this software installed. Kindly email the remote login details and the drop name. (Quintos, Ronaldo M. Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Kindly find the attached Remote_login_details.doc file for connecting to Drop231 for above mentioned Points 1-3 and Drop250 for above mentioned Point4. (Singh, Ghanshyam Nov 27, 2012)<br><br>Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013)<br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 8877 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Singh, Ghanshyam EMR SYSS PWS LEIC | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74085
29998 | FINDING | GB Basic: two help buttons are not working. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Two help buttons are not working in graphics builder:<br>1.Quick button<br>2.ol rectangle (Singh, Ghanshyam Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The help button on the GBNT:olrectangle/frame dialog is working in the u7 version I am running. The Help menu item on the GBQuickView window is grayed out (not working). Is this what you mean? Can you re-check the olrectangle/frame help? The help topic displayed should vary depending on which item is selected on the dialog. The same dialog is used to create both olrectangle and frames in GBNT. (Johnson, Kathy Sep 12, 2012)<br><br>GS:Yes,the Help menu item on the GBQuickView window is grayed out (not working).You are correct ol rectangle is now working. (Singh, Ghanshyam Sep 12, 2012) <br> |  | 35 | FINDING | 8878 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74088
29999 | FINDING | OSR does not report details of Non-Ovation OSC Server Drop. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Ovation Security Center is a Non-Ovation Drop. It is a Dell PowerEdge R610, 32-bit machine.<br>OSR_1.3 agent is installed on it. <br>Now, its IP is added in Non Ovation drops IP Address, on Registered System Contact Information Window.<br>A report is generated, but the details of this drop are not received. Error shown is &quot;No responses to request was received.&quot; Both the drops are pinging to each other.<br><br>Kindly find the remote login details. (Sachan, Pallavi Sep 12, 2012)<br><br>Is OSRU agent installed on the non-Ovation drop? OSRU UI communicates with the agent to collect the information from the machine. Please verify. (Quintos, Ronaldo M. Sep 12, 2012) (Sachan, Pallavi Sep 12, 2012)<br><br>May I know if you can ping the non-Ovation drop from the DBS machine? (Quintos, Ronaldo M. Oct 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SureService Ovation System Registration Utility 1.3 is installed on the system. Also OvSysRegAgent.exe is found running in the drop. (Sachan, Pallavi Sep 12, 2012)<br><br>Yes, I can ping the Non-Ovation Drop from DBS, This non -ovation drop is acting as OSC server and it pushes the MSPatches updates to all the networks on weekly basis. (Sachan, Pallavi Oct 25, 2012) <br> |  | 35 | FINDING | 8879 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74091
30000 | FINDING | Enhanced Keyboard Alarm Function (SRF #742) can not be tested for 32bit Windows7 drop. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | &quot;5.4.14 Test: Enhanced Keyboard Alarm Function (SRF #742)&quot; regarding 3.5_WIN_OPCON_SVTP_rev2.H_SM.doc can not be tested. To test it, we need the driver-software of Dell extended keyboard for 32bit Windows7 OS. We have the software for Windows-XP OS system only in our validation lab.<br>The driver-software for 32bit Windows7 OS drop is not available here,so &quot;5.4.14 Test:&quot; of 3.5_WIN_OPCON_SVTP_rev2.H_SM.doc can not be verified. (Mitra, Sambuddha Sep 12, 2012) (Capani, Nooch Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - marked test as N/A in STP rev 1.3. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8880 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74093
30002 | FINDING | Redundant Workstations when configured as Redundant VCH drops are not downloaded correctly | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When 2 redundant Workstations are configured as Redundant VCH drops (226/227)<br>1. The config.vch.227 has the IP of 226.<br>2. the config.vch.226 is downloaded also to 227. (Benzvi, Mati Sep 12, 2012) |  |  |  | The save and download functionalities of the Ovation developer Studio have been affecte. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Ok in 3.5.0_U8 @ 18-Sep-2012<br> Drop record in Studio must be touched to regenerated the CONFIG.VCH files before download (Benzvi, Mati Sep 18, 2012) <br> |  | 35 | FINDING | 8882 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74097
30004 | FINDING | Numa-Logic EIO modules do not boot. | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 43/93 (EMILY) was duplicated from the Ovation 3.4.0 system (used for the Clover project). The power supplies for the six redundant EIO modules were power-cycled. After 30 minutes the modules have not booted. There are no messages in the Ovation Error Log or in the controller error buffer about the EIOs. The LEDs on the EIOs indicate that they are continuously trying to boot. (Brown, Sean Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The tftp server daemon was not being started. The files on the db server were dated August 22nd. A change was made to start the new tftp daemon (the Interpeak tftp used in vxWorks 6.8) after this date. The fix has been lib&quot;d and will be available in the next update. This was verified in the development labs and the latest changes were applied to the validation screen and the tftp server spawned and the nodes booted successfully. (Ciccozzi, Anthony Sep 12, 2012)<br><br>This appears to be resolved in U8; closing. Refer to Finding 8941. (Brown, Sean Sep 20, 2012) <br> |  | 35 | FINDING | 8884 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74101
30005 | FINDING | The vxsimnetd.conf file should be configurable other than IP:x.x.x.0 & NM:255.255.255.0 | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The vxsimnetd.conf file should be:<br>a. configurable to IP other than x.x.x.0 and nemask other than 255.255.255.0.<br>b. Should not be downloaded over.<br>Cases in point: <br>a. Wide switch setting: VCH IP 3rd digit one lower than IP of VCs with netmask 255.255.254.0.<br>b. Narrow switch setting: as in base IP x.x.x.32 and netmask 255.255.255.224 (Lab setting) (Benzvi, Mati Sep 12, 2012) |  |  |  | The vxsimnetd.conf file should now be downloaded with a netmask of 255.255.254.0. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The netmask issue was addressed by patches 8 and 15. The default netmask is now 255.255.254.0. (Perdeus, Matthew Jul 17, 2013) <br> |  | 35 | FINDING | 8885 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74103
30006 | FINDING | Unable to convert Sim COntroller(1100) to Standard Controller(1100). | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | 1:- Convert Standard COntroller(1100) to SIM Controller.It is working properlly.<br>2:- In Developer studio, Change the Sim Controller Type to Controller type.<br>3:- Delete all the file from both controller flash.<br>4:- Download the controller drop &amp; select the Reboot check box.<br>5:- During loading the controller following message are popping up.<br> <br>&quot; Unable to write: /ata0/module/profibus/boot/vxWorks &quot;<br><br>Note:- When download the condroller drop with uncheck reboot option, it will download properlly.<br><br>For more information please find the attached screeen shots(changing problem from SIM To con1100.jpg) (Agarwal, Gaurav Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This issue was beign caused by an RPC call timming out on the controller end. This was because disk accesses were not being done in the context of the writing task but in the context of the atasvc task which could take longer at times. Changed vxworks so that disk access were immediate. (Christy, Benjamin Dec 20, 2012)<br><br>SDR 19344 created (Ritenbaugh, David W. Jan 16, 2013) <br> |  | 35 | FINDING | 8886 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Ritenbaugh, David PROCESS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74105
30007 | FINDING | Configured third party driver also appear in download preview window if any new driver is added or existing is removed. | Swartz, Mark EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Following steps are performed in drop1/51(OCR400-Emily system).<br>1. Configured a devices for third party drivers (e.g GE Genius, Modbus, MHI etc) in<br> Developer&quot;s studio.<br>2. Performed download operation of drop1/51.<br><br> It is observed if any new driver (e.g MHI) is added or any configured driver is<br> deleted and drop1/51 is downloaded then its Download Preview window shows Query result <br> of all the drivers which already been downloaded (in step2). (Sahay, Madhukar Sep 12, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Swartz, Mark E.</p> <p><strong>Notify List:</strong> Pingree, Douglas K. Sahay, Madhukar Ciccozzi, Anthony</p> <p><strong>Entry Date:</strong> 2012-09-12T15:20:00-04:00</p> <p><strong>Modified Date:</strong> 2012-12-20T10:17:45-05:00</p> | 0 |  | Ovation for Windows/General/Software | Dev Studio changes all device files any time any driver change is made. Re-assigning to Kim. (Boehmer, Robert W. Dec 19, 2012) <br> |  | 35 | FINDING | 8887 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | Ritenbaugh, David PROCESS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74106
30008 | FINDING | Alarm Summary Point should be off alarm when all the points in the group are back with Return value. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Alarm Summary Point should turn off alarm when all the points in the group are back with Return value.<br>Currently, Tha Alarm summery Point remains in Alarm until all the points are Return, acknowledged and reset. (Benzvi, Mati Sep 12, 2012)<br>---<br>msb - Closed: converted to SDR 19114 @ 08-Oct-2012 (Benzvi, Mati Oct 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8888 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74108
30010 | FINDING | Few of the test cases in TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx cound not be done at IEC due to unavailability of HW | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following test cases in TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx could not be done at IEC as G02 processor module hardware is not available:<br>- 5.23.2 l)<br>- 5.23.4 b)<br>Hence these test cases are NA. (Gupta, Chandresh Sep 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/2712 - asked Dave Dailey to ship G02 OCR400 to IEC on 9/17/12. (Capani, Nooch Sep 27, 2012)<br><br>cg (10/04/12) - OCR400 G02 modules received in IEC. This will enable to do test cases mentioned above. Hence this finding is closed. (Gupta, Chandresh Oct 4, 2012) <br> |  | 35 | FINDING | 8890 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74112
30011 | FINDING | OSR, Drawing,Firm version, IP address and Netmask are not present in report. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Drawing,Firm version, IP address and Netmask are not present in OSR report of Network Device information.IP and Netmask were present in previous testing of OSR1.3. (Singh, Ghanshyam Sep 13, 2012)<br><br>The IP and MAC addresses have been removed in this release to comply with NERC. (Quintos, Ronaldo M. Oct 31, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Finding is closed as per developer&quot;s commnets. (Singh, Ghanshyam Nov 14, 2012) <br> |  | 35 | FINDING | 8891 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74114
30012 | FINDING | Alarm Summary Point should be able to Scan off/on and revert to the driven Alarm group value. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Alarm Summary Point should behave the same as other originated points.<br>1. Tester should be able to take it off scan and put a test value.<br>2. When put back on scan it should revert to the value driven by the Alarm group points.<br> (i.e. Alarm if any in alarm, Return if all in return). <br>Currently, If Summary point is taken off scan while in Alarm and set to return, it will not <br>re-alarm when put back on scan if any of the Alarm group points goes into alarm. (Benzvi, Mati Sep 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19115 (Benzvi, Mati Oct 8, 2012) <br> |  | 35 | FINDING | 8892 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74116
30013 | FINDING | PWSIT - Commissioned FF device with backup LAS does not have a reserved node address per FF specification | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Per FF specification AG-181 on page 48: &quot;The field device with backup LAS enabled shall have the lowest commissioned foundation fieldbus device address.&quot; <br><br>Currently, commissioned FF device node adddresses are auto assigned randomly with lowest address &quot;20&quot; not reserved for backup LAS enabled device. (Phan, Quang Sep 13, 2012) (Hutchison, Steven B. May 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Performed several tests to confirm.<br> 1. Commissioned a backup linkmaster device at node address 20.<br> Had another device commissioned at node address 22. <br><br> 2. Commissioned a backup linkmaster device at node address 21.<br> Had another device commissioned at node address 20. <br><br> 3. Commissioned a backup linkmaster device at node address 35.<br> Had another device commissioned at node address 20. <br><br>In each of the above test cases, and using the 475 Field Communicator, it was noticed that communication continued with the backup link master device in control of the segment. (Morris, Gilbert L. May 23, 2013) <br> |  | 35 | FINDING | 8893 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | [7 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74118
30014 | FINDING | On Host Based Redundancy set up failed Virtual Controller doesn"t force its Host to fail | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On 3.5 EMILY network Drop226 is Primary VCH and Drop227 is Backup VCH. Drop156 is Primary VC tied to Primary VCH Drop226 and Drop157 is Backup VC tied to Backup VCH Drop227. Per specification if Virtual Controller fails, it must also force the Host to fail. But it is observed that if VC Drop156 (in control)fails it doesn&quot;t force VCH Drop226(in control)to fail. Similarly if VC Drop157 (in backup)fails it doesn&quot;t force VCH Drop227(in backup)to fail.Please refer attached snapshot. (Lal, Ramesh Sep 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb 2/18 - Closed: Converted to SDR 19417 (Benzvi, Mati Feb 18, 2013) <br> |  | 35 | FINDING | 8894 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74120
30015 | FINDING | Hide / Show hierarchy in Ovation System Viewer is not working | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Hide / Show hierarchy in OSV is not working (Jayarajan, Jayakumari Sep 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | To hide the hierarchy, please try to unpin the &quot;Ovation System Viewer&quot; on the left side of the window (the tree structure is listed below).<br>To restore the hierarchy, please select the tab on the left (&quot;Ovation System Viewer&quot; ) and repin it.<br><br>I do not believe there is a problem here. (Wozniak, Diane M. Sep 14, 2012)<br><br>JJ(17Sep2012)<br><br>I have tried to unpin the &quot;Ovation System Viewer&quot; on the left side of the window and found it is working so the finding status is changed in to close (Jayarajan, Jayakumari Sep 17, 2012) <br> |  | 35 | FINDING | 8895 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U8 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74122
30016 | FINDING | The operator events are not correct in Historical Reviews for Test mode on/off/good/bad/poor/fair | Burgoon, Frank AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The operator events are not correct in Historical Reviews for Test mode on/off/good/bad/poor/fair when changes are done throgh Point Information or Ovation system viewer (Jayarajan, Jayakumari Sep 14, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Ovation System Viewer (OSV)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Jayarajan, Jayakumari</p> <p><strong>Responsible:</strong> Burgoon, Frank J.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jayarajan, Jayakumari</p> <p><strong>Entry Date:</strong> 2012-09-14T06:05:05-04:00</p> <p><strong>Modified Date:</strong> 2012-10-08T11:28:59-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8896 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74123
30017 | FINDING | Test cases 5.9.4 ,5.9.5 ,5.9.9,5.9.10 of 3.5_SRF1450_ SVTP_rev1.2_JJ need correction | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | As bits from 0 to 7 of packed points are only used by the Distributor Algo to set various i/o conditions. So in test cases bit till 7 should be mentioned (Jayarajan, Jayakumari Sep 14, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Algorithms (ALG)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Jayarajan, Jayakumari</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Jayarajan, Jayakumari</p> <p><strong>Entry Date:</strong> 2012-09-14T06:26:00-04:00</p> <p><strong>Modified Date:</strong> 2012-10-01T12:15:20-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8897 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74124
30018 | FINDING | VC status doesn"t necessarily follow its Host status on Host based redundancy set up | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On 3.5 EMILY network Drop226 is Primary VCH and Drop227 is Backup VCH. Drop156 is Primary VC tied to Primary VCH Drop226 and Drop157 is Backup VC tied to Backup VCH Drop227. Per specification Virtual Controller must monitor the status of host machine. Virtual controller currently in control must reside on the host machine currently in control. But it is observed that Virtual Controller does not necessarily follows the status of Host. For example VC can be in backup whereas Host is in Control.Please refer the attached snapshot. (Lal, Ramesh Sep 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb 2/18 - Closed: Converted to SDR 194187 (Benzvi, Mati Feb 18, 2013) <br> |  | 35 | FINDING | 8898 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74126
30019 | FINDING | VCoordManager GUI doesn"t show the correct status of a Failed Virtual Controller | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | VCoordManager GUI doesn&quot;t show the correct status of a Failed Virtual Controller. For a Failed VC it shows &quot;Running&quot; or &quot;In Alarm&quot;. It is not possible to Stop/Start failes VC from GUI. Please refer attached snapshot for Failed VC Drop148. (Lal, Ramesh Sep 14, 2012) |  |  |  | Test vcoordmanager with a vxsim in failed state. (we can supply information or help to fail a controller if required for testing.) | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added failed state check to vcoordmanager. (Perdeus, Matthew Sep 20, 2012)<br>---<br>msb - Closed; Converted to SDR 19147 (Benzvi, Mati Oct 17, 2012) <br> |  | 35 | FINDING | 8899 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74128
30020 | FINDING | Advanced Virtual Controller not operational | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Advanced Virtual Controller after first download and reboot stops responding. The issue is that drop type set in config.shc is 9 and is not recognized by virtual controller during boot time. This causes vxsim controller become not operational (it&quot;s not pinging and no operation can be executed on that). (Zochowski, Piotr Sep 14, 2012) |  |  |  | Ensure that a drop configured as Advanced Virtual Controller starts up properly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added Advanced virtual controller to valid drop type check. (Perdeus, Matthew Sep 17, 2012)<br>---<br>msb - Closed; Converted to SDR 19148 (Benzvi, Mati Oct 17, 2012) <br> |  | 35 | FINDING | 8900 |  | FINDING | Kossowski, Grzegorz PROCESS PWS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Piotr EMR SYSS RS WRSW | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74130
30021 | FINDING | On host based redundancy the backup VCH fails after taking control for about 10 seconds. | McMaster, James External Artech | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | On 3.5 EMILY network Drop226 is Primary VCH and Drop227 is Backup VCH. Drop156 is Primary VC tied to Primary VCH Drop226 and Drop157 is Backup VC tied to Backup VCH Drop227. It is observed that when Primary VCH Drop226 (in control) is booted, the Backup VCH Drop227 (in backup) takes control but it enters into FAIL mode after about 10 seconds. It happens after each try. (Lal, Ramesh Sep 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Found that the redund.exe process was not in the firewall exception list. This should be investigated. After adding redund.exe to the exception list, the secondary MMI (VCH) is not failing. (Perdeus, Matthew Oct 25, 2012)<br><br>12/27/12:RL - Added redund.exe (Ovation Redundancy Process) in firewall exception list and observed that secondary VCH is not failing. However, redund.exe should be added in the exception list by itself during VCH configuration(it should not be left for the user to do so). This practice is already in vogue for other processes e.g. VController.exe, Vcordinator.exe, Ovation OPC Redundancy Server etc. (Lal, Ramesh Dec 27, 2012)<br><br>The firewall exception list is not maintained by the virtual controller group. Re-assigning to Jim McMaster. (Boehmer, Robert W. Jan 4, 2013) <br> |  | 35 | FINDING | 8901 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | Staab, Randy AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | System Deviation Report to be created | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
30022 | FINDING | In Ovation Error Log, the controller version is not logged upon restart | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Per test case 5.23.2 k) of TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx, the controller version should be logged on restart as OCR400 G01 (for G01 processor group) in the Error Log of configured logging target. <br>I have defined EWS drop233 (Net#7) as 1st logging target for Controller drop#33/83 (OCR400 G01). However, when any of these controller drop 33 or 83 is rebooted, there is no message mentioning the controller version appears in the Error Log. (Gupta, Chandresh Sep 14, 2012) (Gupta, Chandresh Sep 14, 2012)<br><br>cg (10/04/12) - Similarly, logging target for drop38/88 (OCR400 G02) was defined to EWS drop251. However, upon reboot of the drop38 or drop88 the controller version G02 did not appear in the error log of drop251. (Gupta, Chandresh Oct 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | cg (09/16/12) - Per developers comments via email, Product of this finding has been changed to Ovation Controller. (Gupta, Chandresh Sep 16, 2012)<br><br>Added support to log controller type and group number to ocr400/1100. (Christy, Benjamin Oct 8, 2012)<br>---<br>msb - Closed: Converted to SDR 19155 (Benzvi, Mati Oct 19, 2012) <br> |  | 35 | FINDING | 8902 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74134
30023 | FINDING | Testing of Engineering Functions in test case 5.9.2 a) to d) of TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc is NA | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.9.2 a) to d) of TR 3.5_WIN_BASIC_SECURITY_SVTP_rev1.3_CG.doc says &quot;Fail the Primary OSS. Verify that :<br>-the Backup OSS &quot;takes control&quot; and functions correctly<br>-Operator and Engineering Functions operate correctly&quot; <br><br>In IEC, we have 2 separate Ov3.5.0 networks viz. FE350 &amp; FE350C but on the same domain Val9Dc9. DBS drops of both the networks are configured as Domain Controller out of which drop176 (DBS-FE350) is Primary Domain Controller &amp; drop20 (DBS &quot; FE350C) is Redundant Domain Controller. <br>When drop176 is Failed no Engineering Functions could be carried out on FE350 n/w because drop176 is also the DBS of that n/w. Same is the case if drop250 is Failed.<br>Hence, the Engineering portion of testing is Not Applicable. (Gupta, Chandresh Sep 14, 2012) (Capani, Nooch Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - its important that these tests get run. Let&quot;s see if we can have Mati run them in Pgh and you can enter the results in your TR, noting the Pgh system was used. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8903 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74137
30024 | FINDING | P/F/F# Colum is not present in the test case 5.1.6 of 3.5_SRF1633_SVTP_rev1.3_GA.doc SVTP. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | P/F/F# Colum is not present in the test case 5.1.6 of 3.5_SRF1633_SVTP_rev1.3_GA.doc SVTP. (Agarwal, Gaurav Sep 14, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U7 22-AUG-12</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2012-09-14T15:15:35-04:00</p> <p><strong>Modified Date:</strong> 2012-09-14T15:15:35-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8904 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74138
30027 | FINDING | GBNT application crashes while browsing OPC points. | Johnson, Kathy EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | While we browse points in GBNT through OPC Point browser, the application crashes giving error &quot; Ovation GBNT application has stopped working and needs to be closed.&quot;<br>OPC server can only be configured on DBS, hence the above scenario is observed on DBS drop only.<br>Kindly find the attached GBNT Crash - OPC Point browser.jpg (Prasad, Parmatma Sep 17, 2012) | This bug caused GBNT to crash after dragging a new draw item (process pt, bar, trend, etc) if/when the new item used an OPC point. GBNT crashed whether the OPC pt name was manually typed into the entry field on the draw item dialog or whether the user dragged the OPC point name from the OPC Pt Browser dialog. |  |  | Drag an OPC point from the OPC point browser dialog onto the GBNT:ProcessPt dialog. Press OK/Apply and then drag the process pt string on the graphic to position it. This bug caused GBNT to crash when you released the mouse button to complete the drag. GBNT should no longer crash and the PROCESS_PT item should be displayed on the graphic and the source command for it should be displayed in the GBNT:SourceEditor window. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Johnson, Kathy Sep 19, 2012)<br>PP-11/20/2013:the above issue is also exitsting in OV351_U2. (Prasad, Parmatma Nov 20, 2013) <br> 1st: Is GBNT application crashing OR is the browse_pts application within GBNT crashing? You can tell which from a snapshot of the crash error. This finding caused GBNT to crash when user attempted to draw/position a process point item after dragging an OPC point name from the GBNT:BrowseOPCPts dialog to the GBNT:ProcessPt dialog and then pressing OK/Apply from that dialog. I see a new problem in 3.5.1 caused by closing the GBNT:BrowseOPCPts dialog window which causes only the browse_pts application to crash and leaves GBNT OK.<br><br>2nd. You should not re-open a 3.5.0 finding while testing the 3.5.1 release - you should write a new finding, but check if it is indeed the same finding 1st though. I cannot duplicate the original finding... I believe this is a new finding specific to 3.5.1. (Johnson, Kathy Nov 20, 2013) |  | 35 | FINDING | 8907 |  | FINDING | Prasad, Parmatma EMR SYSS PWS NOIDA | [9 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74143
30028 | FINDING | Test case 5.8.6 "SIS - Allow test mode on-off" in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc is NA | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.8.6 in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc says to test &quot;SIS - Allow test mode on-off&quot;. However, as per dev. comments in F#7591, the SIS Test Mode security rule was not meant to be used by the Operator Station Programs (Point Information, Point Review, and Alarms). This stands as is for 3.5.0 release as well. <br>Hence this test case is NA for both Local as well as Remote Security System Functions. (Gupta, Chandresh Sep 17, 2012) (Gupta, Chandresh Sep 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - removed from STUDIO_SVTP_Rev3.6, noted as NA in STP rev 1.3. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8908 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74145
30029 | FINDING | Fourth digital variable test for Hi P AI module in "3.5_CONTROLLER_SVTP_rev4.5_xx.docx¿ needs to be marked NA. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In ¿3.5_CONTROLLER_SVTP_rev4.5_XX.docx¿ SVTP, Test case 5.6.1.3 (Local) and 5.6.3.3 (Remote) for verification of all Hi P AI module multivariable Values.<br>To perform test, Temperature device (3144T) connected to Hart Hi P AI module.<br>Observation is, Fourth digital variable not updated in Point info, shows BAD status. AMS Device Manager (AMS 11.5) shows fourth variable as &quot;Not Used&quot;. For reference ¿AMS 3144T-AI FDV.jpg¿ screenshot is attached. Above test cases need to be marked NA. (Pandey, Vijay Sep 18, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U8 14-SEP-12</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2012-09-18T04:44:09-04:00</p> <p><strong>Modified Date:</strong> 2012-09-18T04:44:09-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8909 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74146
30035 | FINDING | Unable to tune enumerated mode block parameter values | McMaster, James External Artech | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Enumerated function block parameter values (MODE_BLK__TARGET, MODE_BLK__NORMAL) cannot be configured using tuning dialog. (Christoforetti, Matthew M. Sep 18, 2012) |  |  |  | Open tuning dialog for a function block and verify MODE_BLK__TARGET and MODE_BLK__NORMAL are configurable. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Sep 18, 2012) <br> |  | 35 | FINDING | 8915 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | ? |  |  | FINDING | [6 empty] | 89600
30036 | FINDING | Missing status dialog when downloading/uploading function block parameters. | McMaster, James External Artech | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-12-10 09:35 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | As per suggestion from projects, the function block upload/download processes needs a status dialog as it was provided in old FET. (Christoforetti, Matthew M. Sep 18, 2012) |  |  |  | Perform function block download/upload; verify proper status dialog appears. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. (Christoforetti, Matthew M. Sep 18, 2012) <br> |  | 35 | FINDING | 8916 |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | ? |  |  | FINDING | [6 empty] | 89600
30038 | FINDING | In point alias Description field we can give more than 16 character | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In point alias Description field we can give more than 16 characters but as in online help it is mentioned that user can give 16 character name but at present it is going up-to 24 character .so online help require updating. (Sharma, Vaibhav Sep 19, 2012) | LC 11/16/2012: Updated the Point Alias field to specify that it will take a 24-character name. |  |  | LC 11/16/2012: Look at the topic called, &quot;Point tab field description.&quot; It is in the chapter on Creating Points in the Developer Studio. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 09/19/12: Please be more specific -- what manual/application are we talking about? Graphics Builder? Developer Studio? Operator Station? Please advise. (Casteel, Linda Sep 19, 2012)<br><br>LC 09/19/2012: Ok. I understand now. I see the screen shot you attached. (Casteel, Linda Sep 19, 2012)<br><br>LC 11/16/2012: Updated a topic called, &quot;Point tab field description.&quot; It is in the chapter on Creating Points in the Developer Studio. Updated the Point Alias description in the tables to say that it can take 24 characters. This fix can be found in OW350_60.pdf in Q:\Communication\Tech Comm\Share\Validation. (Casteel, Linda Nov 16, 2012) <br> |  | 35 | FINDING | 8918 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Sharma, Vaibhav PROCESS PWS NOIDA | [8 empty] | Implementation | OW350_60_NOV_16_12 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74164
30039 | FINDING | Distributor algo symbol in ctrl builder not matching with the symbol in help details | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Distributor algo symbol in ctrl builder not matching with the symbol in help details (Jayarajan, Jayakumari Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 09-19-2012: Works as Designed -- no plans to fix. The algorithms symbols in the manual are not designed to match the Control Builder. The manual specifies the symbol as a &quot;functional symbol&quot; meaning that it is only representing the possible pins and pin locations. The Algorithm table gives more information on additional pins that can be added. Also, the Control Builder is such that the user can build their own symbols. (Casteel, Linda Sep 19, 2012) <br> |  | 35 | FINDING | 8919 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74166
30040 | FINDING | SVTP: Delete ¿enhanced button " in 5.22.3 Test of SVTP "SRF1421_SVTP_rev1.2.docx" | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | As no button is available for this enhancement. So ¿Help for enhanced button is available ¿ should be deleted and replaced with &quot; Help for enhancement is available.¿ in 5.22.3 Test of SVTP &quot;SRF1421_SVTP_rev1.2.docx&quot; . (Singh, Ghanshyam Sep 19, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN GB (WGB)</p> <p><strong>Release Level:</strong> 3.5.0_U8 14-SEP-12</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2012-09-19T02:17:04-04:00</p> <p><strong>Modified Date:</strong> 2012-09-19T02:17:04-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8920 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74167
30041 | FINDING | Help button for "SRF 1421 2.25 Support for string manipulation functions for ascii-type variables" is not working. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Help button for &quot;SRF 1421 2.25 Support for string manipulation functions for ascii-type variables&quot; is not working. (Singh, Ghanshyam Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I assume you mean that the Help button on the GBNT:ApplicationPrograms gui is not working when any of the variable string functions is selected? Is this correct? Also, I noticed that the help does not work when the Set_variable program is selected ... (Johnson, Kathy Sep 19, 2012)<br><br>GS: Yes, you are correct. Help is not available for both the above mentioned programs. (Singh, Ghanshyam Oct 1, 2012) <br> |  | 35 | FINDING | 8921 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74170
30042 | FINDING | Can not deselect the Toolbars option in Ovation Point Review. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | This issue is similar to finding#8779.<br>In Ovation 3.5.0 following steps are performed: Open Ovation Point Review---&gt;Click on Start and let points come---&gt;Right click on the bottom side Ready row bar---&gt;click on Customize... Here we can not deselect the Toolbars option &quot;Status&quot;.<br>Please find the attached snapshot for reference. (Mitra, Sambuddha Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Create SDR (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19116 (Benzvi, Mati Oct 8, 2012) <br> |  | 35 | FINDING | 8922 |  | FINDING | [10 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74172
30044 | FINDING | Print screen function wrongly updated in developer studio | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Print screen function wrongly updated in OvPtStudio350 book (developer studio help)and needs to be removed from the same.<br>As print screen function comes under ovation operator utility function, so it should be updated in Ovation utilities of OvationApplication book. (Singh, Ghanshyam Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SJ 29 Nov 2012: I have added the Print screen utility as a shared topic from the Developer Studio book. (Jain, Swati Nov 29, 2012)<br>---<br>msb - Closed; Converted to SDR 19267 (Benzvi, Mati Nov 29, 2012) <br> |  | 35 | FINDING | 8924 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74176
30045 | FINDING | Location provided for Ovation System Viewer application is wrongly mentioned in help. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Open OSV, go to help, opens OvationApplication online help. Here it is mentioned that to access OSV, open &quot;Ovation Utilities&quot; and click on System viewer icon.<br>The path should be &quot;Ovation Application&quot; folder and click on System viewer icon. (Sachan, Pallavi Sep 19, 2012) | SJ September 24, 2012: The OvationApplication online help has been updated. |  |  | SJ September 24, 2012: The OvationApplication online help has been updated. Please see the U9 build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SJ September 24, 2012: The OvationApplication online help has been updated. Please see the U9 build. (Jain, Swati Sep 24, 2012)<br><br>Found Fixed in U9. Hence Finding closed. (Sachan, Pallavi Sep 28, 2012) <br> |  | 35 | FINDING | 8925 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.0_U9 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74178
30046 | FINDING | Online help looks for path in 64 Bit EWS and DBS. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Online help looks for path in 64 Bit EWS and DBS .Click on online help in Ovation Application .This operation looks for HH.exe file then ask for &quot;Fix it&quot;. Once click on &quot;fix it&quot; the it searches the HH.exe file and produce online help. (Singh, Ghanshyam Sep 19, 2012) (Burgoon, Frank J. Oct 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Create SDR. (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19119 (Benzvi, Mati Oct 9, 2012) <br> |  | 35 | FINDING | 8926 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74180
30047 | FINDING | Online help has no mention of SureService Ovation System Registration Utility. | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OvationApplications -&gt; Online Help -&gt; Index -&gt; Ovation Utilities. This has no mention for &quot;SureService Ovation System Registration Utility&quot; (seen only on DBS drops). (Sachan, Pallavi Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed; Converted to SDR 19335 @ 11-Jan-2013 (Benzvi, Mati Jan 11, 2013) <br> |  | 35 | FINDING | 8927 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74182
30048 | FINDING | Help buttons not linked in Ovation Developer Studio | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | A few help buttons not linked in Developer Studio:<br>1) Ancillary labels (Error message shown on clicking the help button)<br>2) Master Virtual Controller Host (Error message shown on clicking the help button)<br>3) Sis Logger ( The help file is not updated as per current release) (Khanna, Anant Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 11/16/2012: This may take some time to research and fix. Create SDR and move to next release - 3.6. (Casteel, Linda Nov 16, 2012)<br>---<br>msb - Closed: converted to SDR 19256 (Benzvi, Mati Nov 26, 2012) <br> |  | 35 | FINDING | 8928 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74184
30049 | FINDING | Excessive time taken to get the filtered points in Historical Review | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It has been observed that if a user opts to filter points in Historical Review, as soon as the user enters the time range and starts the filter operation (keeping the point filter as */*), the CPU usage and memory usage of the application &quot;HistReview.exe&quot; is increased (at times it reaches the 220,000K mark)<br>The filter process is slow only in case of filtering points. (Filter by all option i.e. */*)<br>Eg: A time difference of 1 minute was given between the start time and end time, it took roughly 6.5 mintues to get the filtered results of 1134 points.<br>Whereas the filter results in Alarm, SOE, Operator Events and ASCII are shown at a fast pace. (Khanna, Anant Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | [JLC 9/19/12]<br>Review retrievals for large point quantities should be expected to take significant time to complete. How does this response time compare to previous releases? (Contento, James L. Sep 19, 2012)<br><br>[ANK 9/20/12]- In the previous build (U7), the point review retrieval was much faster.<br>The above stated example which is taking 6.5 minutes in U8 would complete in roughly 2-3 minutes in U7. I request you to kindly re-check the same at your end. (Khanna, Anant Sep 19, 2012) <br> |  | 35 | FINDING | 8929 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74186
30051 | FINDING | Bit details of bit 25 "Alarm Reinhibit" in 1W status word need to be added for all Record type points | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Bit details of bit 25 &quot;Alarm Reinhibit&quot; in 1W status word need to be added for all Record type points. Help file mentions it but when seeen in PI the same is not available. (Gupta, Chandresh Sep 19, 2012) (Gupta, Chandresh Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Create SDR. (Burgoon, Frank J. Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19123 (Benzvi, Mati Oct 10, 2012) <br> |  | 35 | FINDING | 8931 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74190
30052 | FINDING | Bit details for 2, 3 & 29 of 1W status word needs to be added in Help file | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following Bit details need to be added for 1W status word in the Help document:<br>- Bit 2 &amp; 3 information &quot;Sensor Alarm - indicated when bits 2 &amp; 3 are set&quot; for LD, DD, LP, DP, RM &amp; RN record type point.<br>- Bit 29 information &quot;Out Of Service&quot; for RN record type point. (Gupta, Chandresh Sep 19, 2012) | PS (Jan 14, 2013): Updated bits 2, 3, and 29 information of the 1W record fields for the LD, DD, LP, DP, RM &amp; RN points SJ (Oct 15,2013): Updated the bits 2, 3, and 29 information of the 1W record fields for the LD, DD, LP, DP, RM &amp; RN points for the online help. |  |  | PS (Jan 14, 2013): Refer to OvationApplications.chm placed at the following path: SourceIntegrity(\\USPIT-FP03)(M:)\TechWriters\3.5CHMs\OvationApplications.chm SJ (Oct 15,2013): -&gt; Updated the Record Types online help as follows: --&gt; Bits 2 &amp; 3 information of the 1W record fields for the LD, DD, LP, DP, RM &amp; RN points --&gt; Bit 29 information of the 1W record fields for the RN point. Check the OvationApplications.chm online help in the next build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SJ Sept 20, 2012: Transferring the finding to Linda Casteel. Please update OW350_R1140 book. (Jain, Swati Sep 20, 2012)<br><br>LC 09/20/2012: If this information belongs in the Record Types book, this Finding should be assigned to Puneet. (Casteel, Linda Sep 20, 2012) <br> PS (Jan 14, 2013): Updated the following in the Ovation Records Type Reference Manual:<br>-&gt; Bits 2 &amp; 3 information of the 1W record fields for the LD, DD, LP, DP, RM &amp; RN points<br>-&gt; Bit 29 information of the 1W record fields for the RN point (Sharma, Puneet Jan 14, 2013)<br><br>cg (10/14/2013) - Finding is fixed in user manual OW350_R1140.pdf. However, online Help still has the same issues as mentioned in the Description field above. Hence, marking this finding as Open (Failed Retest) and chaging the Action field to DRR. (Gupta, Chandresh Oct 14, 2013)<br><br>PS (14-Oct-2013): Assigning the finding to Swati, as she is assigned with the Record Types book in Ovation 351 release. (Sharma, Puneet Oct 14, 2013)<br><br>SJ (Oct 15,2013): -&gt; Updated the Record Types online help as follows:<br>--&gt; Bits 2 &amp; 3 information of the 1W record fields for the LD, DD, LP, DP, RM &amp; RN points<br>--&gt; Bit 29 information of the 1W record fields for the RN point.<br>Check the OvationApplications.chm online help in the next build. (Jain, Swati Oct 16, 2013)<br>cg (11/7/13) - Finding retested in U2 build. Now, online help is also ok. Hence finding closed. (Gupta, Chandresh Nov 7, 2013) |  | 35 | FINDING | 8932 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | Ovation 3.5.0, 3.5.1_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74192
30053 | FINDING | Invoking Trace properties in Live trend changes the duration of the running trend. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On Behalf of Prashant:<br>Following steps is done to recreate the issue :<br>a.Set the Live Trend duration to 30 min or more (other than 10 min).<br>b.Invoke Trace Properties dialog.<br>c.Click OK.<br>d.The trend duration now becomes 10 min. (Kumar, Shailendra Sep 19, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | [JLC - 09/24/2012]<br>Please track this via SDR. (Contento, James L. Sep 24, 2012)<br>---<br>msb - Closed: Converted to SDR 19046 (Benzvi, Mati Sep 25, 2012) <br> |  | 35 | FINDING | 8933 |  | FINDING | Bargaje, Prashant C EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74194
30058 | FINDING | GBNT:Multi TrendPtColorCond Failed | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When a specific color condition is assigned to multi points of multi trend in GBNT:trend, Multi-Trend window, system shows error and failed to run ON-LINE grafics.<br>please refer to snapshot. (Kumar, Sudheer Sep 20, 2012) (Kumar, Sudheer Sep 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed graphics to handle multi trend color conditionals correctly. (Spillane, Donal A. Oct 11, 2012)<br>---<br>msb - Closed; Converted to SDR 19131 (Benzvi, Mati Oct 13, 2012) <br> |  | 35 | FINDING | 8938 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74204
30059 | FINDING | PROFIBUS module points go to Sensor Alarm when OCR reboot occurs. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 39/89 (EMILY) is configured with PROFIBUS. RM points assigned to PROFIBUS modules go into Sensor Alarm for approximately 20 seconds when a controller reboot is performed. Might this be related to Finding 8765?<br><br>This has not been observed with DeviceNet. (Brown, Sean Sep 20, 2012)<br><br>Unable to replicate with U9. In addition, several changes were made post U9 that will be released in a patch. There were issues involving shell configuration, shell priority set to 1, and debug messages spamming the console that were corrected. Retest with the patch. (Ciccozzi, Anthony Oct 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19183 (Benzvi, Mati Oct 24, 2012) <br> |  | 35 | FINDING | 8939 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Plymire, Alvan AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74206
30060 | FINDING | After pressing the "Print Advance" option, after some time Printer stop printing. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | 1:- Configured the alarm Printer &amp; reboot the drop.<br>2:- After rebooting the system, Open the alarm window, Alarm start printing with regular alarm.<br>3:- In Alarm window, go to &quot;print Advance&quot; option &amp; press it.<br>4:- After some time, Printer stop printing. Wait for more than 10 min but Printing does not start .<br><br>Note:- In alarm window ,alarm is continuously updating with current time. (Agarwal, Gaurav Sep 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19124 (Benzvi, Mati Oct 10, 2012) <br> |  | 35 | FINDING | 8940 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74208
30061 | FINDING | No more than four Numa-Logic EIO modules will boot up (dhcpinfo entries are missed). | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 43/93 (EMILY) is configured with six EIO nodes. No more than four will boot up successfully (the others keep rebooting).<br><br>The system has functioned correctly for over a year on the Ovation 3.4.0 NUMALOG1 system, so this is not due to cabling, switch configuration, faulty EIO modules etc.<br><br>It has been observed that no more than four dhcpinfo entries are being used. All six pairs of EIOs can be made to eventually boot by iteratively commenting out all but four entries, downloading and rebooting the OCRs. (Brown, Sean Sep 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | See finding 7694. The same issue came up with 3.4 and we added 8 DHCP entries to allow 4 additional Numalogics. I am changing this to a cat 3 since up to 4 Numalogics work correctly. (Boehmer, Robert W. Sep 20, 2012) <br> |  | 35 | FINDING | 8941 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74210
30062 | FINDING | After controller boot message appear in Ovation error log N1 & N4 port up even though those are not connected. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following are the observations regarding N1 &amp; N4 .<br><br>1.N4 port of Drop1/51 (OCR 400-SIS system) is used for Control syncronization or can be <br> configured for Third party communication through custom networking.<br>2.N1 port is not configured.<br>It is observed whenever drop1 or 51 is booted then in ovation error log message appears N1 up &amp; N4 up when drops comes on highway even though N1 &amp; N4 port is not connected. (Sahay, Madhukar Sep 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19141 (Benzvi, Mati Oct 15, 2012) <br> |  | 35 | FINDING | 8942 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74212
30065 | FINDING | For Historical Trend, When MOVE DOWN menu is used,it does not appear in TREND. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On behalf of Prashant:<br>For Historical Trend, When MOVE DOWN menu is used to move an item to LAST position, that item does not appear in TREND.<br><br>1)Make sure that &quot;Show Fully Qualified Name&quot; is YES.<br><br>2)Do &quot;New Historical Trend&quot;. It will show DESIGN mode.<br><br>3)Use POINT BROWSE to add say 3 points.<br><br>4)Right click on second point in DETAILS PANEL and click &quot;MOVE DOWN&quot; in the context menu.<br><br>5)Click on &quot;BEGIN&quot;.<br><br>6)LAST point, does not appear on Trend. (Kumar, Shailendra Sep 21, 2012) (Contento, James L. Sep 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: coverted to SDR 19047 (Benzvi, Mati Sep 25, 2012) <br> |  | 35 | FINDING | 8945 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74218
30066 | FINDING | Browse Point does not work if DisplayUnqualifiedPointNames is true. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On Behalf of Prahant:<br>If &quot;DisplayUnqualifiedPointNames&quot; is configured as true for Point Names, and user tries to add points using BROWSE dialog (data source = Ovation Point Directory) (both from ribbon bar and Trace Properties dialog), TREND does not show up for these points. This applies to LIVE as well as HISTORICAL trend.<br><br>To verify this bug, the point names should show up as unqualified in Browse dialog. (Kumar, Shailendra Sep 21, 2012) (Contento, James L. Sep 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | [JLC 09-24-2012]<br>Please track as SDR. (Contento, James L. Sep 24, 2012)<br>---<br>msb - Closed: Converted to SDR 19048 (Benzvi, Mati Sep 25, 2012) <br> |  | 35 | FINDING | 8946 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74220
30068 | FINDING | Progress bar not functional in Historical Review | Contento, James AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The Historical Review progress bar presnt on the bottom right corner is not operational.<br>Once a user sets the desired filter/ time frame and initializes the historical review operation, the point initialization progress bar present on the bottom right of the screen does not display the progress status. (Refer to the snapshot1.jpg)<br>Whereas, in other Ovation applications, the progress bar is working fine. (Refer to snapshot2.jpg) (Khanna, Anant Sep 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | [JLC - 9/21/2012] Former Historical Review did not show progress either. Retrieval progress is not provided by the OPH server and therefore cannot be displayed at GUI. (Contento, James L. Sep 21, 2012)<br><br>[ANK - 9/26/2012] If the same cannot be implemented in the GUI, then what is the need of having a progress bar in the historical review UI ? At present one sees a blank progress bar on the right bottom corner. (Khanna, Anant Sep 25, 2012)<br><br>Progress bar removed in patch version. (Contento, James L. Nov 12, 2012) <br> |  | 35 | FINDING | 8948 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | OVA350_Patch. OPH340 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74224
30069 | FINDING | A Numa-Logic EIO RNC failure caused both controllers to fail. | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 43/93 (EMILY) is configured so that a loss of an RNC will cause a controller failover. 43 was in Control; 93 was in Backup. The Ethernet cable was removed from the N1 port of 43. 43 failed as expected, but 93 failed after taking control with a DPU timeout error.<br><br>The Error Log messages are attached. (Brown, Sean Sep 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - close, track as SDR 19060. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8949 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74226
30070 | FINDING | In Trend, Unable to filter real & Digital data type together from Point Browse window. | Contento, James AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | 1:- Open the trend window &amp; Press Add Option to add points.<br>2:- Specify point Information window will open.<br>3:- Open the Point Browse window in Point name option.<br>4:- Select the Historian Point Source.<br>5:- Select the Real &amp; Digital Data type together.<br>6:- Press Start. None of the points are found. <br> As shown in screen shots &quot; None of the points are found.jpg&quot;.<br><br>Note:-<br> This issue is occur, when select any two combination together (e.g.:- real &amp; Digital, Digital &amp; Packed etc.). (Agarwal, Gaurav Sep 21, 2012) (Contento, James L. Sep 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is the same as Finding #8985. (Contento, James L. Oct 19, 2012) <br><br>It is being tracked via SDR #19157. (Contento, James L. Nov 12, 2012) <br> |  | 35 | FINDING | 8950 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74229
30071 | FINDING | Test cases 5.1.14 and 5.6.3 of SVTP 3.5_VxSIM_VC_SVTP_Rev2.0_RL can not be performed | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Advanced Control Algorithm support (APC Toolkit) for Virtual Controller is not available in 3.5 release. Therefore, Test cases 5.1.14 and 5.6.3 can not be performed. These should be considered as Not Applicable. (Lal, Ramesh Sep 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - STP rev 1.3 notes 5.1.14 and 5.6.3 of SVTP 3.5_VxSIM_VC_SVTP_Rev2.0 are N/A. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8951 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74231
30072 | FINDING | After changing Users password from Security Manager--&gtManage Database Users, OSR 1.3 Utility does not collect data | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Following steps were performed:<br>1. Changed the password of &quot;ptadmin&quot; user from default &quot;ptadmin&quot; to &quot;ptadmin1&quot; thru [Manage Database Users] option in Ovation Security Manager window.<br>2. After that, tried to collect data using &quot;SureService Ovation System Registration Utility 1.3&quot;.<br>However, it is giving error &quot;Failed to retrieve the drop list......&quot; &amp; collection stops.<br>Please refer the attached snapshot file MDU-OSR-error.jpg for the error. (Gupta, Chandresh Sep 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013)<br><br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 8952 |  | FINDING | Base, Olivia AUTOSOL MNL | Gupta, Chandresh EMR SYSS PWS NOIDA | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74233
30073 | FINDING | ovation manual OW331_60 need correction | Gola, Megha EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | 3.6.0_U2 |  |  | 2015-12-10 23:37 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation manual &quot;OW331_60&quot;, &quot;page 137&quot;, &quot;To Insert an I/O Device in an Ovation Drop&quot;, topic no 5 &quot;Select the I/O Device Number from the drop-down list (0 [for IOIC], 5-9 [third-party and Bus].) Here &quot;5-9&quot; should be &quot;5-11&quot; as shown in developer studio.<br><br>This is against SDR 17874. (Joshi, Parmesh Sep 22, 2012) | <p>LC 11/16/12: Updated the manual to present the correct available device numbers.</p><p><br></p><p>MG 12/11/2015:&nbsp;&nbsp;It is updated in the manual.</p> |  |  | LC 11/16/2012: Check the topic called, &quot;To insert an I/O Device in the Developer Studio&quot; (Step 4). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>LC 11/16/12: Created a topic called, &quot;To insert an I/O Device in the Developer Studio.&quot; In this topic, step 4 says, &quot;Select the I/O Device Number from the drop-down menu. The choices are: 0 for IOIC and 5 - 11 for third-party and Bus devices.&quot; This fix can be seen in OW350_60.pdf in Q:\Communication\Tech Comm\Share\Validation. (Casteel, Linda Nov 16, 2012)<br><br>LC 08/27/2012: Retest in Ovation 3.5.1, U1 build. (Casteel, Linda Aug 27, 2013) </p><p><br></p><p>MG 12/11/2015:&nbsp;It is available in the manual. Check section &quot;9.3.2 To insert an I/O device in the Developer Studio&quot; bullet no. 4 of Developer Studio manual.</p><b><p><br></p><font size=3><p><br></p><p><br></p></font><p><br></p></b><p><br></p><p><br></p> |  | 35 | FINDING | 8953 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.1_U1, 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Not Critical for This Release | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  | MG 12/11/2015:&nbsp;Update in the manual.&nbsp;Check&nbsp;3.6.0 U2 build. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 112961
30074 | FINDING | Operator and Engineer icons (graphics, Historian,Dev studio) are not coming at desktop pan for some systems. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When we open Graphics, Historians, developer studio,Trends, point Info etc, their icons are not coming properly at desktop pan.This happened in some of the systems after ov 3.5.0_U9 installation (win32 and win64).<br><br>please find attached snapshot of icons and remote login details of one of the affected system (drop247) (Gupta, Chandresh Sep 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I have not been able to reproduce this. None of the workstations in the Pittsburgh validation lab exhibit this behavior. When logging in remotely to the 40.247 machine the icons appear correct. This may be the result of some local configuration. Try to determine what the affected machines have in common, or what is different from the unaffected machines. (Burgoon, Frank J. Oct 2, 2012)<br><br>cg (10/03/12) - The mentioned issue occurred on 3-4 drops out of 17 drops in IEC during U9 upgradation. Some of the drops are W7 (32-bit) &amp; some are W7 (64-bit). So it is hard to say about the difference between them &amp; the normal drops.<br>After changing/updating Windows desktop screen or reboot of the drop, the icons appeared OK.<br>Today, we tried to recreate the issue again by uninstalling U9 &amp; reinstalling it back but was not successful. The mentioned issue appeared during upgradation from U8 to U9. (Gupta, Chandresh Oct 3, 2012) <br> IC 10/25/12 - closing as CND. Val can reopen if issue re-occurs. (Capani, Nooch Oct 26, 2012) |  | 35 | FINDING | 8954 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74237
30075 | FINDING | After EWS upgradation with U9, Operator Functions Security & PSG remain [Disabled] as seen in Ovation Session Manager | Burgoon, Frank AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Ovation drops were upgraded with U9. However, after upgradation when EWS drop comes up for the first time the Operator Functions Securities &amp; Point Security Groups appear [Disabled]. Please refer attached snapshot file. Due to this issue several options in right click context menu of Developer Studio remain greyed out in these drops.<br>After 1-2 reboots of the drop these Securities become [Enabled].<br>The above behavior is inconsistent but was visible on 5-6 EWS drops out of 15 in IEC. (Gupta, Chandresh Sep 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | In Event Viewer/Applications and Services logs/Ovation there may be messages related to OvSecSyncMan during the time where this behavior was observed. See if you can find these messages and report them. This will need to changed to an SDR. (Burgoon, Frank J. Oct 2, 2012)<br><br>cg (10/03/12) - Eventviewer snapshot files are attached. It contains details of events occurred related to SecSyncMan &amp; OvationOnlineSynchronizer. (Gupta, Chandresh Oct 3, 2012)<br><br>First we&quot;ll change this to an SDR. We will set the SDR to &quot;monitoring&quot;. When one sees this behavior collect the Event Viewer logs noted above, from both the computer exhibiting the behavior and the primary domain controller, and provide them to product development. (Burgoon, Frank J. Oct 9, 2012) <br> |  | 35 | FINDING | 8955 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | System Deviation Report to be created | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74239
30077 | FINDING | Test Case 5.13.12 of SVTP ¿3.5_WIN_OPCON_SVTP_rev2.H_RS.doc¿ needs to be updated. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The below Test Case of SVTP ¿3.5_WIN_OPCON_SVTP_rev2.H_RS.doc¿ defines as- <br>&quot;5.13.12 Test: When the user selects a control sheet from the navigation tool the Signal Diagram highlights all algorithms on the sheet where that point is used. ¿<br>Whereas in this case Signal diagram highlights only the algorithm on the sheet where that point is originated. (Singh, Rajan Sep 24, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Singh, Rajan</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Singh, Rajan</p> <p><strong>Entry Date:</strong> 2012-09-24T02:58:11-04:00</p> <p><strong>Modified Date:</strong> 2012-09-24T02:58:11-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8957 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74243
30079 | FINDING | Ov3.5.0 Trend(Live and Historical) of Ov3.4.0 points shows description upto 15 characters. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Ov3.5.0 Trend(Live and Historical) of Ov3.4.0 points shows description upto 15 characters only it truncates the chararcter above then 15 characters.Tested on Win7 64 bit machine. (Kumar, Shailendra Sep 24, 2012)<br><br>Seems Ok now hence closing.Will monitor for future. (Kumar, Shailendra Sep 24, 2012)<br><br>Again recreated hence reopened the finding.<br>Basically steps are :<br>1)Open Historical Trend ,Click Set button, change start time- end time and then click &lt;Begin&gt;.This will correctly show the trend with description(refer attached Trend_OK.jpg)<br>2)In same Trend Again click Set button, change start time- end time and then click &lt;OK&gt;,in Trend it gives message &quot;Please Click Begin to start the Trend&quot;.<br>3)Now click &lt;Begin&gt; from menu option after while it shows Point with 15 character and sometimes Blank description.It is not specific to any point or duration.Bacically Sequence of operation --&gt;<br> &lt;Set&gt;&lt;OK&gt;&lt;Begin&gt; is creating problem.&lt;Set&gt;&lt;begin&gt; does not create problem.<br>For reference attached is the snapshot(refer attached Trend_NOT_OK.jpg).<br><br>Also attached is the remote login step to OPH drop231. (Kumar, Shailendra Oct 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19200 (Benzvi, Mati Oct 26, 2012) <br> |  | 35 | FINDING | 8959 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74247
30080 | FINDING | Update time of SIS I/O depends on load of control tasks |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When measuring time required for change of SIS input channel to propagated to Ovation Highway it was observed that this time depends on quantity of logic executing in control tasks. For heavy loaded controller (avarage execution time of control task 2 ~800ms) update time was delayed or, when there was a lot of input channels configured (~1000), values was lost because receive buffer was full. (Czak, Jakub Sep 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Below issue occured because during execution of control task sisio task (one responsible for receiving I/O data and setting points values) didn&quot;t get any of CPU time. Since there was a lot of channels configured to update value and status in 100ms interval, receive buffer was easily filled up.<br><br>Following fix was implemented:<br>- sisio task was splitted into two tasks with high and low priority. High priority task handles receiving of I/O data and sets values and qualities of SIS I/O points. Its priority is equal to control task 1<br>- sending of I/O data from SDS was optimized. SDS sends update only if there was change in value or quality. (Czak, Jakub Sep 24, 2012) <br> |  | 35 | FINDING | 8960 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74249
30082 | FINDING | It is not possible to configure SIS device for VxSim controller. | Perdeus, Matthew AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | After adding SIS driver and SIS I/O device and downloading controller error is reported: <br>IO_get_config_info: Unsupported driver found - change to none<br>Vxsim controller is expecting io type to be &quot;dl&quot; but in driver.cfg file in entry for SIS driver io type is &quot;sisio&quot;. When I manually changed that entry it still wasn&quot;t working. In other place (__IO_config_info_process function in io_base.c file) controller is expecting &quot;sisio&quot; (or other dl driver) as io type. (Czak, Jakub Sep 24, 2012) (Perdeus, Matthew Sep 25, 2012) (Perdeus, Matthew Oct 23, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Allow use of SIS I/O driver in virtual controller. (Perdeus, Matthew Oct 23, 2012) <br> |  | 35 | FINDING | 8962 |  | FINDING | [10 empty] | Implementation | OVA350005 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74253
30084 | FINDING | TR "3.5_U9_BASIC_FUNCTIONS_SVTP_rev1.M" needs some modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.15.1.(f) of &quot;TR 3.5_U9_BASIC_FUNCTIONS_SVTP_rev1.M&quot; says :-<br>Verify the module and its devices communicate mormally after the FW update.<br>Here the word &quot;mormally&quot; has a typo, it should be replaced with word &quot;normally&quot;. (Sahay, Madhukar Sep 24, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2012-09-24T16:26:46-04:00</p> <p><strong>Modified Date:</strong> 2012-09-24T16:26:46-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8964 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74256
30086 | FINDING | RLogin should be disabled on Ovation3.5 U8 | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | From Ovation 3.5 U8 build, Telnet had been disabled for increasing the security, but we are able to login to the controllers through RLogin using Putty or Plink by providing any username without any password. RLogin protocol should be disabled or atleast password protected. (kant, krishna Sep 25, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Removed rlogin from ocr400 (Christy, Benjamin Sep 26, 2012)<br>---<br>msb - Closed: Converted to SDR 19140 (Benzvi, Mati Oct 15, 2012) <br> |  | 35 | FINDING | 8966 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Goel, Prakhar EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jankowiak, Michael AUTOSOL DX WRSW | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Kossowski, Grzegorz PROCESS PWS WRSW |  |  | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74260
30087 | FINDING | Help file needs to be corrected regarding "Allen-Bradley driver". | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation Developer Studio, Help file is not showing correct information regarding &quot;Allen-Bradley driver&quot;.<br>Please find the attached JPEG file, in which the red marked words to be corrected.<br>1. Instead of PLC, PAC should be used.<br>2. Instead of ControlLogic, ControlLogix should be used.<br>3. Instead of MicroLogic, MicroLogix should be used. (Mitra, Sambuddha Sep 25, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 11/14/2012: Assigned to Ron Skena. This information is in the Controller book. (Casteel, Linda Nov 14, 2012)<br><br><br>Notations to PLC (programmable logic controller), ControlLogic, and MicroLogic will corrected in the next release of the Controller manual. (Skena, Ronald E Nov 14, 2012) <br> |  | 35 | FINDING | 8967 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74262
30088 | FINDING | In non-redundant VCH failover to backup controller does not take place if Primary VCH drop goes into Fault mode | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | There are two non redundant VCHs on 3.5 SIS Network Drop139 and Drop137. VCH Drop139 is hosting Primary Virtual Controller Drop142, Drop143 and VCH Drop137 is hosting Partner Virtual Controller Drop162, Drop163 respectively. When VCH Drop137 is in Fault mode its Virtual Controller i.e. Drop142,Drop143 remain in control, they do not failover to their corresponding backup controllers Drop162,Drop163. Similarly when VCH Drop139 is in Fault mode its Virtual Controllers i.e. Drop162,Drop163 remain in control, they do not failover to their corresponding backup controllers Drop142,Drop143. This behavior in contrary to the functional specification, please refer test case 5.5.2 which states that &quot;failover to backup controller takes place if Primary Virtual Controller Host drop goes into Fault mode&quot;. Please refer the attached snapshot. (Lal, Ramesh Sep 25, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The virtual controllers run independent of the VCH status in non-redundant VCH configurations as per test case 5.5.7. Test case 5.5.2 should not state &quot;Host&quot; in item 1. This should be &quot;Primary Virtual Controller drop goes into fault mode&quot;. (Perdeus, Matthew Sep 26, 2012)<br><br>9/27/12:RL - Based on Dev&quot;s comment this finding is closed and a new finding is written against<br> SVTP. (Lal, Ramesh Sep 27, 2012) <br> |  | 35 | FINDING | 8968 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74264
30089 | FINDING | Points review is crash, during reviewing more than 90K points. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Drop:- Drop126<br>Os:- Win7-64bit<br>Ov:- Ov3.5.0<br><br>Step followed:-<br>1:- Open the Point review &amp; go to filter tab.<br>2:- Configured the filter.<br>3:- Press start button.<br>4:- searching is started.<br>Iit is observed that when points goes into above 90K &amp; it is going into reviewing state, point review is crashed.<br><br>For more information please find the attached screen shots&quot; Point review cresh.jpg&quot; &amp; &quot;Point Review Error details.txt&quot; file. (Agarwal, Gaurav Sep 25, 2012) (Burgoon, Frank J. Oct 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Create SDR (Burgoon, Frank J. Oct 2, 2012) <br> |  | 35 | FINDING | 8969 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74266
30090 | FINDING | SNR firmware upgrade tool does not prompt user for parameters when launched without them. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When tool is launched from command line without any parameters it informs user about usage and terminates. In such case tool should prompt for SDS IP, SNR redundancy flag and path to idf file. (Czak, Jakub Sep 25, 2012) |  |  |  | Launch SNR firmware upgrade tool without command line parameters. It should prompt for: - SDS IP address or host name - if SNR is redundant - path to idf file from upgrade package | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8970 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74268
30091 | FINDING | SNR firmware upgrade tool hangs when there is an attempt to upgrade disconnected device. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When trying to upgrade disconnected SNR, tool hangs. It should timeout and inform user about issue. (Czak, Jakub Sep 25, 2012) |  |  |  | Turn off SNR and start upgrade application. Utility should report error and return. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8971 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74270
30092 | FINDING | Controller interfaces redundancy not working | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Two issues with interface redundancy were observed:<br><br>1) When OHI is configured on controller for SIS interface (N1 and N4) and during boot up only N4 interface is connected, controller is not communicating. Checking interface status on controller shows that link is up. If failover to backup occurs when controller is already running, backup interface works fine. Same issue happens with OHI 0 (N2, N3). This was observed on OCR1100 only.<br><br>2) On OCR400 with OHI 1 configured failover to N4 is not working. Checking status on controller shows that link is up. (Czak, Jakub Sep 25, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | For fei interfaces ...<br>Moved link-state-checking/ohi-failover into the watchdog routine.<br>This reduces processor load and addresses finding #8972.<br><br>For gei interfaces ...<br>Added OHI data structure semaphore. We now accurately determine <br>the NICs initial link state. (Zaremsky, Mark Oct 30, 2012) <br> |  | 35 | FINDING | 8972 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74272
30093 | FINDING | Search option is not working in online help | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Search option is not working in online help (Singh, Ghanshyam Sep 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 11/16/2012: This will require some research. Create an SDR and move to next release - 3.6 (Casteel, Linda Nov 16, 2012)<br>---<br>msb - Closed; Converted to SDR 19257 (Benzvi, Mati Nov 26, 2012) <br> |  | 35 | FINDING | 8973 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74274
30094 | FINDING | Many topics are showing "untitled" in online help | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Many topics are showing &quot;untitled&quot; in online help. when ever we select any topic from index tab of online help then its showing untitled. Although we are able to open after selecting anyone.e.g ZL,ZH,ZG.YK,U9,U8,U7 etc. (Singh, Ghanshyam Sep 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 11/14/2012: The record types portion of the OvationApplications.chm is complicated, but works in the regular display. There are no plans to investigate fixing these links for the Index tab. It may break something else. Works as designed/no plans to fix. (Casteel, Linda Nov 14, 2012) <br> |  | 35 | FINDING | 8974 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74276
30095 | FINDING | SVTP:Ovation system viewer should be incorporated in Basic function SVTP for Menu. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Ovation system viewer should be incorporated in Basic function SVTP&quot;3.5_U9_BASIC_FUNCTIONS_SVTP_rev1.M_GS.doc&quot; for Menu Fucntion TEST CASE 7. (Singh, Ghanshyam Sep 26, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2012-09-26T05:25:31-04:00</p> <p><strong>Modified Date:</strong> 2012-09-26T05:25:31-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8975 |  | FINDING | Singh, Ghanshyam EMR SYSS PWS LEIC | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74277
30096 | FINDING | Point Menu: System Viewer is missing in point menu fuction once point menu called in Graphics. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Point Menu: System Viewer is missing in point menu fuction once point menu called in Graphics. By right clicking on a point in graphics. (Singh, Ghanshyam Sep 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added the System Viewer and the Remote Alarm Viewer options to the point menu in Graphics. (Spillane, Donal A. Oct 11, 2012)<br>---<br>msb - Closed: Converted to SDR 19132 (Benzvi, Mati Oct 13, 2012) <br> |  | 35 | FINDING | 8976 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74279
30097 | FINDING | Graphics:Help button is not working in Group option of Graphics. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Graphics:help button is not working in Group option of Graphics.Open online graphics-&gt;file menu-&gt;group-&gt;help(Here it is not working). (Singh, Ghanshyam Sep 26, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Graphics (GR)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2012-09-26T06:12:03-04:00</p> <p><strong>Modified Date:</strong> 2012-09-26T06:12:03-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8977 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74280
30098 | FINDING | Downloading firmware to new ERVP module corrupts module. | Shaw, Scott External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Firmware was downloaded to a prototype ERVP module using the Diagnostics tool. After the download was completed and the module was rebooted, communication could no longer be established between the controller and the ERVP module. (Wood, Tom Sep 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/27/12 - close, track as SDR 19059. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8978 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | Labans, Michael EMR SYSS PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74282
30100 | FINDING | Hovering of mouse does not show any details at Ovation System Viewer Help icon. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation 3.5.0, Ovation System Viewer is opened. At the right top corner side of the window, if mouse pointer is hovered over the &quot;?&quot; icon, then no details are shown regarding Help file. Pressing F1 key from the operator station keyboard does not open the Help file.<br>Please find the attached snapshot for reference. (Mitra, Sambuddha Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | partial fix - the hover will show the tooltip. This is in the Nov 1 patch.<br>The missing help file is not my responsibility. (Wozniak, Diane M. Oct 29, 2012)<br>---<br>msb - Closed: Converted to SDR 19222 (Benzvi, Mati Oct 31, 2012) <br> |  | 35 | FINDING | 8980 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74286
30102 | FINDING | Test case 5.5.2 of SVTP 3.5_VxSIM_VC_SVTP_Rev2.0_RL needs changes | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.5.2 of SVTP 3.5_VxSIM_VC_SVTP_Rev2.0_RL (point 1) should read as follows:<br>1.Primary Virtual Contrller drop goes into Fault mode. (Lal, Ramesh Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Ic 9/27/12 - fixed in VxSIM_VC_SVTP_Rev2.1. (Capani, Nooch Sep 27, 2012) <br> |  | 35 | FINDING | 8982 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74289
30103 | FINDING | Point Menu:Sometimes point menu is not able to produce the signal diagram. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Sometimes point menu is not able to produce the signal diagram specially in case of 64 bit system . Please find attached the point which is not able to produce signal diagram by right click on PI and selecting signal diagram on the drop250 &amp; remote login details for drop250. (Singh, Ghanshyam Sep 27, 2012) (Singh, Ghanshyam Sep 27, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | There is not an issue with Point Menu. As you can see the Signal Viewer gives error that 0120.svg does not exist. You should investigate to see if that sheet does exist on that machine. If not you need to investigate does it exist on other Operator Stations. If it doesn&quot;t exist on some machines you need to write a finding for the Control Builder group (McMaster, James Sep 27, 2012)<br><br>GS: Please find attached &quot;diagram.zip&quot;. The used point can produce signal diagram through &quot;where used&quot; option but not through point menu. Issue can be recreate on drop231 (remote login detail is attached as &quot;Remote_Login_Details.doc&quot;). (Singh, Ghanshyam Oct 1, 2012) (Burgoon, Frank J. Oct 1, 2012)<br><br>Found there is an issue if the system is configured to not display fully qualified point names.<br>An SDR should be generated against Point Menu (McMaster, James Oct 1, 2012)<br>---<br>msb - Closed: Converted to SDR 19126 (Benzvi, Mati Oct 10, 2012) <br> |  | 35 | FINDING | 8983 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74291
30104 | FINDING | At Trend Help icon, hovering of mouse does not show any details. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | In Ovation 3.5.0, Trend is opened. At the right top corner side of the window, if mouse pointer is hovered over the &quot;?&quot; icon, then no details are displayed regarding Help file.<br><br>Please find the attached snapshot for reference. (Mitra, Sambuddha Sep 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8984 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74293
30105 | FINDING | Browse point in Historical review /Historical Trend for source as Historian with certain combination does not work. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When Browse point is done with source as Historian following comination does not gibve any result:<br>1)When Data Type selection is Digital,packed and real is unckecked:Result is 0 point.<br>2)When data type slection Real, Packed and digital is unchecked:Result is 0 point.<br>3)When data type slection Real, digital and packed is unchecked:Result is 0 point.<br>4)When Point category selection is all(DCS,LAB,STATISICS and SCADA)::Result is 0 point. (Kumar, Shailendra Sep 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Create SDR. (Burgoon, Frank J. Oct 2, 2012)<br>---<br>msb - Closed: Converted to SDR 19157 (Benzvi, Mati Oct 19, 2012) <br> |  | 35 | FINDING | 8985 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74295
30108 | FINDING | Few files of ELC module appears for download again with a small time stamp changes. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following steps are performed :-<br><br>1. Firmware of ELC module has neen download in drop18/68 (OCR1100).<br>2. Same module is connected to 1.2.3 in drop40/90 (OCR400).<br> Controller diagnotic window shows few files (hw.out,RDP_M.out etc) to download again<br> with a small time diiference between Contoller &amp; Module version.<br> e.g AB.so has a time difference of only 2 sec betwwen Contoller &amp; Module version.<br> Please refer attached snapshot&quot;ELC_module.jpg&quot; for the reference. (Sahay, Madhukar Sep 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The files downloaded to any module can have a small difference in times between an 1100 and a 400. Though the files are the same they are copied at build time hence resulting in a slightly different time stamp. (Christy, Benjamin Dec 17, 2012)<br><br>I am closing this finding. (Sahay, Madhukar Dec 17, 2012) <br> |  | 35 | FINDING | 8988 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74300
30109 | FINDING | PWSIT - Ovation Native Wireless HART driver would fault when configured for redundancy. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Gateway connected to Ovation as Redundancy pair. In Developer Studio, bind devices to Wireless Engineering matrix and assign both Node and Analog points to each devices. Point Review does show some reading from device. However, the status point are all bad. Did set the limit in point property to make sure reading are within range.<br><br>Did a quick test by switching temperature unit on device variable from degC to degF in AMS UI but didn&quot;t see value update in point review.<br><br>Tony Ciccozzi has been remote in and trouble shooting issue and did found a problem. Patch applied need to be enter into next build. (Phan, Quang Sep 28, 2012) (Swartz, Mark E. Sep 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A bug was found in the logic used to process device status. (Ciccozzi, Anthony Oct 5, 2012)<br>---<br>msb - Closed: Converted to SDR 19139 (Benzvi, Mati Oct 15, 2012) <br> |  | 35 | FINDING | 8989 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74302
30110 | FINDING | Test Case 5.7.1.d in 3.5_SRF1525_SVTP_rev1.4_xx.doc needs modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case is &quot;d)To verify that errors encountered during display are logged in the log file.&quot; There is no seperate log file for this product. All the events are logged in as event messages of Historian. <br>Hence the test case must be modified. (Sachan, Pallavi Oct 1, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN OpCon (WOP)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-10-01T07:00:05-04:00</p> <p><strong>Modified Date:</strong> 2012-10-01T07:00:05-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 8990 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74303
30111 | FINDING | Deleting Multiple Remote Networks from Studio takes too long to complete | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Deleting Multiple Remote networks from Studio takes too long to complete<br>because Studio readjust the indecies of the remote networks after each delete.<br>Steps:<br> 1. we had 200 Remote networks configured on 3.5.0 server (125)<br> 2. On Sat 09/29 - All 200 objects were selected in a single directory for Delete.<br> 3. On Mon 10/01 - Studio still deleting... <br> A refresh shows only the 1st 20 networks were deleted.<br>Notes:<br> a. If we select last object and delete, it takes 5 seconds.<br> b. If we select objects in reverse order, is still deletes in forward order. (Benzvi, Mati Oct 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Way it works this release. SDR for future consideration. (Swartz, Mark E. Oct 16, 2012)<br>---<br>msb - Closed, Converted to SDR 19158 (Benzvi, Mati Oct 19, 2012) <br> |  | 35 | FINDING | 8991 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74305
30113 | FINDING | Field bus Device update cannot be done through ovation. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | There is no option available in Ov3.5 to field bus device updtae. (Sahay, Madhukar Oct 1, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed in Patch OVA350002 via integration with AMS 12<br>- (Hutchison, Steven B. Oct 22, 2012)<br>---<br>msb - Closed: Converted to SDR 19163 (Benzvi, Mati Oct 22, 2012) <br> |  | 35 | FINDING | 8993 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74309
30120 | FINDING | Freeze command doesn"t work as expected on redundant Virtual Controllers | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | There are two non redundant VCHs on 3.5 SIS Network Drop139 and Drop137. VCH Drop139 is hosting Primary Virtual Controller Drop142 and VCH Drop137 is hosting Partner Virtual Controller Drop162 respectively. <br>1. In SimControl GUI giving Freeze command freezes Drop142 (in control). When Drop142 is rebooted Partner Drop162 takes control and enters into Freeze mode. But when Drop162(which is now in control)is rebooted Primary Drop142 takes control but doesn&quot;t enter into Freeze mode(it is in Run mode).<br>2.Freeze command freezes a non redundant Virtual Controller drop.But when this drop is rebooted it comes up in Run mode instead of remaining in Freeze mode. (Lal, Ramesh Oct 2, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Simulator commands are only valid for controllers currently in control. Other than &quot;STOP&quot; command, simulator commands received in backup controllers are not acted upon. A reboot of a controller will always bring it up in &quot;Run&quot; mode, it should not revert to its previous mode. (Perdeus, Matthew Oct 16, 2012)<br><br>11/06/12:RL - Finding closed based on Dev&quot;s explanation. (Lal, Ramesh Nov 5, 2012) <br> |  | 35 | FINDING | 9000 |  | FINDING | [10 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74323
30136 | FINDING | Need to Remove test case 5.15.6 from the SVTP 3.5_Algorithms_SVTP_rev2.0_GA.doc. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Need to Remove test case 5.15.6 from the SVTP 3.5_Algorithms_SVTP_rev2.0_GA.doc because SLCPDOUT Algo does not exist in the control builder. (Agarwal, Gaurav Oct 3, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Algorithms (ALG)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2012-10-03T15:08:48-04:00</p> <p><strong>Modified Date:</strong> 2012-10-03T15:08:48-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9016 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74354
30137 | FINDING | Controller shell tool gets highest priority. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It is observed that when ever drop40 or drop90(OCR400) has been loaded which ever is in control mode become unavailable. 1800.diag show that it is healthy but when any operation (drop load or download) is performed then it says drop is unavailable.<br>Ben investigated this issue &amp; confirmed that this is because of shell tool got the highest prority 1 it should have priority below.<br>He has fixed it temporary for drop40. (Sahay, Madhukar Oct 3, 2012) (Sahay, Madhukar Oct 3, 2012)<br>But the fix will be go off once the drop is rebooted, so Ben has suggested not to reboot the drop till we get the patch. (Sahay, Madhukar Oct 5, 2012) |  |  |  | From the vxWorks console, perform an &quot;i&quot; command to get a task list. Verify tShell has a priority = 250. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The tShell task priority was changed to 250 (a very low priority). (Ciccozzi, Anthony Oct 5, 2012)<br>---<br>msb - Closed: Converted to SDR 19138 (Benzvi, Mati Oct 15, 2012) <br> |  | 35 | FINDING | 9017 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74356
30138 | FINDING | Test case 5.23.4 a) & b) of TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx are Not Applicable | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.23.4 a) &amp; b) of TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx says to check controller version of OCR400 in Controller Diagnostics. However, as per F#8667 Controller Diagnostics do not show controller version for OCR400. It only shows controller version for OCR1100.<br>Hence, these 2 test cases are NA. (Gupta, Chandresh Oct 4, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-10-04T05:01:37-04:00</p> <p><strong>Modified Date:</strong> 2012-10-04T05:01:37-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9018 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74357
30139 | FINDING | a procedure is required to load the Radius Protocol on WS03 Domain Controller | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Since telnet is disabled in Ov-3.5.0 and a multi-net setup can be configured with an older<br>Ovation Security Server (OSS) on a Windows Server 2003 Domain Controller (DC),<br>a procedure is required to load the Radius Protocol on WS03 DC to allow communication <br>to the Controllers on the Ov-3.5.0 network. (Benzvi, Mati Oct 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The general RADIUS setup information for the Ovation Domain Controllers will be covered in the Ovation Managing Security guide. This will cover general RADIUS server configuration. <br><br>The Ovation controller specific configuration, will be a issued as a SWAT Knowledge Base Article. For security and reliability reasons, it will not be formally documented for Ovation Users since controller access should only be done by certain Emerson PWS personnel. (Ciccozzi, Anthony Feb 11, 2013)<br>---<br>msb - Same as SDR 19468 by Tarek ftom 12-Mar-2033 (Benzvi, Mati May 23, 2013) <br> |  | 35 | FINDING | 9019 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74359
30140 | FINDING | Bit wise Descriptions of packed points are not available in trend display | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Bit wise Descriptions of packed points are not available in trend display while viewing the trend of particular bit of a packed point . (Jayarajan, Jayakumari Oct 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9020 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74361
30141 | FINDING | Acknowledging and clearing alarms caused an OCR400 to fail. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OCR400 Controller 43/93 (EMILY) was in the process of rebooting (control and a relay panel are used to cause continuous hard-reboot failovers). Points originating from the OCR were being acknowledged and cleared when 43 failed. This has been observed previously with 3.5.0_U9.<br><br>Ovation error buffer messages will be attached. (Brown, Sean Oct 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Any time that drop 93 came up in controll it immediately fails.<br>Doing a hard clear of the controller using the command &quot;deleteAllFiles&quot; resolved the issue. Moving to monitoring please le me know if this occurs again. (Christy, Benjamin Oct 17, 2012)<br><br>Occurred again. 93 was in Control; 43 was in Backup. Alarms were caused then acknowledged and cleared. 93 was rebooted from Studio; 43 went into Control then failed within 10 seconds. (Brown, Sean Oct 17, 2012) <br> Multiple tasks were using the send socket for sending admdb messages. Corrected that code so that each task uses a seperate socket(). (Christy, Benjamin Nov 20, 2012)<br><br>SDR 19351 created (Ritenbaugh, David W. Jan 16, 2013) |  | 35 | FINDING | 9021 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74363
30142 | FINDING | SDR 18504: Speed Detector open-wire detection/point quality information not in OW350_R1150. | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Skena, Ronald E AUTOSOL PWS PITT | 2018-12-04 08:51 | [11 empty] | Skena, Ronald E AUTOSOL PWS PITT | 2018-12-04 08:51 |  |  |  | 2018-12-04 08:51 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | SDR 18504 (Speed Detector channel notations should be added to explain open-wire detection/point quality).<br><br>Notations are not in Ovation I/O Reference Manual (Val\Tests\3.5.0\Docs\Ov350_SmartDocs). (Brown, Sean Oct 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9022 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | 3.5 |  |  | FINDING | [6 empty] | 135019
30143 | FINDING | Test proceedure 3.5_SRF1630_SVTP_rev1.1_RL needs changes | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2015-06-19 13:08 | [11 empty] | McMaster, James External Artech | 2015-06-19 13:08 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In Test case 1.1.1 of test proceedure 3.5_SRF1630_SVTP_rev1.1_RL the location of the Snapshot files should be changed to c:\ovation\Drpxx\ata0\wdpf\dpu\sim. (Lal, Ramesh Oct 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9023 |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81503
30144 | FINDING | Online graphics is getting crashed. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Steps to be followed to recreate the issue:<br>1. Create an enhanced entry field of type operator or both, format=real, and associate an integer runtime trigger (i.e. 3) with the entry field. PFA &quot;gb-config2.jpg&quot; for clarity.<br>2.In the graphic in the given trigger section, add a RUN_PROGRAMS command and run application program 224 (READ_ENTRY_FIELD) and enter the local variable name as the destination to read the entry field value into. PFA &quot;gb-config1.JPG&quot; for clarity.<br>3. Download the drop then open respective online graphics, give some value entry field and click over enter button. Once we click over button system is getting crashed. PFA &quot;crashed.jpg&quot; for clarity.<br>PFA remote login details for drop231 and use graphics &quot;GS_350_FT.diag&quot;. (Singh, Ghanshyam Oct 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | An invalid parameter was used for program 224 (READ_ENTRY_FIELD) which caused the displayer to crash. The &quot;Read Status&quot; parameter should be a Pointer or a Variable. I will make a change to the Graphics Builder Application Program wizard to check for a valid entry. I will also change the Graphics displayer to check for an invalid entry and issue a warning. (Spillane, Donal A. Oct 11, 2012)<br>---<br>msb - Closed, Converted to SDR 19159 (Benzvi, Mati Oct 19, 2012) <br> |  | 35 | FINDING | 9024 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74367
30145 | FINDING | Help alogo :Formula for interpolation algo is incorrect. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:26 | [11 empty] | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-15 04:26 | 3.6.0_U1 |  |  | 2017-06-15 04:26 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Formula for interpolation algo is incorrect in the document &quot;Control Builder help REF_1100&quot;.<br>.PFA for clarity as I have marked the formula. Given formula doesn&quot;t support the linear equation .I think the formula for linearity is Yout=Yn+((Yn+1-Yn)*((Xin_Xn)/(Xn+1-Xn))) in the document &quot;Control Builder help REF_1100&quot;. (Singh, Ghanshyam Oct 8, 2012) | <p>AA 12/01/2015: The particular finding was fixed by Linda. Hence, closing the finding.</p> |  |  | <p>LC 11/22/2013: Look at the formula for the INTERP algorithm.</p><p>AA 12/01/2015: The issue related to the&nbsp;INTERP algorithm has been resolved by Linda. Please find attached the latest online help screenshot. I will be closing this finding.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>LC 11/23/2012: Need a clarification before I make the change. You have the formula written as, &quot;Yout=Yn+((Yn+1-Yn)*((Xin_Xn)/(Xn+1-Xn))) However, should it really be &quot;Yout=Yn+((Yn+1-Yn)*((Xin-Xn)/(Xn+1-Xn))) ??? Please clarify the properties for the &quot;X&quot; part of the equation. (Casteel, Linda Nov 23, 2012)<br><br>GS 09/23/2013: Small bracket is misplaced in a formulae .So formulae looks wrong as per the interpolation theory.<br>given formulae &quot;Yout=(Yn+(Yn+1-Yn))*((Xin_Xn)/(Xn+1-Xn))&quot;.<br>if you observe the formulae part &quot;(Yn+(Yn+1-Yn))&quot; in which Yn is cancelled by another Yn in formulae. It has no meaning.<br>Please take a reference form the developer for better clarity. (Singh, Ghanshyam Sep 23, 2013) <br> LC 11/22/2013: For the INTERP algorithm, I changed the formula to: <br>YOUT = Yn + ( (Yn+1 - Yn) * ( (XIN - Xn) / (Xn+1 - Xn) ). This fix will be available in the Ovation 3.5.1 U3 build and in OW351_R1100.pdf on Q:\Communication\Tech\Comm\Share\Validation. (Casteel, Linda Nov 22, 2013)</p><p><br></p><p><br></p><p>AA 12/01/2015: The issue related to the&nbsp;INTEREP algorithm has been resolved by Linda. Please find attached the latest online help screenshot. I will be closing this finding. The latest updated manual is kept at: Q:\Communication\TechComm\Share\Abhinav_Ovation 3.6.0 manuals\Ovation Algorithms Reference Manual (OW360_R1100). This is visible in 3.6.0_U1 build.</p> |  | 35 | FINDING | 9025 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Bush, Kirt T EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  | <p>LC 11822/2013: Updated the INTERP algorithm to provide the correct formula.</p><p>AA 12/01/2015: The issue related to the&nbsp;INTERP algorithm has been resolved by Linda. Please find attached the latest online help screenshot. I will be closing this finding.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 114325
30146 | FINDING | Can not download firmware to ERVP module. | Shaw, Scott External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It was attempted to download the required files to an ERVP module using the controller diagnostics utility. The utility could detect that the module was present on the controller branch but could not communicate with the module to determine the current level of files on the module. (Wood, Tom Oct 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: (same as F# 8978) converted to SDR 19059 (Benzvi, Mati Mar 4, 2013) <br> |  | 35 | FINDING | 9026 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74371
30147 | FINDING | OSR, reports Optimizer software under Other Installed Softwares. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Smart Process Optimizer Software is reported under &quot;Other Installed Software&quot;, this should be reported under &quot;Other Ovation Software.&quot; (Sachan, Pallavi Oct 9, 2012)<br><br>I need access to your machine with this software installed. Kindly email the remote login details and the drop name. (Quintos, Ronaldo M. Oct 31, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Smart Process Optimizer software is installed on Drop231, this can be logged in using the attached Remote_Login_Details.doc (Sachan, Pallavi Nov 1, 2012)<br><br>Fixed with the latest code. (Benig, Ronaldo B. Dec 9, 2013)<br><br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 9027 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74373
30148 | FINDING | Test Case 5.3.1 of SRF1584_SVTP_rev1.2.doc needs modifications. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Description of I/O MODULES in Test Case 5.3.1 of SRF1584_SVTP_rev1.2.doc needs modifications as below.<br><br>g) 1C31194G03/1C31197G05:Valve Position Controller Enhanced 17 Volt LVDT:50 mA(G03)<br>to be modified as &quot;Valve Position Controller Enhanced 24 Volt DC LVDT:50 mA(G03)&quot;<br><br>h) 1C31194G04/1C31197G01: Valve Position Controller Enhanced 17 Volt LVDT:24.9 mA<br>to be modified as &quot;Valve Position Controller Enhanced 23.75 Volt LVDT:24.9 mA&quot;<br><br>i) 1C31194G04/1C31197G02: Valve Position Controller Enhanced 17 Volt LVDT:16.8 mA<br>to be modified as &quot;Valve Position Controller Enhanced 23.75 Volt LVDT:16.8 mA&quot;<br><br>j) 1C31194G04/1C31197G03: Valve Position Controller Enhanced 17 Volt LVDT:8.3 mA<br>to be modified as &quot;Valve Position Controller Enhanced 23.75 Volt LVDT:8.3 mA&quot;<br><br>k) 1C31194G04/1C31197G04: Valve Position Controller Enhanced 17 Volt LVDT:36 mA<br>to be modified as &quot;Valve Position Controller Enhanced 23.75 Volt LVDT:36 mA&quot;<br><br>l) 1C31194G04/1C31197G05: Valve Position Controller Enhanced 17 Volt LVDT:50 mA(G03)<br>to be modified as &quot;Valve Position Controller Enhanced 24 Volt DC LVDT:50 mA(G04)&quot;<br><br>m)5X004119G02/1X00569H01:Ethernet Link BusModule(Time Synchronization)<br>to be modified as &quot;5X00419G01/1X00569H01.&quot; (Sachan, Pallavi Oct 9, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Ovation System Registration (OSR)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-10-09T05:14:14-04:00</p> <p><strong>Modified Date:</strong> 2012-10-09T05:14:14-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9028 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74374
30152 | FINDING | Test Case 5.1.4 of SRF1584_SVTP_rev1.2.doc needs modifications. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Module Numbers in Test Case 5.1.4 of SRF1584_SVTP_rev1.2.doc needs modifications as below:<br><br>a) 1C31199G04 Servo Drive w/Readback DC LVDT Output: needs to be modified as &quot;1C31199G01&quot;<br><br>b) 1C31199G05 Servo Drive w/Readback 1 kHz LVT Output: needs to be modified as &quot;1C31199G02&quot;<br><br>c) 1C31199G06 Servo Drive w/Readback 3 kHz LVT Output: needs to be modified as &quot;1C31199G03&quot; (Sachan, Pallavi Oct 10, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Ovation System Registration (OSR)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sachan, Pallavi</p> <p><strong>Entry Date:</strong> 2012-10-10T02:32:29-04:00</p> <p><strong>Modified Date:</strong> 2012-10-10T02:32:29-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9032 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74381
30153 | FINDING | Quality of Whart process points keep changing from good to bad in every 1-2 mins. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following steps are performed :-<br>1. Wireless gateway 1420 has been configured.<br>2. Wireless device (TT) has been configured.<br>3. Different process values (e.g PV, SV,TT etc) of the device are configured to a LA <br> points in drop1/51.<br> It is observed that process points of a WHART device keep changing its quality from GOOD <br> to BAD in every 1-2 mins (approx) &amp; remain in BAD quality for 1-2 mins (approx) <br> then turn to GOOD. (Sahay, Madhukar Oct 10, 2012)<br><br> Please refer attached snapshot F#9033.jpg for the reference. (Sahay, Madhukar Oct 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Wireless HART devices burst variables at a defined rate to the 1420 Wireless HART gateway. The 1420 then caches this information. When a controller requests a process variable (via command 2, command 3, or command 9) the 1420 gets the value from the cache. If a variable is not configured in the cache (either it does not exist or the device was not configured to burst this value) then a DR_RUNNING response code is returned. This response code will be set until the 1420 is able to retrieve the value for the device. This is what causes the node record alarm and quality to cycle. <br><br>In the device node record, bits 1 (Response Code Error) and 5 (DR_RUNNING) are set causing the node record to alarm and all of the associated points to go to bad quality. <br><br>In this case, There were 2 variables configured LCURRENT and BATTERY that were configured in Ovation but not configured in the device. (Ciccozzi, Anthony Oct 12, 2012) <br> |  | 35 | FINDING | 9033 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74383
30156 | FINDING | OSR reports Q line details which are not configured in the Developer studio. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In the 3.5.0 Ovation network, Net#7, observed Q line details like IO device, location &amp; serial nos.which are not configured in the Developer studio for all physical controllers.KIndly let me know from where it is including in the report,&amp; whether the sr. nos are randomly generated? (N, Thamaraiselvi Oct 11, 2012)<br><br>Can you send a sample screen shot of the issue? (Quintos, Ronaldo M. Sep 20, 2013).<br>Kindly find attached the OSR report taken on the day I reported the finding. The extra serial no. details of the IOIC , Q line details are reported as <br>Location: DROP23/DROP73:5:18:1 <br>Serial Number: 0000052185 under the controller 23/73. I don&quot;t have the snapshot of the studio. The network is upgraded to 3.5.1 &amp; all configurations are changed now. (N, Thamaraiselvi Sep 26, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9036 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74390
30158 | FINDING | Connection lost message from Gateway does not report every time. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Following steps are performed :-<br><br>1. Whart has been configured in drop1/51 (Emily system).<br>2. When Gateway communication cable is disconnected then communication lost meesage appears <br> in ovation error log.<br>3. Communication cable is connected.<br>4. Now when communication cable is again disconnected or Gateway is powered off then it does<br> not report loss of communication message in ovation error log. (Sahay, Madhukar Oct 11, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2012-10-11T16:41:10-04:00</p> <p><strong>Modified Date:</strong> 2012-10-22T16:34:49-04:00</p> | 0 |  | Ovation for Windows/General/Software | Loss of communication is no longer being logged to the error log. This is a remnant from the initial release. The logging will be removed. The gateway node record will reflect status and failure states and will alarm accordingly. (Ciccozzi, Anthony Oct 18, 2012)<br><br>MS : As per developer&quot;s comment &quot;loss of communication is no longer being logged to the error log&quot;<br> so the test case 5.25.8(a-d) of TR &quot;3.5_CONTROLLER_SVTP_rev5.2&quot; should be update accordingly.<br> I am redirecting this finding to SVTP. (Sahay, Madhukar Oct 22, 2012) <br> |  | 35 | FINDING | 9038 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74393
30159 | FINDING | Description of Q line modules are not reported in the OSR report. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In Net#7, controller 23/73, the local Q line modules are configured in the Developer studio.The Description of Q line modules are not reported in the OSR report. (N, Thamaraiselvi Oct 12, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation System Registration (OSR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Benig, Ronaldo B.</p> <p><strong>Notify List:</strong> Quintos, Ronaldo M. N, Thamaraiselvi</p> <p><strong>Entry Date:</strong> 2012-10-12T05:55:44-04:00</p> <p><strong>Modified Date:</strong> 2012-10-24T02:46:43-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9039 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74394
30160 | FINDING | Device type shown in Sycon Tool under Device Assignment tab needs changes | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | SDR#17580:In configuration window of Sycon Tool the when we select &quot;Device Assignment&quot; tab it shows &quot;DEVICNET&quot; for device type DeviceNet. It should show &quot;DEVICENET&quot;. (Lal, Ramesh Oct 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The field is limited to 8 characters. The &quot;E&quot; was omitted to keep DEVICNET 8-characters (PROFIBUS is also 8 characters). (Ciccozzi, Anthony Oct 23, 2012)<br><br>10/24/12: RL - Finding closed in view of Dev&quot;s comment. (Lal, Ramesh Oct 24, 2012) <br> |  | 35 | FINDING | 9040 |  | FINDING | Plymire, Alvan AUTOSOL PWS PITT | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74396
30161 | FINDING | In Historical Review, Few data filters are not working properly. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It is observed in Historical Review that, Following Data filter are not working properly.<br>1:- SID ALARM<br>2:- INITIAL VALUE<br>3:- TAGGED OUT<br>4:- LIMIT ALARM<br>5:- Alarm checked Removed<br><br>Case 1:-<br>a:- Create a SID alarm in a point which is configured in HCT.<br>b:- Open the Historical review &amp; Filter the Sid alarm .<br>c:- Set the time duration in which, SID alarm has created &amp; Press Start Historical Review button. <br>d:- Blank pages will appear in Historical review.<br> Note:- Above case is also observed in Tagged Out &amp; Limit Alarm filter.<br><br>Case 2:- <br>In Initial value filter, Screen shots (Initial value filter.jpg) show that <br>RAW value filter is applicable in place of initial value filter.<br><br>Case 3:-<br>a:- Create a Alarm checked removed in a point.<br>b:- Open the Historical review &amp; Enable the Alarm checked removed filter.<br>c:- Set the time duration in which, Alarm checked removed has created &amp; Press Start Historical Review button. <br>d:- Blank pages will appear in Historical review.<br> as shown in screen shots(AR Enable.jpg)<br>e:- Now enable the Limit checked removed filter.<br>f:- Historical review show that with the Limit checked , Alarm checked is also appear in same page.<br> As shown in screen shots (AR &amp; LR.jpg) (Agarwal, Gaurav Oct 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Next build/patch should have this fix. (Matreja Shyam Oct 19, 2012)<br>smatreja: OPH.3.4.1_Patch (for OPH) or 3.5.0_Patch (for Ovation). (Matreja Shyam Oct 22, 2012)<br>---<br>msb - Closed: Converted to SDR 19188 (Benzvi, Mati Oct 24, 2012) <br> |  | 35 | FINDING | 9041 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR/DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74398
30163 | FINDING | OSR, report does not display any difference between Wireless HART/ Redundant Wireless HART configurations. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Drop 1/51 on SIS Network in PGH, has Wireless HART configuration.<br>Where as Drop 1/51 in Austin (used by Quang Phan), has REDUNDANT Wireless HART configuration.<br>But there is no difference in the reports from both the networks.<br><br>OSR should differentiate between the two configurations. (Sachan, Pallavi Oct 15, 2012)<br><br>Kindly send a screen shot of the configuration in Dev Studio or related tool where Wireless HART is configured. (Quintos, Ronaldo M. Sep 20, 2013)<br><br>Changed Action from MIS to MNR. (Quintos, Ronaldo M. Sep 26, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | These configurations were during testing of Ovation3.5.0, one in PGH and one in Austin. Need to check with the configurations and will report back soon. (Sachan, Pallavi Sep 20, 2013) <br> |  | 35 | FINDING | 9043 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74402
30165 | FINDING | OSR, Oracle user credentials are not captured in report. | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | As per SRF1584_SVTP_rev1.2.doc, <br>TEST CASE 5: Oracle user credentials. <br>5.5.1 Test : Verify that the 3.5.0 Sys Registration Utility captures data from the 3.5.0 Database station correctly.<br><br>User credentials are not seen in the OSR report. (Sachan, Pallavi Oct 15, 2012)<br><br>There is no requirement to display the user credentials in the report. (Quintos, Ronaldo M. Oct 24, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | As per above cooments, this test case is not valid and should be removed from SVTP. (Sachan, Pallavi Nov 27, 2012)<br><br>Changed Action from MIS to WIW. (Quintos, Ronaldo M. Sep 26, 2013)<br><br>Please close. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 9045 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [7 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74406
30166 | FINDING | Exception for SIS events not added in Windows Firewall. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Exception for SIS events in Windows Firewall is not added. SIS events exception needs to be added to Windows Firewall. (Pandey, Vijay Oct 15, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9046 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74408
30167 | FINDING | Discrepancy between Ovstudio fieldbus port(p01/p02) right click options details and Ovstudio help. | Antony, Leena PROCESS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Discrepancy between Ovstudio fieldbus port(p01/p02) right click options details and Ovstudio help. Ovstudio help needs to be updated. (Pandey, Vijay Oct 16, 2012) | LA 11/7/2012: The screenshot in section 8.5.4 has been updated to show the updated Port right-click options. |  |  | LA 11/7/2012: Please check topic 8.5.4: To download a Foundation Fieldbus module port screenshot. The updated document is stored at \\Uspit-fp05\ohara\Communication\TechComm\Share\Validation\Fieldbus 3.5\Review 5. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LA 11/7/2012: The screenshot has been updated to show the updated Port right-click options. (Antony, Leena Nov 7, 2012)<br>---<br>msb - Closed; Converted to SDR 19268 (Benzvi, Mati Nov 29, 2012) <br> |  | 35 | FINDING | 9047 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Casteel, Linda EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [7 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74410
30170 | FINDING | SDR 18548- Module Communication during download could render the module inoperative. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Used build: - <br>Ov: - Ov3.5.0_U9<br>ELC: - ELC1.2_U9<br><br>Note: - Tested on ELC Module.<br><br>Step Followed:-<br>1:- Before testing this SDR, ELC Module was working fine.<br>2:- Open the diagnostic tool &amp; Select the ELC Module.<br>3:- Press &quot;Download Available Firmware&quot; button.<br>4:- &quot;Module Firmware download&quot; window will open.<br>5:- Select all files &amp; Press download.<br>6:- During downloading, disconnect the ELC module from the Branch.<br>7:- Wait for more than 30 min &amp; again connect the module into the Branch.<br>8:- Again try to download firmware But unable to download &amp; module become inoperative. (Agarwal, Gaurav Oct 16, 2012) (Boehmer, Robert W. Oct 16, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This was added and built but was never moved over from the 6.5 to the 6.8 build. This is accomplished by running the appropriate script on the build machine. (Christy, Benjamin Oct 16, 2012)<br>---<br>msb - Closed: SDR 18548 changed from Lib = 3.5.0_U8 to PlannedRelease = 3.5.0_Patch (Benzvi, Mati Oct 22, 2012) <br> |  | 35 | FINDING | 9050 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74416
30171 | FINDING | THUM failure or recovery from the mesh is not reported in error log. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | following steps are performed :-<br>1. 1420 Gateway has been configured in Emily system.<br>2. THUM is wired to DVC 6000 &amp; added to a mesh.<br>3. Value of a varaibles (e.g PV ) of DVC 6000 can seen in P.I.<br>4. Now if wiring of THUM get disturbed then Gateway GUI shows THUM device unreachable , PV of <br> DVC 6000 shows BAD quality but ovation error log does not reports THUM device failure.<br>5. On the otherhand if wiring of a THUM is restored then THUM can be reached in Gateway <br> GUI &amp; P.I shows GOOD quality but ovation error log does not report anything. (Sahay, Madhukar Oct 16, 2012) (Ciccozzi, Anthony Oct 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Ovation Error log does not record these types of device failures. The node records assigned to the devices will reflect the device state (as reported by the HART7 protocol and the 1420) and alarm accordingly. (Ciccozzi, Anthony Oct 17, 2012)<br><br><br>MS : As per developer&quot;s comment &quot;THUM device failure is not logged &quot;<br> so the test case 5.25.5(m&amp;n) of TR &quot;3.5_CONTROLLER_SVTP_rev5.2&quot; should be update accordingly.<br> I am redirecting this finding to SVTP. (Sahay, Madhukar Oct 22, 2012) <br> |  | 35 | FINDING | 9051 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74418
30173 | FINDING | Information about the drop not configured in the the developer studio appears in the report. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Information about the drop#176 not configured in the the developer studio appears in the report of another nettwork with the same domain.<br>THe extra drop is the basically the prime domain controller. (N, Thamaraiselvi Oct 17, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - WAD. Domain Controller should always appear in the report (Benzvi, Mati Oct 17, 2012) <br> |  | 35 | FINDING | 9053 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74422
30176 | FINDING | PWSIT - HART-IP ports can not be update in Redundancy mode | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | HART-IP ports are set at 5094 originally on both gateway and on Ovation. Found out that it need to be 20004 in order for devices to communicate with Ovation.<br>Tried to change it on the active gateway but when switch over to other gateway, it kept going back to the old one 5094 on Active Gateway.<br><br>GW backup file (attached) was sent to Bob Beckmann for investigation. Bob confirmed there is a bug in gateway firmware and working to fix it on next gateway firmware release. (Phan, Quang Oct 17, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Test Plan (STP)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U8 14-SEP-12</p> <p><strong>Originator:</strong> Phan, Quang</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Phan, Quang Capani, Nooch</p> <p><strong>Entry Date:</strong> 2012-10-17T14:32:09-04:00</p> <p><strong>Modified Date:</strong> 2012-10-17T14:32:09-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9056 |  | FINDING | Phan, Quang EMR ENT TECH AUS | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74427
30177 | FINDING | SIS event retrival is not available in Historical review | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | SIS event rerival is not available in Historical review. (Pandey, Vijay Oct 18, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. OPH.3.4.1_Patch (for OPH) or 3.5.0_Patch (for Ovation). (Matreja Shyam Oct 22, 2012) <br> |  | 35 | FINDING | 9057 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR/DIR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74429
30178 | FINDING | Distributor algo help information is not getting properly. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Step to reproduce:<br><br>1.Add any algorithm in control builder &amp; Right click the algo and select Help. <br>2.Now add the Distributor algo <br>3.Right click the algo and select Help.<br>4.Now the information is displaying previously opened help details<br>5.It suppose to be displayed the Distributor algo help details only.<br><br>This observations found only in Distributor algo.<br>Please see the attached snap shot for reference. (K, SendhilKumar Oct 18, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Control Builder - Unified (CBU)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> K, SendhilKumar</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Hutchison, Steven B. K, SendhilKumar</p> <p><strong>Entry Date:</strong> 2012-10-18T07:35:30-04:00</p> <p><strong>Modified Date:</strong> 2012-10-18T07:35:30-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9058 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74430
30179 | FINDING | Licence descrepency details between the Licence Manager in the studio & Licence details in the OSR report. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | I have observed the following descrepency between the Licence Manager in the studio &amp; Licence details in the OSR report.<br>1.SCADA BRISTOL_OPENBSI, feature name 47 is missing in the report of both Net#7 &amp; net#8, where as the same is available in the Studio Licence Manager.<br>2.ELC 1.2.0 is installed in the net#7, appears both in control panel programme &amp; features as well Licence Manager in studio, but missing in the report. (N, Thamaraiselvi Oct 19, 2012)<br><br>Kindly send a screenshot of the License Manager with the said feature. I need the details displayed in the screen. (Quintos, Ronaldo M. Oct 25, 2012).<br><br>Please find attached the two snapshots.the 1st one of SCADA is observed in the drop#250 of net#7 in OV 3.5.0. &amp; the 2nd one about ELC details is observed in the drop#176 in net8 of OV 3.5.0. (N, Thamaraiselvi Nov 4, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013).<br>Generated the report in Ov3.5.1_U3 &amp; verified the report. FOund the SCADA licence has been reported but the ELC license details are still missing. (N, Thamaraiselvi Jan 13, 2014).<br><br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 9059 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74432
30188 | FINDING | Test case 5.8.5 in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc is Not Applicable | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.8.5 in TR 3.5_STUDIO_SVTP_Rev3.5_CG.doc says &quot;Configure Security: Setting Security for Default Drops&quot;.<br>The Default All Drops were existing in Solaris Security Manager but not in the Windows Security Manager.<br>Therefore, Test 5.8.5 is NA and needs to be removed from the SVTP. (Gupta, Chandresh Oct 21, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-10-21T23:32:34-04:00</p> <p><strong>Modified Date:</strong> 2012-10-21T23:32:34-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9068 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74448
30189 | FINDING | PWSIT - Pulse counter block increase by 5 instead of 1 | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When configure a PULSECNT block together with TIMEMON block to monitor number of pulse over period of time, counter is increased by 5 instead of 1 per block specification. Monitor block using Signal Digram and note that number jump by 2 (sometime by 1) then immediately to 5 until the next count.<br>For example, it would jump to 2 then immediately 5, 7 then 10, 12 then 15 and so on.<br><br>Step to reproduce:<br><br>Configure a module as shown in attached screenshot. <br>Tune ISEC on TIMEMON to 30 seconds then initialize DVALGEN by enter 1.<br>Monitor counter in Signal Diagram (Phan, Quang Oct 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | What is the period of the control task this is running in? (Boehmer, Robert W. Oct 29, 2012)<br><br>This is not a Pulse Counter block problem. The TIMEMON algorithm was running in a 100 msec task. This is the way the TIMEMON algorithm works when run in a 100 msec task. Rather than giving a single pulse on FLG2 when the controller time equals the start time plus multiple of incremental time, the TIMEMON algorithm will toggle FLG2 each time it runs while controller time equals start time plus multiple of incremental time. If the TIMEMON algorithm runs in a 100 msec control task then FLG2 will pulse 5 times. Due to the large base of installed systems that exhibit this behavior there is no plan to change this. (Boehmer, Robert W. Nov 2, 2012) <br> |  | 35 | FINDING | 9069 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74450
30190 | FINDING | PWSIT - Load failure on DBS | Swartz, Mark EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Load failure on DBS<br><br>Was building a module in control build to check system time and using DVALGEN to initiate the SYSTEMTIME block. Module in Control builder was modified, save and controller was load to update change.<br><br>Intitially was able to tune the DVALGEN to ON and OFF in Signal Diagram. All the sudden, was not able to do that any more. Even Log in Signal Diagram shown value been change from Previous to New but it doesn&quot;t take affect in current value. <br><br>Noted that System Status Display graphic shown DBS drop in Failed mode.<br><br>Steve Hutchison remote in to investigate the issue. He noted that controller failed to load (10/17/12) which cause change in Signal Diagram to not forward request to controller. Doesn&quot;t know how load failed on DBS.<br><br>Attached is error log during which time controller load failure occurred.<br><br>Reboot DBS drop did clear out failure issue.<br><br>Only saw this issue once and doesn&quot;t know how to reproduce it.<br><br>Filed as irreproducible anomaly (Phan, Quang Oct 22, 2012) (Phan, Quang Oct 22, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Move finding to monitoring per Steve Hutchison. (Phan, Quang Oct 23, 2012) <br> |  | 35 | FINDING | 9070 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74452
30196 | FINDING | Test case 5.23.2 g) in TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx could not be done in IEC due to unavailibility of hardware | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Test case 5.23.2 g) in TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx says to &quot;Verify ¿security¿ related events are sent to the targets&quot;.<br>However, the Nitro SIEM hardware required for it is not available in IEC. Hence this test could not be done here. (Gupta, Chandresh Oct 23, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-10-23T11:01:36-04:00</p> <p><strong>Modified Date:</strong> 2012-10-23T11:01:36-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9076 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74463
30206 | FINDING | Expanded Multi-Networking implemented in Ov-3.5.0 with 1 local network + 299 Remote networks | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The &quot;Ovation Expanded Multi-Networking Functional Specification - SRF Number 1632&quot; specifies:<br> - The software must be enhanced to accommodate up to 300 remote networks.<br> - This addressing scheme must be updated to handle at least 300 remote networks.<br>Howver, when the 300th remote network is added in Studio, the following error is dsplayed:<br>*--------------------&gt; Error Information &lt;--------------------*<br>Unable to complete the requested operation <br>Code : 0x80004005 Source : Ovation Developer Studio<br>*--------------------&gt; Error Stack Dump &lt;---------------------*<br>&lt;OvPtObject.cpp:1095&gt; [OvPtApi]: (Field Validation Error)<br>&lt;OvPt_Validate.cpp:8108&gt; [OvPtApi]: (Remote Network Alias Id Value must be between 1 and 299 (inclusive))<br><br>and if entered by import: <br>d:\db\Remote&gt;ovptimport -u ptadmin/ptadmin@ptdb Remnet_300.imp<br>[OvPtApi]: (Remote Network Alias Id Value must be between 1 and 299 (inclusive))<br>[OvPtImport]: Required attribute REMOTE_NET_NUMBER_ALIAS at line 10 failed validation<br>[OvPtImport]: &lt;V2Object.cpp:640&gt; Unable to add object NTWRK300 at line 10<br> --------------<br>Accordingly, The &quot;3.5_SRF1632_300-Multnet_SVTP_rev1.3_MB.docx&quot; states:<br> 5.1.5 Test : Verify that the total number of Remote Networks defined in Studio must handle at least 300 remote networks.<br> a) 31 Top Level Remote networks + 269 Nested node networks<br> b) 300 Remote Networks in Nested nodes<br> c) More than 300 Total Remote Networks are not allowed<br><br>Therefore, <br>1. The SRF should be changed to state: &quot;to accommodate up to 299 remote networks.<br>2. The SVT - 5.1.5 should be change to:<br> at least 299 remote networks<br> a) 31 Top Level Remote networks + 268 Nested node networks<br> b) 299 Remote Networks in Nested nodes<br> c) More than 299 Total Remote Networks are not allowed<br>3. The Documentation should also state: 1 Local network + 299 Remote Network (Benzvi, Mati Oct 29, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Multi Networking (MN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Benzvi, Mati Augustine, Lisa Casteel, Linda</p> <p><strong>Entry Date:</strong> 2012-10-29T12:46:32-04:00</p> <p><strong>Modified Date:</strong> 2012-10-29T12:50:54-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9086 |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Casteel, Linda EMR SYSS PWS PITT | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74478
30214 | FINDING | Test Case 5.2c.4 - 5.2c.6 in 3.5_WIN_OPCON_SVTP_rev2.H_XX.doc needs modification. | Capani, Innocenzo AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | As per page 4 of SRF 1579 Functional Specification Rev. 1.1, &quot;The feature to directly trend OPC points will no longer be supported. OPC data must be converted to Ovation points via the Client Mapper function.&quot;<br>Hence Test Case 5.2c.4 - 5.2c.6 in 3.5_WIN_OPCON_SVTP_rev2.H_XX.doc cannot be performed and the SVTP needs to be modified.. (Sachan, Pallavi Oct 31, 2012) | The feature to directly trend OPC points will no longer be supported. OPC data must be converted to Ovation points via the Client Mapper function. This change is noted in the Trend Enhancement (SRF1579) functionalspec. |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 11/26/12 - need to update SVTP and add note to DIR (under SRF 1579). (Capani, Nooch Nov 26, 2012) <br> |  | 35 | FINDING | 9094 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Note to be added to DIR | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74494
30215 | FINDING | OSR does not reports the installed Ovation Alarm Analyser Tool. | Benig, Ronaldo PROCESS PWS MNL | Active | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | OSR does not reports the installed Ovation Alarm Analyser Tool.This is common with OV 3.5.0, 3.4, 3.3.1, 3.1.3 &amp; 3.0.4.version. (N, Thamaraiselvi Oct 31, 2012)<br><br>I need access to your machine with this tool installed. Kindly email the remote login details. (Quintos, Ronaldo M. Oct 31, 2012)<br><br>Using the remote_login_details.doc details, I don&quot;t see any Ovation Alarm Analyser Tool installed on drop177 (in Control Panel --&gt; Add or Remove Programs)? (Quintos, Ronaldo M. Oct 31, 2012)<br><br>As I informed early, kindly look into the 3rd uploaded file named &quot;drop233_gateway_login_ste.doc. inwhich I have given the respective I.P addresses of those drops # 233,202,192,150 in OV 3.5.0,3.3.1,3.1.3,3.0.4 respectively where OVation Alarm Tool are installed. It&quot;s is not in drop#177. I am sorry since the name was same, I haduploaded the wrong files. Please remote into the above drops as per the 3rd file. (N, Thamaraiselvi Oct 31, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in (Benig, Ronaldo B. Dec 9, 2013).Generated the report in Ov3.5.1_U3 &amp; verified the report. Observed still the issue remains same in Ov3.5.1_U3. (N, Thamaraiselvi Jan 13, 2014).<br><br>Fix included in 3.5.1_U4 build. (Benig, Ronaldo B. Jan 20, 2014) <br> |  | 35 | FINDING | 9095 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74496
30221 | FINDING | 3.5_SRF1632_300-Multinet_SVTP_Rev1.3, Test 5.1.9.b is NA and the whole 5.1.9 test should be removed | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | 3.5_SRF1632_300-Multinet_SVTP_Rev1.3.docx - <br>Test 5.1.9: The Ovation Developer Studio will not increase the maximum of 31 concurrent actively mapped remote networks.<br>The limitation of 31 Remote Networks apply to Controllers only (test 5.1.10)<br>Therfore:<br>1. Test 5.1.9.b is NA and the whole 5.1.9 test should be removed.<br>2. the STP should state:<br>&quot;The Ovation Developer Studio will not increase the maximum of 31 concurrent actively mapped remote networks on Controllers.&quot; (Benzvi, Mati Oct 31, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Multi Networking (MN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2012-10-31T18:55:24-04:00</p> <p><strong>Modified Date:</strong> 2012-10-31T18:55:24-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9101 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74506
30224 | FINDING | OSR reports ISB 2.5 as "other installed software" | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | ISB2.5 is installes in the drop#233 0f OV 3.5.0 net#7. The report taken from the DBS server shows the software as &quot;other installed software&quot;. (N, Thamaraiselvi Nov 2, 2012)<br><br>I need access to your machine with this issue. Kindly email the remote login details and the drop name. (Quintos, Ronaldo M. Nov 13, 2012)<br><br>Fixed. Changes will be included in next release. (Quintos, Ronaldo M. Nov 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed already checked in. (Benig, Ronaldo B. Dec 9, 2013).<br>Generated the report in Ov3.5.1_U3 &amp; verified the report. FOund the issue has been fixed. Tnus closing the finding. (N, Thamaraiselvi Jan 13, 2014) <br> |  | 35 | FINDING | 9104 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74512
30227 | FINDING | Test case 5.5. in 3.5_SRF1584_SVTP_rev1.2 can be enhanced furthur for the clarification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | The test case of <br>5.5 TEST CASE 5: Oracle user credentials <br>-Verify that the 3.5.0 Sys Registration Utility captures data from the 3.5.0 Database station correctly.If it can be enhanced with the clear description of what exactly the Oracle user credentials, then it would be clear to the tester. (N, Thamaraiselvi Nov 2, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Ovation System Registration (OSR)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch N, Thamaraiselvi</p> <p><strong>Entry Date:</strong> 2012-11-02T02:37:12-04:00</p> <p><strong>Modified Date:</strong> 2012-11-02T02:37:12-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9107 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74517
30233 | FINDING | Some of the Algo cannot able to inject invalid calculted error number. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | As per the TP:3.5_SDR17703_SVTP_rev1.2_SKK. Step:5.1.1:Inject invalied calculted error number an algorithm.<br>The following algo we could not inject invalid calculted error number:<br><br>MASTATION,SETPOINT,ASSIGN,BILLFLOW,COUNTER,DISTRIBUTOR,HIGHLOMON,ONDELAY,OFFDELAY,ONESHOT,MEDIANSEL,QULITYMON,RATEMON,RSRSTATUS,RUNAVG,SATOSP,STATISTICS,PIDFF,FUNCTION,STEAMFLOW,STEPTIME,TRANSLATOR,X3STEP,XMA2,XML2.<br><br>we are using &quot;NAN&quot; &quot;negative Sqaure root value&quot; and &quot;divided by zero value&quot; to inject the invalid value to algo, even though we could not inject invalid calculted error number. (K, SendhilKumar Nov 2, 2012) (K, SendhilKumar Nov 8, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Algorithms (ALG)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> K, SendhilKumar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Boehmer, Robert W. K, SendhilKumar</p> <p><strong>Entry Date:</strong> 2012-11-02T08:48:33-04:00</p> <p><strong>Modified Date:</strong> 2012-12-05T16:10:19-05:00</p> | 0 |  | Ovation for Windows/General/Software | What do you mean &quot;we could not inject invalid calculated error number&quot;? Can you provide a screen shot for one of these algorithms to show how you have configured the test? (Boehmer, Robert W. Nov 2, 2012)<br>SKK:<br>I used &quot;NAN&quot; value as an input value to create invalid value.(This information we got from &quot;Plamowski, Sebastian&quot;(Developer)long back while we were testing APC3.2) The same method I had used for &quot;POLYNOMIAL&quot; algorithm. I could able to create invalid value also the SID number had received in the Ovationerrorlog.txt.(Please find the attached snapshot &quot;poly_nan&quot;)<br><br>But, In the SETPOINT &amp; MEDIANSEL algorithm, we are not able to create the same.(please see attachment &quot;mediansel_nan_used&quot; &amp; &quot;Setpt nan value&quot;).<br>Such a way, I found some algorithm which I could not create invalid value, I had raised as finding<br>(9113).<br><br>I used the other method also, the value from -1e+37 to 1e+37, apart from this value (Minimum or Maximum) as invalid value, Is it correct? if I am wrong please correct me.<br>I entered this value, even though, I could not generate invalid value for some algorithm which I had raised in this finding #9113.<br> <br>If this all method is wrong, then,please share with me the proper procedure to create the invalid value. (K, SendhilKumar Nov 8, 2012) <br> As discussed with Developer this finding changed against testcase<br>Testcase 5.1.2. need to be changed as below:<br><br>5.1.2 Test : Verify that if the invelid calculated number is entered into an algorithm, then SID number will be of LC record of the algorithm in error message. And verify that in error log, the error message displays the correct SID of the algorithm or the input SID to the algorithm. (K, SendhilKumar Dec 5, 2012) |  | 35 | FINDING | 9113 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | K, SendhilKumar PROCESS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74528
30234 | FINDING | In TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx, test case 5.23.2 i) is Not Applicable | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | In TR 3.5_CONTROLLER_SVTP_rev5.1_CG.docx, test case 5.23.2 i) says to verify changes to network connection state &quot;link fail&quot; sent to the Event Log targets.<br>However, as per developer, this test of &quot;link fail&quot; is not possible to reproduce for controller. Hence this test is Not Applicable &amp; needs to be removed from TR. (Gupta, Chandresh Nov 4, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2012-11-04T11:10:22-05:00</p> <p><strong>Modified Date:</strong> 2012-11-04T11:10:22-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9114 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74529
30236 | FINDING | A booted OCR sometimes get stuck in Startup Mode. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Automated soft reboots of OCR1100 Controller 32/82 (EMILY) were performed. During 5% of the reboots, a controller did not enter Backup Mode. It stayed in Startup until its partner rebooted (then it entered Control Mode). (Brown, Sean Nov 5, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Unable to recreate with the patch. Over 150 automated reboots were attempted without the issue occurring. Numerous items were addressed in the patch that affected timing, startup behavior, and network behavior. Continue to monitor the problem to check for recurrence. (Ciccozzi, Anthony Dec 11, 2012)<br><br>Cannot duplicate with OVA35005 or later. (Ciccozzi, Anthony Feb 20, 2013) <br> |  | 35 | FINDING | 9116 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74533
30249 | FINDING | SDR#18831: No negative Value should be shown for "SIS Data Server ID" is partially failed. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Validation of negative Value for &quot;SIS Data Server ID&quot; in studio iks working fine.<br>In Affected areas of SDR#18831 it is also written to test Ovptimport validation of <br>SIS Data Server ID so following steps were done:<br>On DBS drop250(net#8)Tried to import SIS items after editing the Database File manually by replacing SIS_DATA_SERVER_ID=&quot;1&quot; with SIS_DATA_SERVER_ID=&quot;-1&quot; refer attached(daily_SIS.lst file used for import.<br>On using command:<br>C:\Ovation\OvationBase&gt;ovptimport -u ptadmin/ptadmin@ptdb -s IVALSYS1 -esi D:\Releases\SIS_db\daily_SIS.lst<br> we got ORA realated error (refer attached error_import.txt).<br>On opening SDS properties under controller 23/73 it gives error nos:0x80004005 and SIS data server ID found in search of SDS is 424967295(refer attached SIS Data Server ID.jpg and sis_error.jpg).<br>Remote login step to DBS drop is attached.Also let us know how to restore this SDS under controller23/73. (Kumar, Shailendra Nov 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The validation check which was introduced to address SDR 18831 checked that the value of this attribute must be greater than or equal to 1. Unfortunately, by the time this check is performed, the attribute value is already reformated to its unsigned equivalent (424967295) which indeed is greater than 0. <br>The validation check will be updated to include an upper limit of 16 (since the maximum number of SIS Data Servers under an Ovation SIS I/O Interface cannot exceed 16.<br><br>In order to restore functionality for the validated system, the underlying data had to be updated in Oracle. This has been done. (Swartz, Mark E. Nov 8, 2012)<br><br>Please create an SDR so that this can be included in the Ovation 3.5 Engineering Tools patch. (Swartz, Mark E. Nov 8, 2012)<br>---<br>msb - Closed; Converted to SDR 19255 (Benzvi, Mati Nov 26, 2012) <br> |  | 35 | FINDING | 9129 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74558
30250 | FINDING | REF_1150 - SVD register 14 is duplicated in two sections | Skena, Ronald E AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Skena, Ronald E AUTOSOL PWS PITT | 2018-12-04 08:49 | [11 empty] | Skena, Ronald E AUTOSOL PWS PITT | 2018-12-04 08:49 |  |  |  | 2018-12-04 08:49 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | REF_1150 - SVD register 14 is duplicated in two sections 9.4.20 and in 9.4.22. <br>Section 9.4.22 documents register 13 so the register 14 info should be removed. (Capani, Nooch Nov 8, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9130 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | 3.5 |  |  | FINDING | [6 empty] | 135018
30268 | FINDING | The CJC channel (9) of the 8-Channel Compact Thermocouple Module is not correctly configured. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OVA350-002-11162012164852<br>Some configuration errors have been observed for the Channel 9 CJC point:<br>1. Register 0xE shows Bit 8 set when a point is assigned.<br>2. The I/O Bias, I/O Scale and I/O Card Type fields are incorrect. (Brown, Sean Nov 19, 2012) |  |  |  | The affected area is in the software responsible for calculating the hardware information for analog (and module) points assigned to both the 16-Channel Thermocouple module as well as the 8-Channel Compact Thermocouple module. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The software which calculates the hardware fields for the 8-Channel Compact Thermocouple module inadvertently was the same (for the most part) as the software used for the 16-Channel Thermocouple module. The items listed above in the description are indeed incorrect for the 8-Channel Compact Thermocouple module.<br>The following will be corrected for the 8-Channel Compact Thermocouple module:<br>1. Register 0xE Data (field WR) will only reflect points assigned to channels 1 through 8. This implies that only bits 0 through 7 will be updated.<br>2. The I/O Bias, I/O Scale, and I/O Card Type of channel 9 will be calculated to be consistent with the use of this assignment as the CJC Channel.<br>3. Register 0xE Mask (field WI) will have a value of 0xFF, to be consistent with the fact that only the first 8 bits are used to indicate channel assignments. (Swartz, Mark E. Nov 19, 2012)<br><br>Addressed in OVA350-002-11262012151419. Closing. (Brown, Sean Nov 27, 2012) <br> |  | 35 | FINDING | 9148 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | OVA350002 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74594
30270 | FINDING | VcoordinateManger GUI Sim Control GUI should be corrected. | Perdeus, Matthew AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Reference:SDR#19147-The status of a Failed VxSim Virtual Controller is now shown correctly <br>(Failed) in VcoordinateMnager GUI but its Control column is blank. Therefore it is not possible to Start/Stop the Failed VxSim Virtual Controller from the GUI.One has go to Developer Studio to to do so. You may consider giving Start/Stop option to Failed VC as well in the GUI similar to VC in normal state.<br>Reference:SDR#19146- In SimControl GUI Freeze, Save, Load,Run commands are working alright but Error log still shows <br> &quot;Error receiving reply, ret=7<br> No response from -- &quot;<br>It should be cleaned up. Please refer the attached screenshot of the error log. (Lal, Ramesh Nov 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Reference SDR 19147 - WAD. A failed controller will not respond (most likely) to these commands. Having the Start/Stop visible would be deceiving.<br><br>Reference SDR 19146 - MIR. Please check the drops.cfg file. It appears there is a blank line in the file. The &quot;No response from&quot; is a blank line. (Perdeus, Matthew Nov 20, 2012)<br><br>Reference SDR 19147 -Will it be possible to provide &quot;Reboot&quot; instead? The purpose is that user <br> need not to go to Studio to restart the Failed VC.<br>Reference SDR 19146 -1.There is no blank line in the drops.cfg file.<br> 2.Please note that for Load command error text is &quot;Error receiving reply for<br> Load Command, ret=7&quot;<br>Please refer the attached screenshot. (Lal, Ramesh Nov 22, 2012)<br><br>Reference SDR 19147 - The GUI is not meant to be a replacement for Studio. It is mainly to give a local status of hosted VCs.<br><br>Reference SDR 19146 - The line after the &quot;No response from&quot; is a blank line, not a drop. Please send actual drops.cfg file, not a snapshot. (Perdeus, Matthew Nov 26, 2012) <br> 11/27/12:RL-<br>Reference SDR 19147 - Then let us ignore this issue.<br>Reference SDR 19146 -drops.cfg which was used for testing is attached for your reference. (Lal, Ramesh Nov 27, 2012). <br>Matt, drops.cfg file was not uploaded in correct format. Therefore, please refer drops.cfg.txt file. (Lal, Ramesh Nov 27, 2012)<br><br>Reference SDR 19147 - OK. WAD.<br>Reference SDR 19146 - There are two blank lines at end for drops.cfg file. Please remove these and retest. (Perdeus, Matthew Nov 27, 2012)<br>12/11/2012:RL - The issue has since been resolved per guidance from Matt, refer email@12/10/2012.<br>Finding closed. (Lal, Ramesh Dec 11, 2012) |  | 35 | FINDING | 9150 |  | FINDING | Staab, Randy AUTOSOL PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74598
30272 | FINDING | PWSIT - Ovation lost communication with gateways during weekend AMS Scan device soak test | Swartz, Mark EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | PWSIT Ovation System 2 has:<br>- 1 set of redundant gateway (30 devices @4s burst rate except for THUMs and wired devices) <br>- 1 simplex gateway (60 devices @8s burst rate).<br>An automation script was setup to continuously scan all devices on redundant gateway for 3 days. <br>During the soak test, AMS starts to loose communcation with gateways and was not able to scan devices again.<br>Check in Ovation Engineering tool, it wasn&quot;t able to see neither gateway (simplex and redundant). See attached for detail.<br><br>Way to recovered the gateways:<br>On redundant set<br>- swith over gateway via Gateway Web Interface<br>- launch Gateway Engnineering tool in Ovation Developer studio<br>- load controllers<br>On simplex set<br>- same as redundant except power cycle gateway instead.<br><br>Also attached are gateways backup files with diagnostic information. (Phan, Quang Nov 20, 2012)<br><br>More information: the system has new controller OCR1100. (Phan, Quang Nov 20, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Wireless HART (WH)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Phan, Quang</p> <p><strong>Responsible:</strong> Swartz, Mark E.</p> <p><strong>Notify List:</strong> Swartz, Mark E. Phan, Quang Capani, Nooch</p> <p><strong>Entry Date:</strong> 2012-11-20T10:35:03-05:00</p> <p><strong>Modified Date:</strong> 2013-09-23T07:08:51-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9152 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74601
30275 | FINDING | After patch installation of OVA350_Patches_11172012.ELC is stop working on OV 3.5.0. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | after installlation of Ovation patch OVA350_Patches_11172012 (OVA350-002).ELC is not working on ovation 3.5.0 as earlier it was working .if we try to open ELC configration tool from Studio it gives error pop up that application is unable to open . (Sharma, Vaibhav Nov 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Patch OV350002 Fixed.<br>- (Hutchison, Steven B. Nov 28, 2012)<br>----<br>msb - Ok with OVA350-002<br> Madhukar 11/27 - The ELC tool issue has been fixed after loading the patch OVA350002 <br>- (Benzvi, Mati Nov 28, 2012) <br> |  | 35 | FINDING | 9155 |  | FINDING | Sharma, Vaibhav PROCESS PWS NOIDA | [9 empty] | Implementation | OVA350002 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Vaibhav PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74606
30280 | FINDING | "RegSvcs.exe - Common language runtime debugging services" warning appears during OV3.5.0 installation. | Burgoon, Frank AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | I used Ov3.5.0 final release CD for Ovation installation on a new fresh Win7 64-Bit (SP1) Machine. During Ov3.5.0 installation one error message related to ¿Common language runtime debugging services¿ is observed 2 times. After selecting ¿Ok¿ Ovation software installed successfully. Please refer Snapshot &quot;Ov350_Installation_Error.jpg&quot;. (Singh, Rajan Nov 22, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Singh, Rajan</p> <p><strong>Responsible:</strong> Burgoon, Frank J.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Singh, Rajan</p> <p><strong>Entry Date:</strong> 2012-11-22T23:40:53-05:00</p> <p><strong>Modified Date:</strong> 2012-11-22T23:40:53-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9160 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74614
30281 | FINDING | T2 should be replaced by T3 in some places of SVTP. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Regarding OV.3.5.0 SVTP, at 3.5_STRESS_SVTP_rev1.0_SM, in 5.7 TEST CASE 7: Full Logic Controller, T3 is not present at Cycle and IO #s. T2 is there twice. (Mitra, Sambuddha Nov 23, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> System Test (ST)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Mitra, Sambuddha</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Mitra, Sambuddha</p> <p><strong>Entry Date:</strong> 2012-11-23T02:07:38-05:00</p> <p><strong>Modified Date:</strong> 2012-11-23T02:07:38-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9161 |  | FINDING | [15 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74615
30287 | FINDING | An OCR1100 reports MAIN task stopped after startup. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OVA350-005-11132012142434<br>OCR1100 Controller 32/82 (EMILY) reports the following messages:<br>0x138384c (main): task 0x138384c has had a failure and has been stopped.<br>0x138384c (main): fatal kernel task-level exception! (Brown, Sean Nov 26, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected a string handling function for SPF type to prevent a buffer overflow (Christy, Benjamin Nov 26, 2012)<br><br>IC 12/11/12 Val+Dev mtg- not required to be fixed for 3.5 Dec patches. Create SDR for next patch release. (Capani, Nooch Dec 11, 2012)<br><br>IC 12/28/12 - closed, track as SDR 19299. (Capani, Nooch Dec 28, 2012) <br> |  | 35 | FINDING | 9167 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74626
30293 | FINDING | While adding the license code of custom protocol to license manager ,developer studio crashed | Spillane, Donal AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 5 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | When we added the license code , 9797 5229 9832 8682 9204 8626 5522 646 of custom protocol to license manager ,developer studio crashed first ,<br> after that we reopened the devolper studio and added the license code again , &quot;error 19 &quot; pop up appeared in the studio.<br><br>Please find attached snap shots of error messages obtained during first time (License_error_1.jpg) and the second time (License_error_2.jpg).<br><br>The license code of other two protocols are successfully added to license manager (Scada Generic Protocol and Scada RTU Protocol )<br>And we have obtaind the licence of DNP3.0 Server, DNP3.0 Client, IEC-870, IEC-870 Simulator, IEC-61850, Bristol Open BSI Modbus Slave, <br>Modbus Master, Modbus Master Buffered and A-B client. (Jayarajan, Jayakumari Nov 28, 2012)<br><br>This issue occured in Drop250_OV3.5 server (Jayarajan, Jayakumari Nov 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | More information required. <br>There is only one attached snap shot (License_error_1.jpg), when the Description above references two.<br>Please note that License_error_1.jpg shows that the application fault is with license.exe, not with OvPtStudio.exe.<br>Please clarify. (Swartz, Mark E. Nov 28, 2012)<br><br>Please find the following snapshots and error details missed to attach along with the finding<br><br>1. Error-1.jpg(This snapsot shows the message comes , when we added the license code)<br>2.error_details.txt(The message in the Error-1.jpg is copied and pasted in to this text file)<br>3.Error-2(Error 19 message ) (Jayarajan, Jayakumari Nov 30, 2012) (Jayarajan, Jayakumari Nov 30, 2012)<br><br>The application is the Ovation License Manager UI, not the Ovation Developer Studio. (Swartz, Mark E. Nov 30, 2012) <br> IC 12/7/12 Val + Dev mtg - related to custom protocols which are not typically used/needed. MNR as Ov 3.5 item. (Capani, Nooch Dec 10, 2012) |  | 35 | FINDING | 9173 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Plymire, Alvan AUTOSOL PWS PITT | [8 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74638
30300 | FINDING | Installing ovation patch "OVA350002" crashing the graphic builder by performing some operation. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Ovation patch &quot;OVA350002&quot; is installed. installed successfully with no problem.<br>Now open graphic builder from developer studio and click on menu option &quot;Browse points&quot;<br>==&gt; GBNT window getting crash and closed.<br>please find attached the snap shot. <br>Note: Removing the obove patch is not crashing the above operation. (Joshi, Parmesh Nov 29, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Need to re-release the patch to also include wesengr.dll (used by gbnt) (Johnson, Kathy Nov 30, 2012)<br>---<br>msb - OK in OVA350-002_12032012 @ 03-Dec-2012<br> New wesengr.dll 12/03/2012 was added to the patch<br> GBNT -&gt; &quot;Browse Points&quot; - OK (Benzvi, Mati Dec 3, 2012) <br> |  | 35 | FINDING | 9180 |  | FINDING | Joshi, Parmesh EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350002 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74652
30320 | FINDING | Test case 3.5_SRF1361_SVTP_rev1.0.doc needs some modifications. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Following modifications are required in test case 3.5_SRF1361_SVTP_rev1.0.doc.<br><br>1. In Procedure 14 of test case 5.4.3 it is mentioned<br> &quot;In the Live List Viewer, click the Refresh button.<br> See comments for step verification&quot;.<br> But in verification step 12 is noted instead of step 14.<br>2. In Procedure 9 of test case 5.4.7 it is mentioned<br> &quot;Click Refresh on the Live List Viewer. You may need to click refresh a few times.<br> See comments for step verification&quot;<br> But in verification step 8 in mentioned instead of 9.<br>3. In Procedure 5 of test case 5.4.8 it is mentioned<br> &quot;Right click on the device in the Studio, and select open if not already opened, then <br> click Refresh.<br> See comments for step verification&quot;.<br> But in verification step 3 in mentioned instead of 5.<br>4. In Procedure 18 of test case 5.4.8 it is mentioned<br> &quot;Right click on the newly commissioned device in Studio and select Open.<br> See comment for step verification.&quot;<br> But in verification step 7 in mentioned instead of 18. (Sahay, Madhukar Dec 4, 2012) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> WIN Studio (WST)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2012-12-04T09:11:30-05:00</p> <p><strong>Modified Date:</strong> 2012-12-04T09:11:30-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9200 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74691
30321 | FINDING | Brwose points does not returns to Points tab at end of search on busy system | Johnson, Kathy EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-04-08 08:58 | [11 empty] | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-04-08 08:58 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | When browsing on Points in GB from a NON-DBS station on a system with many points, <br>the browse seems to get stuck at the &quot;Generating Attributes&quot; step. <br>The &quot;Server Busy&quot; popup sits on top of the Search screen - forever?!<br>and the Browser does not jump from the Filters tab to the Points tab, as it should when <br>the search is complete.<br><br>I duplicated it on Emily network with 150K points, on controllers with 32k, 16k or 6k points.<br>Donal found it too on his own system.<br><br>However, if you click on another screen outside of GB and click back on the GB icon again, <br>the Browser reopens in the Points tab and shows all the points.<br><br>It did not seems to occur on the Glenn network that have much fewer points, or on drops in Emily network with only few 100s points. (Benzvi, Mati Dec 4, 2012) (Johnson, Kathy Dec 6, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9201 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Johnson, Kathy EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | 3.5.0_OVA350_Patches |  |  | FINDING | [6 empty] | 94631
30343 | FINDING | SDR-19220 fail after loading patch OVA350003. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Hierarchy Search is not working properly in Ovation System Viewer window after load patch OVA350003 commissioned and alert searches is not working properly. (Kumar, Sudheer Dec 7, 2012)<br>---<br>msb - WALT network - drop16 -<br> Select both: Commissioned, Uncommissioned = 75<br> Commissioned (CO) = 38<br> Uncommisioned (UC) = 37<br> Select All Alerts: = 1 (with FS)<br> Failed (FS) = 1<br> Communication (CS) = None - At least 5 devices are in CS alert.<br> Therefore, Filter: FB Commission - Work OK<br> Filter: Alerts - Not (Benzvi, Mati Dec 12, 2012)<br><br>from sdr 19220:<br>msb - OK in Ov.3.5.0 + OVA350-015 @ 22-Mar-2013 (sdk) (Benzvi, Mati Mar 24, 2013) (Wozniak, Diane M. Jul 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9223 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74735
30351 | FINDING | Ovation System Viewer crashes while refreshing the drop list after drop-add or drop-delete | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | When a System Viewer is opened while a drop is added or deleted from the system, after the drop is loaded, the Viewer is prompted to refresh the drop list, by User selection or<br>auto-refresh after few seconds. <br>When the Refesh occurs the System Viewer UI crashes.<br>When reopened the new selected drop is added or deleted as expected.<br>(For steps, see test records of SDR 19153). (Benzvi, Mati Dec 9, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 12/11/12 Val+Dev mtg- not required to be fixed for 3.5 Dec patches. Marked as MFX (May Fix). If Dev decides to fix this in a future patch, we will close the finding and open an SDR. (Capani, Nooch Dec 11, 2012)<br>---<br>msb - Closed: Converted to SDR 19454 (Benzvi, Mati Mar 5, 2013) <br> |  | 35 | FINDING | 9231 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74751
30356 | FINDING | Import window of grahics stopped working while importing the macros | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following steps were done for testing purpose<br><br>Opened the import window by right clicking the diagram option in Graphics <br><br>Selected the folder that contains the macro by browsing <br><br>Then the import window of grahics stopped working<br><br>Please find the attached snap shots for reference (Jayarajan, Jayakumari Dec 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Need to re-release 3.5.0 patch to include import_graphics.exe (because OvPt server code changed). (Johnson, Kathy Dec 10, 2012)<br><br><br>After loading the patch OVA350-002-12102012 it is found that macros are imported properly (Jayarajan, Jayakumari Dec 11, 2012) <br> |  | 35 | FINDING | 9236 |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350002 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74762
30362 | FINDING | After Load the Controller Diagnostic Tool is not showing the sheet information. | Ciccozzi, Anthony AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | 1. Add New sheet with APC algorithms or Standard Algorithms.<br>2. Compile successfully and Load the Controller (we used Redundant VCH &amp; VC).<br>3. Verify the Controller Diagnostic Tool is showing the sheet information (New Loaded sheet)<br>4. Sometimes it is not displaying the loaded sheet information and this is cause user could not be operate from signal diagram. <br>5. Please find the attachment(Command execution is not possible from the signal diagram) <br>6. We observed this Occasionally, after 2 or 3 times controller load and doing some other operations it&quot;s getting normal (till now we faced this situation more than 10 times but not frequently). (K, SendhilKumar Dec 10, 2012) (Ciccozzi, Anthony Dec 10, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Not enough control memory was allocated for the control task. The control task was at 99% capacity. Not all of the sheets could be loaded. There were other sheets missing from controller diagnostics. When the Sheet Set Size, in the control task configuration, was increased from 65000 to 165000, all of the sheets could load (after performing a download, clear, and load with the new Sheet Set Size). The attached document shows more detail. (Ciccozzi, Anthony Dec 10, 2012)<br><br>SKK:<br>There were no error message observed in developer studio while we loading the APC sheet.It suppose to show some pop message so that user can expand the memory size.we could consider this as enhancements. (K, SendhilKumar Dec 11, 2012)<br><br>Please see the attached documents (finding9242Info.docx the same file attached as a .rtf file - some browsers have trouble with the .docx format). A pop-up message does appear when loading the controller indicating not enough control task memory. If the &quot;Move Sheet Failed&quot; pop-up appears, this means a failure occurred during a previous load. When this occurs, clear the controller and reload - the initial error will be indicated (as was done here with the not enough control task memory message). (Ciccozzi, Anthony Dec 20, 2012) <br> |  | 35 | FINDING | 9242 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | K, SendhilKumar PROCESS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74774
30364 | FINDING | SDR19221, partially fail as Attributes for SIS still shows few dispcrepancies. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Attributes for SIS shows few dispcrepancies as listed below: ( SDR19221, partially fail)<br>1&gt; Under Point attributes for SDS: RNHILK IO Module is seen instead of Ovation Point name. Kindly find the attached 19221-SIS-sds01.jpg<br>2&gt; Under Point attributes for SLS: Both RNHILK IO Module and Ovation Point name are seen instead of Ovation Point name only. Kindly find the attached 19221-SIS-SLS02.jpg<br>3&gt; Under SIS IO Channel: (a) CRC for individual I/O channel shows some point name which is not the CRC as actually seen in Developer studio. Kindly find the attached 19221-SIS-CH-CRC.jpg <br>4&gt; Under Point attributes for Control Modules: (Both RNHILK IO Module and Ovation Point name are seen instead of Ovation Point name only. Kindly find the attached 19221-SIS-Control Module.jpg<br><br>Kindly find the SDR19221.zip file for all the above mentioned jpegs. (Sachan, Pallavi Dec 11, 2012)<br><br><br>These issues should be resolved with the following exception:<br>Open items #3 crc for individual i/o channel is not a systemviewer problem (Wozniak, Diane M. Mar 5, 2013) (Wozniak, Diane M. Jul 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 12/11/12 Val+Dev mtg- not required to be fixed for 3.5 Dec patches. Marked as MFX (May Fix). If Dev decides to fix this in a future patch, we will close the finding and open an SDR. (Capani, Nooch Dec 11, 2012)<br><br>PS 22MAR13: <br>It is observed that Point attribute tab is removed from 1&gt; SDS, 2&gt; SLS and 4&gt; Control Modules, while the issue reported under <br>3&gt; SIS IO Channel still remains - CRC for individual I/O channel shows some point name which is not the CRC as actually seen in Developer studio.<br><br>Hence status of F#9244 is Changed to Open Failed Retest and SDR19221 status is changed to SDR Failed Partially, Finding Written. (Sachan, Pallavi Mar 22, 2013) <br> |  | 35 | FINDING | 9244 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | MFX |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74778
30369 | FINDING | SDR#19217:SNR firmware upgrade tool hangs when there is an attempt to upgrade disconnected device is failed. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Following step was done on DBS drop250 of SIS network(loaded with OVA350006 patch):<br>SIS net repeater of SDS02 is in OFF state.<br>1)Ran Firmware upgrade tool from C:\Ovation\Ovationbase<br>2)In Console gave Ip address of SDS02 , entry for net redundancy and then path of idf file.<br>3)After pressing enter it gives message &quot;adding host to cache Hosts in cache:1 &quot;(refer attached snapshot)<br>It hangs at this point and after 20 minutes tool closes by itself without giving any error or message. (Kumar, Shailendra Dec 11, 2012)<br><br>Note :Tool upgrades the SNR firmware to version 2.1 if SNR in ON state. (Kumar, Shailendra Dec 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 12/11/12 Val+Dev mtg- not required to be fixed for 3.5 Dec patches. Marked as NAR and closed this finding since this issue will continue to be tracked as SDR 19217. Mati wil have to document that this SDR is NOT in the Dec patches (OVA350006). (Capani, Nooch Dec 11, 2012) <br> |  | 35 | FINDING | 9249 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74788
30371 | FINDING | Start/All Programs/Ovation/Ovation Applications/On-Line Help is not opening on few 64-bit Ovation drops | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | On few 64-bit Ovation drops (230, 232, 235), OnLine Help is not opening from the shortcut located at Start/All Programs/Ovation/Ovation Applications. Upon doing so it gives 1st Error message: Missing Shortcut Windows is searching for HH.exe. To locate the file yourself, click browse. After few seconds, 2nd Error message: Problem with Shortcut The item &quot;HH.EXE&quot; that this shortcut refers to has been changed or moved... [Fix it] [delete it]. Once clicked on [fix it] the online help is displayed. The path for hh.exe program in the mentioned drops is not same as the &quot;WINDIR&quot; environment variable (C:\Windows). Instead, it is pointing to &quot;C:\Windows\system32&quot;.<br>This issue was fixed for the shortcut in the Ovation Applications folder found on the desktop (SDR19119) via patch OVA350003. (Gupta, Chandresh Dec 11, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 12/11/12 Val+Dev mtg- not required to be fixed for 3.5 Dec patches. Marked as MFX (May Fix). If Dev decides to fix this in a future patch, we will close the finding and open an SDR. (Capani, Nooch Dec 11, 2012) <br> |  | 35 | FINDING | 9251 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | MFX |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74792
30377 | FINDING | Not able to view other network filter in Alarm, Operator Event, SOE & ASCII | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | OV:- OV 3.5.0<br>Used patch:- OVA350003<br><br>It is observed that, Network/Unit option is available in Alarm, Operator Event, SOE &amp; ASCII. But when comparison between above option &amp; Point tab Network/Unit option than we saw that we are able to select other network from Point tab option But from the other option (e.g.:- Alarm, Operator Event, SOE &amp; ASCII option) we are able to select either local network or all network. <br><br>As per tester point of view, both windows should be same.<br><br>For more information please find the attached screen shots (Alarm filter.jpg, Point filter.jpg) (Agarwal, Gaurav Dec 12, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The lists of available networks are derived via different means. The point&quot;s list is via Ovation system calls, and the message list is via an OPH query. The OPH query determines available systems by where the different types of scanners are deployed. It is possible that the list of available systems will be different between points and messages, and between messages types themselves - if each system does not have all scanner types. The current implementation is the best that can be achieved using existing infrastructure, and provides the user with valuable filtering capability that did not previously exist. (Contento, James L. Dec 13, 2012)<br><br>As per Developer comment , Findfing is closed. (Agarwal, Gaurav Feb 20, 2013) <br> |  | 35 | FINDING | 9257 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74804
30378 | FINDING | In Non ovation system, help file is not opening in Historical review & Historical Trend. | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It is observed in non ovation system that in Historical Review &amp; Historical Trend , help file is not opening. (Agarwal, Gaurav Dec 13, 2012) | The issue, &quot;help file is not opening in Historical review &amp; Historical Trend&quot;, would be rectified in the next build of the OPH341 software (March 2013), which would contain the latest help files. |  |  | PS (5-Mar-2013): The OPH 341 manual is now complete and released. FYI, the latest OPH 341 files are placed at the following path: * PDF file is in Q:\Communication\TechComm\Share\OPH341_Final\OH341_70.pdf * CHM (Help) files are in M:\sourceintegrity\TechWriters\OVH_3.4.1_CHMs | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | PS (5-Mar-2013): The OPH 341 manual is now complete and released. The issue, &quot;help file is not opening in Historical review &amp; Historical Trend&quot;, would be rectified in the next build of the OPH341 software (March 2013), which would contain the latest help files.<br><br>FYI, the latest OPH 341 files are placed at the following path:<br>* PDF file is in Q:\Communication\TechComm\Share\OPH341_Final\OH341_70.pdf<br>* CHM (Help) files are in M:\sourceintegrity\TechWriters\OVH_3.4.1_CHMs (Sharma, Puneet Mar 5, 2013) <br> PS (19-Jan-2015): As this issue pertains to OPH341 and seems to be fixed, I am closing this finding. (Sharma, Puneet Jan 19, 2015) |  | 35 | FINDING | 9258 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | OPH341_Patch_Mar2013 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74806
30379 | FINDING | In Historical Review help file, Detail of Network/Unit option are not available. | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | It is clear from the screen shots (N-W help unavailable.jpg) that in Alarm Tab, Network/Unit option detail are not available in help file.<br><br> Same issue observed in Operator Event, SOE &amp; ASCII tab. (Agarwal, Gaurav Dec 13, 2012) | PS (5-Mar-2013): Documentation is already updated to include the Network/Unit option in the Historical Reviews section. The next build of the OPH341 software (March 2013) would contain the latest help files. |  |  | PS (5-Mar-2013): Documentation is already updated to include the Network/Unit option in the Historical Reviews section. The latest files are placed at the following path: * PDF file is in Q:\Communication\TechComm\Share\OPH341_Final\OH341_70.pdf * CHM (Help) files are in M:\sourceintegrity\TechWriters\OVH_3.4.1_CHMs | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | PS (5-Mar-2013): The OPH 341 manual is now complete and released. Documentation is already updated to include the Network/Unit option in the Historical Reviews section.<br>The latest files are placed at the following path:<br>* PDF file is in Q:\Communication\TechComm\Share\OPH341_Final\OH341_70.pdf<br>* CHM (Help) files are in M:\sourceintegrity\TechWriters\OVH_3.4.1_CHMs<br><br>The next build of the OPH341 software (March 2013) would contain the latest help files. (Sharma, Puneet Mar 5, 2013) <br> PS (19-Jan-2015): As required changes are already done in the OPH manual, I am closing this finding. (Sharma, Puneet Jan 19, 2015) |  | 35 | FINDING | 9259 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | OPH341_Patch_Mar2013 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74808
30391 | FINDING | In Historical Review, Limit checked removed filters is not working properly. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Create a Limit checked removed in a point.<br>1:- Open the Historical review &amp; Enable the Limit checked removed filter.<br>2:- Set the time duration in which, Limit checked has created &amp; Press Start Historical Review button. <br>3:- Historical review show that with the Limit checked , Alarm checked is also appear in same page.<br> As shown in screen shots (AR &amp; LR1.jpg) (Agarwal, Gaurav Dec 13, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This behavior implementation precedes the current historian product. Reason for this specific implementation is unknown. We have no current plans to change this behavior. (Contento, James L. Nov 4, 2013)<br><br>GA:-<br>As per developer, Finding is closed. (Agarwal, Gaurav Jan 27, 2014) <br> |  | 35 | FINDING | 9271 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74831
30395 | FINDING | "Set time" not working properly in "Historical review" of Ov3.5.0. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | &quot;Start time &amp; end time&quot; in &quot;Time span&quot; tooltab under &quot;Alarm&quot; review tab is not working expectedly.<br>It gives no error for wrong time span entry, and process goes on.<br>Find attached snapshots and correspoinding exported log file. (Jain, Yukta Dec 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja. Fixed. Next update will have the changes. Error text will be displayed in status window. (Matreja Shyam Jan 28, 2013)<br><br>YJ:Fixed in patch OVA-350013 (Jain, Yukta Mar 31, 2013) <br> |  | 35 | FINDING | 9275 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | OVA350013 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74839
30396 | FINDING | SDR19236, partially fail as functional block details show dispcrepancies in OSV. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Attributes for Foundation Field Bus/ Profibus /DeviceNet show few dispcrepancies as listed below: ( SDR19236, partially fail)<br><br>Under Functional block details for Foundation Field Bus module, the Next Block in Sequence parameter is shown as some numerical value instead of the point name as seen in Studio.<br>Eg. In Studio the &quot;Next Block in Sequence&quot; parameter: &quot;848T-P01/FFAI2&quot;, this is shown as &quot;175420&quot; in OSV.<br><br>For Profibus Modules, the Point Attribute Window for Device shows INPUT and OUTPUT details which are not seen in Studio.<br><br>For DeviceNet Modules, the Point Attribute Window for Device shows INPUT and OUTPUT details as PHILK IO modules which are not seen in Studio.<br><br>Rest all the places in FieldBus/ Profibus/ DeviceNet ,the RM point attributes are denoted as RHILK IO module instead of Ovation Point Name and the RN point attributes are <br>denoted as RNHILK IO module instead of Ovation Point Name. (Sachan, Pallavi Dec 14, 2012)<br><br>from sdr 19236:<br>msb - OK in Ov.3.5.0 + OVA350-015 @ 22-Mar-2013 (ps) (Benzvi, Mati Mar 24, 2013) (Wozniak, Diane M. Jul 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9276 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74841
30397 | FINDING | Progress status window displays wrong information in "Historical review" of Ov3.5.0. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:04 | [11 empty] | USPITTFSService | 2015-06-12 04:04 |  |  |  | 2015-06-12 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:04 |  | Progress window displays wrong information- &quot;Preparing to print&quot; on exporting &quot;Alarm&quot; logs from &quot;Historical review&quot;.Find attached snapshot. (Jain, Yukta Dec 14, 2012) |  |  |  | perform export and see if it is fixed. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja. Fixed. Next update will have the changes (Matreja Shyam Jan 28, 2013)<br><br>YJ:Resolved. (Jain, Yukta Apr 1, 2013) <br> |  | 35 | FINDING | 9277 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | OVA350013 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74843
30407 | FINDING | SOE Review of SIS SOE points is not comming. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:04 |  | Defined DI channel of SLS01 to SOE.This point is used at multiple LSDI algos.<br>Changed Value from O to 1 and then back to 0.Done Hist review but nothing comes.<br>On same controller if Ovation SOE point review is done with Ovation SOE module it is working fine.<br>SYStem is is loaded with OVA35002,OVA35005 patch. (Kumar, Shailendra Dec 14, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <br> |  | 35 | FINDING | 9287 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30421 | FINDING | Trend sometimes shows "Point not found" for description after adding points using Historian option. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Live Trend sometimes shows &quot;Point not found&quot; for description after adding points using Browse point using Historian option.These points are already having some description.This is generally seen when new trend window is opened and directly added points from historian.<br>For reference attached the snapshot and remote login steps of the drop where it was observed. (Kumar, Shailendra Dec 20, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | It isn&quot;t clear what steps are to be followed to recreate this problem. Please describe in more detail. Also, no remote login instructions were provided. (Contento, James L. Dec 20, 2012)<br><br>SK:Following steps were done:<br>1)Opened blank trend window ,&lt;Browse point&gt;, select Point source as:Historian.<br>2)Open PointName/Description filter in this browse window and entered *OPH*,pressed&lt;ok&gt;,Then &lt;Start&gt;, double clicked point name :OPH1-TAS0K01-LD-A-A.UNIT0@FE241,OPH-231-DD.UNIT0@FE350 and OPH-231-LA.UNIT0@FE350,Then pressed &lt;OK&gt;.<br>3)Trend opens with description as Point not found although Values,EU are displayed and updated correctly.<br>Attached is the login steps of drop174 (win7,32 bit) and snapshot(trend_description.jpg). (Kumar, Shailendra Dec 21, 2012)<br>---<br>msb - Closed: Converted to SDR 19340 (Benzvi, Mati Jan 15, 2013) <br> |  | 35 | FINDING | 9301 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74889
30437 | FINDING | SDR19223/SRF1722/OVA350002: A/C Line Frequency is no longer used and affects module operation. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR19223/SRF1722/OVA350002: A design change to the 16-Channel and 8-Channel Compact TC modules removed Bit 9 (A/C Line Frequency) as a configurable bit. A 1 in Bit 9 of the D Register Mask prevents the module from operating correctly. (Brown, Sean Dec 21, 2012)<br><br>In addition, the IT field of the RM point assigned to these modules was incorrect. Was 0x40001302 and should be 0x40171202, utilizing pcl data type RLINE_MODULE_D_C (0x12) and ioic access type PCXL_DPR_ACCTYPE_TYPE_SCAN_D_C_15 (0x17). (Swartz, Mark E. Jan 3, 2013) |  |  |  | The affected area is in the software responsible for filtering the list of Ovation module attributes to those applicable to a specific Ovation module during configuration/edit via the Ovation Developer Studio. In addition, the software responsible for generating the hardware information for RM points has been changed to treat bit 9 of the Configuration Register D (data and mask) for the specified Ovation modules. Note that for testing purposes, the user must modify either the configuration of the specified Ovaiton modules or any field of the associated RM point via the Ovation Developer Studio -- followed by a load to the Ovation controller. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The engineering tools software will be changed to remove the A/C Line Frequency attribute from the list of attributes applicable to these Ovation modules. This will also result in bit 9 of the D Register Mask from being set to 1.<br>Note that a work-around with the existing software would be to configure the module for 50 Hz -- this results in a 1 being set in bit 9 of the D Configuration Register, which is the same as the reserved read-back value of the bit. This will prevent the Ovation controller from continually attempting to configure the module.<br><br>Once this software change has been deployed to an Ovation system which already utilizes these Ovation modules, the user must modify either the I/O Module itself or the associated RM point (any attribute will suffice) via the Ovation Developer Studio -- followed by a load to the Ovation controller. (Swartz, Mark E. Jan 3, 2013)<br><br>Addressed in OVA350015; closing. (Brown, Sean Apr 3, 2013) <br> |  | 35 | FINDING | 9317 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Piper, Timothy EMR SYSS PWS PITT | [8 empty] | Implementation | OVA350015 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74921
30438 | FINDING | Patch OVA350002 is forcing a reboot on all drops and on every Update installation run | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Patch OVA350002 has the [Priority Reboot Required] box checked to force a reboot after <br>patch is installed on the DBS drop, for OvPtBridge upgrade. <br>However, the FORCED reboot is also unnecessarily enforced:<br>a. On the DBS, on a subsequent install when the patch is already installed.<br>b. On all other stations on the Ov-3.5.0 network.<br>The install tool should enforced the reboot only on the DBS and when the patch is not already installed on it. (Benzvi, Mati Dec 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. (Matreja Shyam Jan 3, 2013)<br>---<br>msb - OK in &quot;Ovation 3.5.0 December 2012 Update-01042013111229&quot; @ 04-Jan-2012<br> Reboot is forced only on DBS after OVA350-002. (Benzvi, Mati Jan 4, 2013) <br> |  | 35 | FINDING | 9318 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | OVA350_Dec12_Update |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74923
30439 | FINDING | OVA350 install program displays a popup error for every inapplicable patch | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | OVA350 Dec12 Update installs patches on drops:<br>DBS - 002, 003, 004, 005, 006, 007<br>Eng - 002, 003, 004, 006, 007<br>Base- 002, 004, 007<br>When the Update install runs on Eng or Base drops, for each inapplicable patch, the Install<br>program displays a popup error:<br> =======================================<br> patch not applicable for this drop type<br> Setup will be aborted<br> =======================================<br>The install program should silently skip over inapplicable patches, just as the Pre-OVA350<br>install program used to do. (Benzvi, Mati Dec 21, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed. (Matreja Shyam Jan 3, 2013)<br>---<br>msb - OK in &quot;Ovation 3.5.0 December 2012 Update-01042013111229&quot; @ 04-Jan-2012<br> No Popup observed on Base &amp; Eng stations during reinstall. (Benzvi, Mati Jan 4, 2013) <br> |  | 35 | FINDING | 9319 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | OVA350_Dec12_Update |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74925
30463 | FINDING | Incorrect labels in Configure Settings dialog box | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | In (Format Ribbon Tab)/Configure Display Settings dialog box, the (General Tab)/Chart <br>Grid-lines section does not have correct labels for primary grid-lines color and <br>secondary grid-lines color. (Benzvi, Mati Dec 28, 2012) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Prashant - The Attached image shows how the correct labels will look in the fixed version. (Benzvi, Mati Dec 28, 2012)<br>---<br>msb - Closed: converted to SDR 19341 (Benzvi, Mati Jan 15, 2013) <br> |  | 35 | FINDING | 9343 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74970
30469 | FINDING | A new trend continues to display the title of previously opened TGD file | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | When a new LIVE or HISTORICAL trend is started from the &quot;Trend Application Menu / New <br>(Live or Historical Trend)&quot;, the title of the Trend main window does not change to <br>&quot;Untitled&quot;, it continues to display the title of previously opened TGD file. (Benzvi, Mati Jan 2, 2013) (Benzvi, Mati Jan 2, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed: Converted to SDR 19342 (Benzvi, Mati Jan 15, 2013) <br> |  | 35 | FINDING | 9349 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 74982
30507 | FINDING | OSR report gives error while saving the report in 3.5.0 & does not generate the required.epm files. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | OSR report gives error while saving the report in the given path in 3.5.0.It is happening in both the DBSdrops#176 &amp; 250 of net 8 &amp; 7 respectively. It gives the error, &amp; &quot;next&quot; button greys out, thus the finish process of complete report generation is not achieved. However the saved file can be opened &amp; the contents are readable for reference. Please find attached the snapshot. (N, Thamaraiselvi Jan 16, 2013). Since the report process is not completed, the reports does not contain the required .epm files for the customers which we upload in the Emerson Crossroad sites.<br>deponding upon the severity by which it fails to generate the required file, converting it to cat 2. (N, Thamaraiselvi Feb 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed. Converted to SDR 19735. (Benzvi, Mati Jul 23, 2013) <br> |  | 35 | FINDING | 9387 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75057
30508 | FINDING | OSR Report does not include the OAA1.2.0 tool installed in the drop. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | OAA 1.2.0 tool is installed in the drop#233. But OSR report generation does not report the same in the report. (N, Thamaraiselvi Jan 16, 2013).<br><br>Found that the issue has been reported earlier. Thus closing the finding. (N, Thamaraiselvi Jan 16, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9388 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75059
30509 | FINDING | OSR reports Ovation APC as "Other software". | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | While Ovation APC toolkit is the part of the Ovation system, OSR reports the same in the Other software catogory. (N, Thamaraiselvi Jan 16, 2013)<br><br>Changed action from DDR to DWI. (Quintos, Ronaldo M. Sep 20, 2013)<br><br>Changed category from Cat3 to Cat5. (Quintos, Ronaldo M. Sep 26, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation System Registration (OSR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_U9 21-SEP-12</p> <p><strong>Originator:</strong> N, Thamaraiselvi</p> <p><strong>Responsible:</strong> Benig, Ronaldo B.</p> <p><strong>Notify List:</strong> Quintos, Ronaldo M. N, Thamaraiselvi Benig, Ronaldo B.</p> <p><strong>Entry Date:</strong> 2013-01-16T23:18:03-05:00</p> <p><strong>Modified Date:</strong> 2013-09-26T22:10:21-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9389 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75060
30536 | FINDING | Bouncer software of Coretrace is not reported in the OSR report for 64 bit systems. | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | All the drops are configured as clients in the Coretrce application in OSC 3.0. With this result Bouncer software is installed in the drops also. This is not seen in the OSR report in 64 bit Systems. (N, Thamaraiselvi Jan 24, 2013)<br><br>Changed action from DDR to DWI. (Quintos, Ronaldo M. Sep 20, 2013)<br><br>Changed category from Cat3 to Cat5. (Quintos, Ronaldo M. Sep 26, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013).<br>Generated the report in Ov3.5.1_U3 &amp; verified the report. FOund the issue has been fixed. Tnus closing the finding. (N, Thamaraiselvi Jan 13, 2014) <br> |  | 35 | FINDING | 9416 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75114
30540 | FINDING | Help file should be corrected for LEADLAG Algorithm. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | In OV.3.5.0, OVA350010 installed. It is observed that in the Control Builder Help regarding LEADLAG Algorithm, the equations are not correct for K1 and K2.<br>Please find the JPEG file &quot;LEADLAG_SDR19258&quot; in the attachment for reference. (Mitra, Sambuddha Jan 25, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/25/2013: Please provide the correct information. (Casteel, Linda Jan 25, 2013)<br><br>The equations should be &quot;K1= GAIN x (H + 2x LEAD)/(H + 2x LAG)&quot; and<br> &quot;K2= GAIN x (H - 2x LEAD)/(H + 2x LAG)&quot;.<br>So, &quot;(&quot; is to be inserted in both equations shown in the attached JPEG file &quot;LEADLAG_SDR19258&quot;. (Mitra, Sambuddha Jan 28, 2013)<br><br>LC 01/29/2013: Move to 3.6 release. (Casteel, Linda Jan 29, 2013)<br><br>IC 2/7/13 - closed finding since this issue is still tracked as SDR 19258. (Capani, Nooch Feb 7, 2013) <br> |  | 35 | FINDING | 9420 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75122
30542 | FINDING | SDR 19224 Partially failed. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR is found fixed in the user manual O350_80,the required note &quot;The Control Builder search function follows the actual disk storage structure. It does not follow the Ovation Developer Studio system tree structure.&quot; is found in it but note could not be found in online help. (Goel, Chetna Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/29/2013: Plase check patch OVA350010. The fix for SDR 19224 should be in that patch. (Casteel, Linda Jan 29, 2013). Also check OW350_80.pdf on Q:\Communication\TechComm\Share\Validation. (Casteel, Linda Jan 29, 2013)<br><br>CHG 01/30/2013: Patch checked again but as described earlier, note is updated in OW350_80.pdf but online help is not updated since earlier version of help file, OW340_80 opens up (snapshot attached). Please provide the path for latest .chm file so that it can be verified. (Goel, Chetna Jan 30, 2013)<br><br>LC 01/30/2013: MNR 3.6 (Casteel, Linda Jan 30, 2013)<br>IC 2/6/13 - closed finding since this isue is still tracked by SDR 19224. (Capani, Nooch Feb 6, 2013) <br> |  | 35 | FINDING | 9422 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75126
30543 | FINDING | Online help file for "Online Sync program" of document OW350_80 manual is not updated. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | According to SDR 18581 , the user manual OW350_80 is updated for Online Sync program example (Section 16.2.1) whereas Online help file is not updated. (Kakroo, Tanisha Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/29/2013: Please check patch OVA350010. The fix for SDR 18581 should be in that patch. If not, the appropriate files did not get included in the patch. (Casteel, Linda Jan 29, 2013) Also check OW350_80.pdf on Q:\Communication\TechComm\Share\Validation. (Casteel, Linda Jan 29, 2013)<br><br>TK 01/30/2013: I checked the patch OVA350010. The online help file for algorithm opens OW340_80 (previous version) it should open OW350_80. The OW350_80.pdf on Q:\Communication\TechComm\Share\Validation is updated. (Kakroo, Tanisha Jan 29, 2013)<br><br>IC 2/6/13 - closed finding since SDR 18581 will continue to track this issue. (Capani, Nooch Feb 6, 2013) <br> |  | 35 | FINDING | 9423 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kakroo, Tanisha EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75128
30544 | FINDING | OSR report does not include for new Non Ovation drops. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | OSR reports as No responses to requests were received.&quot; for the new new Non Ovation drops configured in the 3.5.0 domain. We confirmed the communication from both ends are possible when we ping the drops.Please find enclosed the report. (N, Thamaraiselvi Jan 28, 2013).<br><br>Checked the report after installing the software in the Non Ovation drops.Found the report is o.k<br>Thus closing the finding. (N, Thamaraiselvi Jan 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9424 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75130
30545 | FINDING | OW331_60 need correction. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | In OW331_60, page 137, the topic &quot;TO insert a new I/O device in an ovation drop&quot; , the third party is written as &quot;5-9 (third party and bus)&quot; should be corrected as &quot;5-11 (third party and bus)&quot; .<br>The help link .chm is showing ok.<br>This vis against SDR 17874. (Pandey, Vijay Jan 28, 2013)<br><br>Closed . Originated by other user. (Pandey, Vijay Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9425 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75132
30546 | FINDING | OW331_60 need correction. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | In OW331_60, page 137, the topic &quot;TO insert a new I/O device in an ovation drop&quot; , the third party is written as &quot;5-9 (third party and bus)&quot; should be corrected as &quot;5-11 (third party and bus)&quot; .<br>The help link .chm is showing ok.<br>This vis against SDR 17874. (Joshi, Parmesh Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/29/2013: This finding says that you checked the 331 book. Please look at OW350_60. The 3.5 version of the Developer Studio book can be found on Crossroads. It should have the same information as the chm file. (Casteel, Linda Jan 29, 2013)<br><br>PJ 02/01: Checked in OW350_60. Here is entries are found as follows:<br><br>Page 216 step-4: 0 for IOIC and 5 - 11 for third-party and Bus devices. <br>Page 243 step-11: 0 for IOIC and 5 - 11 for third-party and Bus devices.<br><br> I checked in OW331_60 as per SDR (No where mentioned to check latest one, No page details). <br>Please confirm with OW350_60 observation mentioned above so that could close the finding. (Joshi, Parmesh Feb 1, 2013) <br> LC 02/01/2013: There are no plans to update OW331_60. The fix is available in OW350_50. Please close this finding. (Casteel, Linda Feb 1, 2013)<br><br>PJ 02/06/13: as per Linda plan to not update OW331_60. Finding Closed. (Joshi, Parmesh Feb 5, 2013) |  | 35 | FINDING | 9426 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75134
30547 | FINDING | Online help file for RESETSUM algorithm (TRST) not updated | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | The RESETSUM algorithm has been updated for TRST in user manual OW350_R1100 according to SDR 18637 , but online help file has not been updated . (Kakroo, Tanisha Jan 28, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/29/2013: Please check patch OVA350010. The algorithm help file should have the fix for SDR 18637. If it does not, then those files were not included in the help. (Casteel, Linda Jan 29, 2013) LC 01/29/2013: Also check OW350_R1100.pdf on Q:\Communication\TechComm\Share\Validation. (Casteel, Linda Jan 29, 2013)<br><br>TK 01/30/2013: The algorithm help file in patch OVA350010 does not have fix for SDR 18637. <br>TK 01/30/2013: The OW350_R1100.pdf on Q:\Communication\TechComm\Share\Validation is updated according to the SDR 18637. (Kakroo, Tanisha Jan 30, 2013)<br><br>LC 01/30/2013: MNR 3.6 (Casteel, Linda Jan 30, 2013)<br><br>IC 2/6/13 - closed finding, continue to track as SDR 18637. (Capani, Nooch Feb 6, 2013) <br> |  | 35 | FINDING | 9427 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kakroo, Tanisha EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75136
30549 | FINDING | Time gap massage is not coming in the historical review when the scanner was stopped. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | When the scanner was stop at 10:00am to 10:30am .it should be Time gap start (10:00AM) and Time gap stop (10:30) massage are showing in the historical point review window. After loading the patch OVA350010 in the machine after that it&quot;s not resolved. (Kumar, Sudheer Jan 29, 2013) (Contento, James L. Jan 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | We could not duplicate this in our lab. Please provide more info on how the test was performed, and how to log in to explore this further. (Contento, James L. Jan 29, 2013)<br><br>Time gap massage are coming in the historical review when the scanner was stopped now. (Kumar, Sudheer Feb 3, 2013) <br> |  | 35 | FINDING | 9429 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75140
30552 | FINDING | Occasionally Server Busy comes on workstation even when developer studio is closed. | Swartz, Mark EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | On drop174 (Win7 +SP1) its found that sometimes Server Busy is found on workstation even when developer studio is not opened.During this period Database server is online and communicating with this workstation.<br>For reference attached the snapshot of task manager and message.<br>Remote login steps to this drop is also attached. (Kumar, Shailendra Jan 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The Server Busy dialog which comes up is not an Ovation dialog and is certainly not a dialog which is part of the Ovation Developer Studio application. It is a Microsoft Windows dialog. <br>This happens when a Windows Microsoft Foundation Class (MFC) COM Client application is calling some method that takes a long time to process. Until the method returns, nothing can be done on the client side and this dialog box pops up -- by the Operating System itself.<br>This can happen for any MFC COM application, not necessarily Ovation Developer Studio. If Ovation Developer Studio is not running on the machine, then this may be due to some other application. <br>When specifically does this occur? At the time this occurs, are there processes which are consuming a significant portion of the CPU (view the Process tab of task manager and the meter in the system tray -- neither of which were provided in the attached screen shot named server_busy.jpg). (Swartz, Mark E. Jan 29, 2013)<br><br>SK:Could not recreate, will update once recreated till then kept this in Montioring state. (Kumar, Shailendra Feb 5, 2013) <br> |  | 35 | FINDING | 9432 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75146
30555 | FINDING | OvSisEvents service crashes on capturing LS events. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | OvSisEvents service is not handling events of type LsEvent correctly. When this kind of event is captured, service crashes.<br>Verified that OvSisEvents service crashes on folowing events.<br>1.Cleared Logic solver 2. Power removed from one of the redundant Logic Solver<br>3. Logic solver reboot 4. Logic solver switchover 5. Logic solver load. (Pandey, Vijay Jan 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed, Converted to SDR 19395 (Benzvi, Mati Feb 4, 2013) <br> |  | 35 | FINDING | 9435 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75151
30556 | FINDING | SIS events message contains XDB ID and LS slot number instead of SDS or LS name. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SIS events message contains XDB ID and LS slot number instead of SDS or LS name.<br>When message is sent form SDS or controller it contains XDB ID and LS slot number instead of SDS or LS name. OvSisEvents service should get name of device and send it to Historian with proper name. (Pandey, Vijay Jan 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed, Converted to SDR 19396 (Benzvi, Mati Feb 4, 2013) <br> |  | 35 | FINDING | 9436 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75153
30557 | FINDING | SDR18823 fails | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Reconciled fields for Analog and Deluxe Analog fields table is verified, after loading the patch, in online help as well as OW350_60.pdf (as on crossroads) but still it is found same as earlier and required fields are still not present in table. (Goel, Chetna Jan 30, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 01/30/2013: MNR 3.6 (Casteel, Linda Jan 30, 2013)<br><br>IC 2/6/13 - closed finding, SDR 18823 will continue to track this issue. (Capani, Nooch Feb 6, 2013) <br> |  | 35 | FINDING | 9437 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75155
30558 | FINDING | SDR19306, OSR Report doesnot identify the Operating System Service Pack for WS2008 R2 64-bit machine. | Quintos, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | As reported in SDR19306, OSR Report doesnot identify the Operating System Service Pack for 64-bit machines. <br><br>After Patch OVA350009 is installed, Win 7 64-bit machine Operating System Service Pack is seen as Service Pack1, while for DBS drop with OS 64-bit machines, OS WS2008 R2, Service Pack version is still seen as (blank). (Sachan, Pallavi Jan 30, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 2/7/13 - closed F#9438 since item is still tracked by SDR 19306. (Capani, Nooch Feb 7, 2013) <br> |  | 35 | FINDING | 9438 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75157
30562 | FINDING | Exported alarm log files having invalid format. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Files exported after loading Patch-OVA350010 are supposed to have wrong format. OAA fails to validate Log files and thus files cannot be imported.<br>Find the attached exported files and snapshot of error massage. (Jain, Yukta Feb 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | What is actually wrong with the export file. Just because OAA has an issue parsing it does not mean that file is invalid. Please investigate with OAA designers to determine what their issue is. (McMaster, James Feb 1, 2013)<br><br>IC 3/25 Val+Dev Mtg - Yukta reports F#9274 &amp; 9442 are resolved by patch OVA350013.<br>This will be noted in the Alarm Analizer DIR. Closed finding, (Capani, Nooch Mar 25, 2013) <br> |  | 35 | FINDING | 9442 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | OVA350013 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75164
30564 | FINDING | In VxSim Controller, SIN, COSINE & TANGENT Algorithms gives wrong output values for valid input values (1e+37). | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | As per Affected area of SDR 19346, Execute Math Algorithms like SIN,COSINE &amp; TANGENT on Vx Sim Controller gives different output value at valid input i.e:- 1e+37.<br><br>SIN :<br>(a)When input values IN1= 1e+37<br> Observation on Vxsim: OUTPUT = &quot;0.988712&quot; with GOOD quality.<br><br>COSINE :<br>(a)When input values IN1= 1e+37<br> Observation on Vxsim: OUTPUT = &quot;0.14983&quot; with GOOD quality.<br>TANGENT :<br>(a)When input values IN1= 1e+37<br> Observation on Vxsim: OUTPUT = &quot;6.5989&quot; with GOOD quality.<br><br>But As per SDR 19346, Out of all these algorithms would be &quot;nan&quot; with BAD Quality. (Agarwal, Gaurav Feb 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed R.E. to Ben Christy. (Perdeus, Matthew Feb 4, 2013)<br><br>This was addressed in another finding/SDR please convert to SDR (Christy, Benjamin Feb 4, 2013)<br><br>IC 1/13/13 - per GA on 2/13/13: I have retest this SDR in OVA350-011-02112013171323 patch &amp; Found that finding 9444 issue has been resolved &amp; issue of SDR 19346 has been resolved . <br>So I am closing the finding. (Capani, Nooch Feb 13, 2013) <br> |  | 35 | FINDING | 9444 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75168
30569 | FINDING | Creation of new Base station,EWS,controller etc crashes the studio. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 11 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | This has been observed in Unit 0 of both DBS &amp; workstations of ne#7 &amp; net8 of Ov3.5.0.Recreated many times &amp; observed the behaviour. Please find attached are the snapshots for reference. However the specified drops are saved &amp; visible in the studio. <br>fig.1-studio crashes after apply config of new drop. <br>fig-2 Pop-up error displayed in the studio when deleting the new created drops 1st time.<br>The drops get deleted in the 2nd time.<br>fig-3 Error observed in the Event viewer of the particular drop in Windows logs application. (N, Thamaraiselvi Feb 3, 2013) |  |  |  | The affected area is in the Ovation Developer Studio call-back functions (i.e., the software which displays progress UIs during various operations). In this particular case, it involved the standard feedback dialog shown during the save of an Ovation drop. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This issue is not repeatable on development system nor on Pittsburgh validation system. <br>More information required. Since the object was saved in the database, the crash probably occurred after the initial save operation to the database. Note that after saved to the database, the engineering tools updates various configuration files -- and the user can see via feedback dialog that this is taking place. Can it be confirmed that the crash occurs during this time period (i.e., while saving configuration files)?<br>The Finding goes on to state that an error is displayed during the attmpted delete of the drop -- error updating the tmp_host file. This may indicate that there is a fundamental problem with this system&quot;s ability to update the files in these locations.<br><br>After the attempted insert of a new drop (and the subsequent crash of the ovation developer studio), please check to see if the host file has been updated with the new drop and its entered IP address (and that the timestamp has been updated). (Swartz, Mark E. Feb 4, 2013).<br><br>1. I could recreate the issue in the EWS drops of #233 &amp;203 of both net7 &amp; net8 respectively.<br>2.Yes, it be confirmed that the crash occurs during this time period (i.e.while saving configuration files.<br>3.Today I did not get the pop up error of &quot;updating the tmp_host file.&quot; It straight away got deleted during the 1st time only.<br>4.I didn&quot;t observe the the host file has been updated with the new drop and its entered IP address (and that the timestamp has been updated.-in the local host file. But I observed the host file in the Primary domain drop ie in drop#176 is updated with the drop no. but not with the timestamp.<br>These are the steps I followed today inboth net7 &amp; net8 drops. <br><br>1. I created the new drop in drop#233 ofnet#7 &amp; saved-the studio crashed-fig.1 of 1st foldershows the snapshot of the same.<br>2.1st-folder-fig-2d shows the new drop saved&amp; displayed in the studio as drop9.<br>3.1st-folder-fig-3rd shows event viewer application error in the drop#233.<br>4.1st-folder-fig-4th shows the host file of the local drop#233.<br>5. Deleted the drop &amp; the did not get the pop up error of &quot;updating the tmp_host file.&quot; It straight away got deleted during the 1st time only.<br><br>I repeated in drop203 of net8 &amp; 2nd folder shows the snapshots of the above sequences in repeat.<br><br>Please find the snapshot folders for your reference.<br>Finally I observed these new created drops in the host file of Primary domain drop#176. (is common for both net7&amp;8) but only drop id with the i.p address but not with the time stamp. Can I change it to cat2? (N, Thamaraiselvi Feb 5, 2013) (N, Thamaraiselvi Feb 5, 2013)<br><br>Development logged into drop250 (DBServer). Issue does not occur there -- drop9 (Opstation) created and deleted successfully, drop43 (Controller) created and deleted successfully. Remote logged into drop233 (EWS). Issue recreated on drop233 (Studio crash).<br><br>This issue is the result of various changes made in OVA350002 to address suspected memory leaks. In this case, Ovation Developer Studio on a non-database machine can crash due to inadvertent memory corruption. These items will be addressed. (Swartz, Mark E. Feb 5, 2013)<br><br>Since OVA350002 has already been released, an SDR should be written so that this issue can be addressed in Ovation 3.5.1 or in a future Ovation 3.5.0 Patch. (Swartz, Mark E. Feb 5, 2013) (N, Thamaraiselvi Feb 6, 2013) <br> Found the issue is solved in drops of both the nets.<br>Hence closing the finding. (N, Thamaraiselvi Sep 24, 2013) |  | 35 | FINDING | 9449 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | N, Thamaraiselvi AUTOSOL PWS NOIDA | [8 empty] | Implementation | 3.5.1_U0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75177
30571 | FINDING | OvPtSvr service stops when pointname of 20 or more character is added as fully qualified in trend default. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | On any workstation :<br>1)Navigate to configuration --&gt;Trend---&gt;Trend Default---&gt;Insert New <br>Enter pointname of 20 or more character as fully qualified (for ex:OVATION-OVATION-OVAT.UNIT0@FE350C).<br>2)Then Click &lt;Finish&gt; it opens new trend default window entered High scale value as 100 and low scale value as 0.<br>3)As soon as &lt;Apply&gt; is clicked Ovptsvr service stops on DBS.<br>For reference attached is the snapshot of Event Viewer error seen on DBS when OvptSvr.exe stops. (Kumar, Shailendra Feb 4, 2013) | The software responsible for generating the name of trend default object names has been modified to ensure that a buffer overflow situation does not occur if fully qualified point names are specified. |  |  | The affected area is in the software responsible for special-case generation of an object name. Specifically, the generated names are unconditionally truncated to result in a maximum length of 40 characters. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please indicate the specified Trend Duration used for these test examples. Please also describe the behavior when these Ovation Developer Studio tests are performed on the Ovation Database Server. (Swartz, Mark E. Feb 4, 2013)<br><br><br>For the above test example default values are used(i.e Trend duration:10 minutes and Scale:Linear).<br>When above tests are performed on Ovation Database Server, Developer studio crashes(attached is the snapshot of this crash). (Kumar, Shailendra Feb 5, 2013)<br><br>The design/implementation of this object (Trend Default) is to generate a name consisting of the point name and the trend duration. If fully qualified point names are used, this can result in a length which exceeds the 40 character object name utilized in the database. The software (in this case) does not check for a maximum length.<br><br>The software will perform a check on the maximum length of a generated object name and limit/truncate this name to the max character length supported by the database (40 characters). Note that the truncation of this name will not effect the contents of the trend default file which is generated and subsequently query/downloaded to Operator Stations. This is because the information used in the generation of the trend default file utilizes the component attributes of the object -- not the object name itself.<br><br>A more thorough solution would be to utilize another method for the generation of the trend default name as stored in the database (e.g., the pointname only). However, this would require a much more significant design change and will not be performed at this time -- only via enhancement. (Swartz, Mark E. Feb 5, 2013) <br> Note that this issue is not new to the Ovation 3.5.0 patches, nor even Ovation 3.5.0. In fact, the issue could have occurred from the earliest release of Ovation on Windows. In order for this to be addressed via Ovation 3.5.1 or 3.5.0 patch, an SDR should be written. (Swartz, Mark E. Feb 5, 2013)<br>---<br>msb - Closed; Converted to SDR 19461 (Benzvi, Mati Mar 8, 2013) |  | 35 | FINDING | 9451 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75181
30572 | FINDING | OSR,Advanced Virtual Controller configured drops are listed as Workstations. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Advanced Virtual Controller configured drops are reported as Workstations.<br>Eg. Drop4, is configured as Advanced Virtual Controller in Dev. Studio, when seen in OSR Report Drop4 appears as Workstation:Drop4 instead of Controller: Drop4.<br><br>Kindly find attached &lt;30Jan13_009Patch-SysRegReport.html&gt; for your reference. As seen in report Drop4, Drop5, Drop8, Drop11, Drop16, Drop41 are configured as Advanced Virtual Controller (Sachan, Pallavi Feb 5, 2013)<br><br>Changed action from DDR to DWI. (Quintos, Ronaldo M. Sep 20, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation System Registration (OSR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Benig, Ronaldo B.</p> <p><strong>Notify List:</strong> Quintos, Ronaldo M. Sachan, Pallavi Benig, Ronaldo B.</p> <p><strong>Entry Date:</strong> 2013-02-05T05:03:51-05:00</p> <p><strong>Modified Date:</strong> 2013-09-20T04:24:47-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9452 |  | FINDING | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75182
30578 | FINDING | SDR#19347 Failed Partially. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | In OCR468, MATH algorithm ( SMOOTH, CALCBLOCK) give wrong output values for Invalid input values (nan).<br>Observation for MATH algorithm ( SMOOTH, CALCBLOCK) are below:<br>a.SMOOTH<br>i.When input<br>IN1 = 0<br>SMTH = NAN<br>Observation on OCR454: OUTPUT = &quot;NAN&quot; with BAD quality.<br>Observation on OCR468: OUTPUT = &quot;0&quot; with BAD quality.<br><br>b.CALCBLOCK<br>i.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = YES<br>EQUATION = (IN1)^(IN2)<br>Observation on OCR454: OUTPUT = &quot;1&quot; with GOOD quality, VALI = TRUE<br>Observation on OCR468: OUTPUT = &quot;0&quot; with BAD quality, VALI = FALSE<br><br>ii.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = NO<br>EQUATION = (IN1)^(IN2)<br>Observation on OCR454: OUTPUT = &quot;1&quot; with GOOD quality, VALI = TRUE<br>Observation on OCR468: OUTPUT = &quot;0&quot; with GOOD quality, VALI = FALSE (Jha, Rahul Feb 8, 2013)<br><br>Assigning to Ben Christy. (Boehmer, Robert W. Feb 15, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - 2/19 Status mtg: will write new SDR for Smooth &amp; Calcblock (Benzvi, Mati Feb 19, 2013)<br>This is the correct behavior. The test cases were inncorect in the SDR. Bellow are the corrected test cases.<br><br>f.SMOOTH<br>i.When input<br>IN1 = 0<br>SMTH = NAN<br>Expected Result: OUTPUT = IN1 with BAD quality.<br><br>g.CALCBLOCK<br>i.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = YES<br>EQUATION = (IN1)^(IN2)<br>Expected Result: OUTPUT = &quot;Last Good Value&quot; with BAD quality, VALI = FALSE<br>ii.When input values<br>IN1 = NAN (GOOD)<br>IN2 = NAN (GOOD)<br>QBAD = NO<br>EQUATION = (IN1)^(IN2)<br>Expected Result: OUTPUT = &quot;Last Good Value&quot; with GOOD quality, VALI = FALSE (Christy, Benjamin Feb 25, 2013)<br><br>RJ: As per Dev,it is WAD. Hence Closed. (Jha, Rahul Dec 23, 2013) <br> |  | 35 | FINDING | 9458 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Jha, Rahul AUTOSOL PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75194
30580 | FINDING | "Control Logic Navigator" is not displaying associated "Control Sheet". | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | After loading Patch &quot;OVA350-010&quot;, Control Logic Navigator is not displaying associated Control Sheet (under &quot;house&quot; icon after point search is completed).<br><br>Follow the steps to recreate the scenario:<br>Load Patch-OVA350010 --&gt; Start -&gt; Ovation -&gt; Ovation Utilities -&gt; Open &quot;Control Logic Navigator&quot; Tool --&gt; Complete a Point Search --&gt; Select any sheet from the list (or an instance on a sheet) --&gt; Control Sheet will not display.<br> <br>Remote login details for Drop203 is attached. (Jha, Rahul Feb 11, 2013) (Capani, Nooch Mar 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 3/1/13 - close, track as SDR #19447. (Capani, Nooch Mar 1, 2013) <br> |  | 35 | FINDING | 9460 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jha, Rahul AUTOSOL PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75198
30583 | FINDING | Some of the tools displayed in Programme & features are not included in the report. | Benig, Ronaldo PROCESS PWS MNL | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | The following tools are not displayed in the OSR report which are visible in the Programme &amp; features in the drops.<br>1.Kaspersky Lab Network Agent is not present in the OSR report.<br>2.Microsoft .NET Framework 1.1 <br>3.Microsoft .NET Framework 4 Client Profile <br>4.Microsoft .NET Framework 4 Extended - Sr. nos .2-4 of the Microsoft .NET patches are not present in drops of 64 bit Systems in the report. (N, Thamaraiselvi Feb 11, 2013) (N, Thamaraiselvi Feb 11, 2013)<br><br>Changed action from DDR to DWI. (Quintos, Ronaldo M. Sep 20, 2013)<br><br>Changed category from Cat3 to Cat5. (Quintos, Ronaldo M. Sep 26, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fix already checked in. (Benig, Ronaldo B. Dec 9, 2013).<br>Generated the report in Ov3.5.1_U3. Verified the reports. Found the issue has been fixed.<br>Thus closing the finding. (N, Thamaraiselvi Jan 13, 2014) <br> |  | 35 | FINDING | 9463 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | N, Thamaraiselvi AUTOSOL PWS NOIDA | Quintos, Ronaldo PROCESS PWS MNL | [6 empty] | Implementation | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75203
30586 | FINDING | ELC Analyzer tool crashes in OCR1100 after loading new patch OVA350-011-02112013171323. | Plymire, Alvan AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Following steps are performed :-<br>1. New patch OVA350-011-02112013171323 has been loaded in drop176 (DBS-Ov3.5.0,Net#8) &amp; all <br> the conttroller drops has been downloaded &amp; cleared and loaded.<br>2. Consider a drop30/80 (OCR1100) which has ELC module configured at 1.1.2.<br>3. Primary drop i.e drop30/80 is in control state.<br>4. ELC configuration tool has been opened.<br>5. Gone to File &gt; Connect &amp; typed drop30 to connect drop30.<br>6. Now expanded Server drop30/80 to access Module at 1.1.1.<br>7. Right clicked on module 1.1.1 &amp; clicked connect then its crashes.<br> Further it is noticed that when back up drop i.e drop80 is in control mode then this<br> error is not seen.<br> Also this issue is not observerd in OCR400.<br> <br>Please refer attached snapshot F#9466.jpg &amp; F#9466.txt copied by expanding the details tab of the error.<br>Please note I have tested SDR#19338 with patch OVA350-011-01212013104937 then this issue was not seen. (Sahay, Madhukar Feb 12, 2013) (Sahay, Madhukar Feb 12, 2013)<br><br>Re-assigning to Al Plymire. (Boehmer, Robert W. Feb 12, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Could you attach the configuration file for ELC 1.1.1? Thanks. (Plymire, Alvan W. Feb 12, 2013)<br><br>Please find the attached xml files. (Sahay, Madhukar Feb 12, 2013)<br><br>I was unable to reproduce this problem. When I logged in to drop 176, the module at 1.1.1 was an RLC. It does not appear on the ELC protocol analyzer. There is an ELC at 1.1.2, but it appears as if both controllers are cleared. I loaded the controllers and could not get the error to occur on module 1.1.2. (Plymire, Alvan W. Feb 15, 2013)<br><br>After clear &amp; load operation of controller , this issue is not seen. (Sahay, Madhukar Feb 18, 2013) <br> |  | 35 | FINDING | 9466 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350011 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75209
30593 | FINDING | Occasionally developer studio is crashed. | Swartz, Mark EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Drop:- drop176<br>Os:- Win 2K8 R2 SP1<br>Ov:- OV 3.5.0<br>OPH:- OPH 3.4.1 with OPH 341003 patch<br><br>Step Followed:-<br>1:- Open the HCT tool &amp; did some changes in the configuration (e.g:- Delete point or scanner group etc).<br>2:- Apply &amp; validate the configuration.<br>3:- it is observed that occasionally developer studio is crashed. <br> it is difficult to reproduce this problem. <br><br>For more information event viewer log file is attached. <br><br>Note:-<br>1:- drop176 is in blacklist state.<br>2:- Remote details is also attached, (Agarwal, Gaurav Feb 13, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Swartz, Mark E.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2013-02-13T06:36:46-05:00</p> <p><strong>Modified Date:</strong> 2013-09-23T07:08:20-04:00</p> | 0 |  | Ovation for Windows/General/Software | Cannot duplicate with latest software. (Swartz, Mark E. Apr 8, 2013)<br><br>GA:-<br>Date:- 04/17/2013<br><br>It was duplicated again on drop250. Please see the Remote login step. (Agarwal, Gaurav Apr 17, 2013) <br> |  | 35 | FINDING | 9473 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75222
30603 | FINDING | Controller fails on configuring 32k points. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | It is observed when controller is configured for 32000 points then after download &amp;<br>Reboot it fails. This is observer in OCR1100 (G02 CPU) as well as OCR400(G01 CPU).<br><br>Please note that this issue is not seen when controller is configured for 16000 points.<br>Please find the attached file of drop30.<br><br>(PS: drop30/80 is OCR1100 in Net#8 &quot;Ov3.5.0) (Sahay, Madhukar Feb 15, 2013)<br><br>Assigning to Ben Christy. (Boehmer, Robert W. Feb 15, 2013) (Benzvi, Mati Apr 30, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Was the drop cleared and loaded after the download? (Christy, Benjamin Feb 15, 2013)<br><br>I have tried downloading &amp; clear operation then controller came up in healthy state.<br>Please find the attached snap shots to refer the files appeared in download.<br>(PS: I have splited the file in 3 snapshots) <br>Please note we have downloaded all the files earlier &amp; performed the clear operation<br>But today attached files again appeared in download of controller. (Sahay, Madhukar Feb 21, 2013)<br>---<br>msb - 30-Apr:<br>a. Attached files may appear again if any change was made on the network<br>b. Testing now OCR1100 (drop30/80) in Pgh with 32k points. (Benzvi, Mati Apr 30, 2013)<br>---<br>msb - 1-May:<br> drop30/80 = OCR1100 G01:<br> 111 Sheets: task1=7, t2=37, t3=20, t4=20, t5=17 <br> 31504 Points: 680 Fast, 18945 Slow, 11954 App (Benzvi, Mati May 1, 2013) <br> |  | 35 | FINDING | 9483 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350014 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75242
30611 | FINDING | While opening the help file, displays the error in Dev studio. | Jain, Swati EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | 3.5.1_U2 |  |  | 2016-05-03 06:12 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Under the System folder-&gt;Trend point groups-&gt;open the existing point group &amp; member. Click the Help file.Displayed the pop up error of &quot;Cannot load helpfile=c:\Ovation\help\En\OVPTStudio.chm, HelpId=1224.<br>Kindly refer the 2 snapshots for the reference. (N, Thamaraiselvi Feb 21, 2013) | SJ: Added the context id to the section &quot;To migrate Trend group definition&quot; in the Operator Station Configuration User Guide. |  |  | SJ: Added the context id to the section &quot;To migrate Trend group definition&quot; in the Operator Station Configuration User Guide. Updated the OvPtStudio351 (Developer Studio online help) for the next build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 02/21/2013: MNR -- 3.5.1 (Casteel, Linda Feb 21, 2013). (Casteel, Linda Aug 16, 2013)<br><br>PS (26-Sept-2013): Per my understanding, a context ID is missing for Section &quot;To migrate Trend group definition&quot; in the Operator Station Configuration User Guide. As only migrate option is supported for the Trend Point Groups option, this help should appear when a user click the respective Help button. Assigning it to Swati for fixing the ID. (Sharma, Puneet Sep 26, 2013)<br><br>SJ: Added the context id to the section &quot;To migrate Trend group definition&quot; in the Operator Station Configuration User Guide. Updated the OvPtStudio351 (Developer Studio online help) for the next build. (Jain, Swati Oct 11, 2013) <br> |  | 35 | FINDING | 9491 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Casteel, Linda EMR SYSS PWS PITT | Contento, James AUTOSOL PWS PITT | N, Thamaraiselvi AUTOSOL PWS NOIDA | [6 empty] | Implementation | 3.5.1_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Not Critical for This Release | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 112961
30613 | FINDING | Redundant VCH Highway communication breaks repeatedly, after Installed patch-11(OVA350-011-02112013171323) | Bush, Kirt T EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | I have observed this issue after installed the patch-11(OVA350-011-02112013171323) on Drop#250(DBS).<br>It occurs while executing the below scenario:<br><br>Installed patch-11(OVA350-011-02112013171323) on Drop#250(DBS) <br><br>Performed Download, Clear &amp; Load operations on VC107 &amp; VC108 (This is Redundant VCH configuration VCH235 for VC107 and VCH236 for VC108) <br>Loaded standard algorithm sheets (where as Loading APC sheets also giving the same event) after few minutes VCH-Drop#235 goes off highway (We can see this on Drop#235 MMI. Please see the attached snap shot)<br>This is only happening on primary VCH Drop#235.At the same time Drop#236 is communicating properly. <br><br>NOTE:<br>VC107/108-Redundant Advanced Virtual Controller with redundant VCH235/236.<br>Initially we observe this issue with APC sheets loading<br>Then we noticed that, Loading standard algorithm sheets also have the same behavior <br>Removed all loaded control sheets (Without control sheets in VC107/108).We did not find any Highway communication failure.Both VCH &amp; VC&quot;s are in healthy state(Primary &amp; backUp)<br>Once loaded the control sheets it&quot;s happening. (K, SendhilKumar Feb 22, 2013) (Long, Edward M. Feb 22, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb 7/24:<br>- Patch 011 was obsoleted and replaced by 014 and newer Ctlr patches.<br> Sendhil, Please recheck with latest OVA350 Update. (Benzvi, Mati Jul 24, 2013)<br>SKK:<br>-Tested with latest OVA350 Update on Emily network drops(Redundant VCH 226/227).<br>-Observed no Highway communication failure during download,clear,load operation.Hence,finding closed. (K, SendhilKumar Aug 1, 2013) <br> |  | 35 | FINDING | 9493 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | K, SendhilKumar PROCESS PWS NOIDA | Long, Edward M EMR SYSS PWS PITT | Shiferaw, Tedla AUTOSOL PWS PITT | [6 empty] | Implementation | OVA350_Aug13_Update |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75260
30614 | FINDING | Updating backup through Controller Diagnostics gives error:SDR#19425 fails. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR#19425 fails:On advance controller drop12/62 (OCR1100 on Ov3.5.0)Updating backup through Controller Diagnostics gives error(refer attached snapshot).Also tested on Advance OCR400 controller drop29/79.Tested with latest Patch-11(2/22/2013) (Kumar, Shailendra Feb 23, 2013)<br><br>Assigned to Ben Christy. (Boehmer, Robert W. Feb 24, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Unitialized variable was preventing the update to occur. (Christy, Benjamin May 8, 2013) <br> |  | 35 | FINDING | 9494 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75262
30618 | FINDING | Ovation Patches are not listed in report for WinS2008-R2 Non-Ovation machine. | Benig, Ronaldo PROCESS PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | When an Ovation patch is installed on a Non-Ovation Drop(As per requirement to check some SDR), it is observed that the drop with OS WinS2008 R2 doesnot list the Ovation Patches, where as the report lists the installed ovation patches from all other non - ovation drops with OS WinXP, Win7, WinS2003, WinS2008(32bit). (Sachan, Pallavi Feb 25, 2013)<br><br>May I know what kind of non-Ovation machine you were referring to (e.g. AV server, stand alone historian)? Is Ovation System Registration agent installed/running on the non-Ovation machine? (Quintos, Ronaldo M. Sep 20, 2013)<br><br>Kindly verify if you can install the agent on the machine before generating a report. (Quintos, Ronaldo M. Sep 26, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation System Registration (OSR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sachan, Pallavi</p> <p><strong>Responsible:</strong> Benig, Ronaldo B.</p> <p><strong>Notify List:</strong> Quintos, Ronaldo M. Sachan, Pallavi Base, Lovely Olivia R. Jimenez, William</p> <p><strong>Entry Date:</strong> 2013-02-25T01:36:11-05:00</p> <p><strong>Modified Date:</strong> 2014-01-20T05:09:06-05:00</p> | 0 |  | Ovation for Windows/General/Software | There was a non-ovation drop with OS WinS2008 R2 which was used as standalone server for Oracle patch testing. This is no more available. We will try to get such setup and send you the report. Thanks! (Sachan, Pallavi Sep 20, 2013)<br><br>A non-ovation drop with OS WS2008R2 is available (Drop229, LAVMgr).<br>OSR_1.3 is installed and is running.<br>Now OVA331149, a patch to be installed on Non-Ovation Drop with OSR is installed. <br>Still there is not entry for this ovation patch.<br>This finding is observed as OPEN till 3.5.1_U2 build. (Sachan, Pallavi Dec 13, 2013) <br> |  | 35 | FINDING | 9498 |  | FINDING | Base, Olivia AUTOSOL MNL | Jimenez, William PROCESS PWS MNL | Quintos, Ronaldo PROCESS PWS MNL | Sachan, Pallavi EMR SYSS PWS NOIDA | [7 empty] | 3.5.1_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75267
30621 | FINDING | COMPARE Algorithm is not working properly for invalid inputs. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | (SDR# 19377 Failed.)<br>Whenever we give an invalid value to its any input, all outputs should set to FALSE.<br>Steps to recreate the issue-<br>(1) Use COMPARE algorithm in a control sheet.<br>(2) Open it in signal diagram.<br>(3) Give invalid value to any input/inputs i.e. &quot;NAN&quot; and observe output values. <br> Here all outputs should set to false. (Singh, Rajan Feb 26, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This finding (9501) was created when testing OVA350011. This fix did not actually make it into patch 11. It was included in patch 14.<br>This has been validated in OVA350014 and SDR 19377 has been updated. (Boehmer, Robert W. Apr 24, 2013)<br><br>IC 4/25/13 - closed, issue is addressed by OVA350014. (Capani, Nooch Apr 25, 2013) <br> |  | 35 | FINDING | 9501 |  | FINDING | [10 empty] | Implementation | OVA350014 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75272
30623 | FINDING | OVA350011/SDR19299: OCR1100 may report MAIN task stopped after startup. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | The following messages still appear occasionally after OCR1100 startup:<br><br>0x138384c (main): task 0x138384c has had a failure and has been stopped<br>0x138384c (main): fatal kernel task-level exception! (Brown, Sean Feb 27, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This has been resolved &amp; validated in patch OVA350014. See SDR 19299. (Boehmer, Robert W. Apr 8, 2013) <br> |  | 35 | FINDING | 9503 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Christy, Benjamin A PROCESS PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75276
30625 | FINDING | Live data filter under "point review tab" need to be updated in online help . | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | The online help manual of &quot;Ovation Application&quot; says that &quot;Do not select the Value/Status change (VL) filter or you cannot apply the Limit/Alarm filter&quot;. It is same for all other live data filter types (Quality, Check/Cutout , Reason and Alert filter). But the data filter behaves in a different way , i.e., if VL is selected , it filters the points but when any other live data filter is selected VL gets deselected and other live data filter takes priority and vice verse ,i.e. if any other live data filter is selected , it filters the points but when VL is selected the selected live data filter gets deselected and VL takes priority. <br><br>However , according to manual it should not allow me to select any other data filter if VL is selected. (Kakroo, Tanisha Mar 5, 2013)<br><br>Documentation should reflect the behavior of the application. (Burgoon, Frank J. Mar 5, 2013)<br><br>TK(07/03/2013) : Same behaviour is observed in 3.3.1_OV331_Patch also. (Kakroo, Tanisha Mar 6, 2013) | SJ: Updated the text of the Filter ribbon tab. |  |  | SJ: Updated the following: Using Point Review at the Operator Station--&gt;Point Review ribbon tabs--&gt;Filter ribbon tab in the Point Review window--&gt;&quot;Limit/Alarm cell of the table&quot; in the OW351_20 manual. Updated manual is placed at Q:\Communication\TechComm\Share\Validation\OW351_20.pdf | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SJ: Updated the following: Using Point Review at the Operator Station--&gt;Point Review ribbon tabs--&gt;Filter ribbon tab in the Point Review window--&gt;&quot;Limit/Alarm cell of the table&quot; in the OW351_20 manual. Updated manual is placed at Q:\Communication\TechComm\Share\Validation\OW351_20.pdf (Jain, Swati Oct 8, 2013) <br> |  | 35 | FINDING | 9505 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Kakroo, Tanisha EMR SYSS PWS NOIDA | [7 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75280
30626 | FINDING | "Export" option should be deactivated when point is not browsed in PI. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Export functionality should not avail at initial in Point info application window. This option should be grayed out as there is nothing to export when no point browse in to PI initially. Find the snapshot PI_1 &amp; PI_2 for reference. (Jain, Yukta Mar 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9506 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75282
30627 | FINDING | "Export" option should be deactivated when point is not browsed in PI. | Augustine, Lisa EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Export functionality should not avail at initial in Point info application window. This option should be grayed out as there is nothing to export when no point browse in to PI initially. Find the snapshot PI_1 &amp; PI_2 for reference. (Jain, Yukta Mar 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Will fix in Ovation 3.5.1 (Augustine, Lisa Jun 5, 2013) <br> |  | 35 | FINDING | 9507 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75284
30628 | FINDING | "Export" option in PI need to be modified. | Augustine, Lisa EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Export option listed in menu items of PI needs modification against following issues:-<br>1) Export window does not reflect the name of &quot;New custom tabs&quot; added in PI. Rather it shows different tab name.<br>2) Only 9 out of 10 new custom tabs appear in export window. Refer to snapshot2.<br>3) Last tab listed in export window is not clearly visible. Refer to snapshot 1.<br>4) &quot;Export as&quot; button remain active in case even when no tab is selected in list and also perform export. (Jain, Yukta Mar 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Will fix in Ovation 3.5.1 (Augustine, Lisa Jun 5, 2013) <br> |  | 35 | FINDING | 9508 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75286
30629 | FINDING | Information of point exported in form of txt file in PI is inconsistent. | Augustine, Lisa EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Point info exported in form of text file missed some info of point for the first time.<br>Follow the steps to recreate the issue:<br>Open PI --&gt; Browse any point --&gt; Click on Menu button --&gt; Select export option --&gt; Select all the tabs listed --&gt; export the file in txt format --&gt; Txt file will not contain all information of point --&gt; Export the point info again will give different file this time which may or not miss any information. Export functionality showing inconsistent behavior. <br>Find the attached exported files of same point. (Jain, Yukta Mar 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Will fix in Ovation 3.5.1 (Augustine, Lisa Jun 5, 2013) <br> |  | 35 | FINDING | 9509 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75288
30633 | FINDING | PI window "Limit" tab do not update to corresponding modification in Developer studio. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | &quot;Limit tab&quot; of PI is showing inconsistent behavior in updating some field values. Values of Field- UL, ZL, DJ, UH, ZI, DB do not refresh in PI window after modification in Developer studio. <br>Steps to reproduce: <br>Create an analog point (LA, DA) --&gt; Keep all the limit setting of the point blank --&gt; Load the drop --&gt; Monitor the limit tab of same point in PI --&gt; All the fields remain inactive which should be actually --&gt; Now assign value to fields- LL, ZM, HL, ZI in Developer studio followed by loading --&gt; Monitor Limit tab in running PI as well as in new PI window. Both PI windows act differently --&gt; Now Remove all the values in Developer studio and load the point again --&gt; Monitor the already opened PI windows, here you will found that some field will updated while other remain active despite the fact corresponding fields are blank in Developer studio. Whereas same point in new PI will give correct field details. <br><br>Running PI Application Window does not update the modified values even after refreshing. Find the attached snapshots. (Jain, Yukta Mar 6, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I see that changing the value of one of these fields in Ovation Studio then loading the drop causes PI to reflect the new values, but if you change between having a value defined and not having a value defined then the editable property on the PI grid does not change on a load. However if you bring up another instance of PI, or view another point and then go back to the point the editable properties are displayed correctly. Do your observations agree with what I have described? (Burgoon, Frank J. Mar 6, 2013)<br><br><br>YJ: Yes observation is close to my observations, but I want to add some more to your knowledge:<br><br>1) In answer to- &quot;I see that changing the value of one of these fields in Ovation Studio then loading the drop causes PI to reflect the new values&quot;<br>Create any LA point keeping all the field value of limit tab null --&gt; Open the point in PI --&gt; Assign value to LL, HL, ZM, ZI fields in limit tab of Developer studio followed by loading the drop and correspondingly observe the changes in PI window. Here I observed that all assigned 4 field became activated. Now open the same point in new PI window. Here I observe that 8 fields become active. This is one observation.<br><br>2)In Answer to- &quot;but if you change between having a value defined and not having a value defined then the editable property on the PI grid does not change on a load.&quot; <br>Now remove values of LL, HL, ZM, ZI fields in Developer Studio followed by loading--&gt; monitor limit tab in already opened PI window. Here I observed that some of fields become de-active but some other remains active despite the fact that there is no value assigned to any field in developer studio. Again monitor the point in new PI window will give different behavior. (Jain, Yukta Mar 8, 2013) <br> No plans to fix. When the limits are enabled or disabled in the studio and the drop is loaded, the user has to reload the point in the point information window since the LB value has changed. As for the incremental fields, there is no bit in LB to identify that the limit is defined. Thus, the high or low limit bit in the LB field is used to determine whether the field should be editable. This is the way the system works, please close this finding. (Augustine, Lisa Mar 19, 2013)<br><br>YJ:Ok i am going to close the finding. (Jain, Yukta Mar 19, 2013) |  | 35 | FINDING | 9513 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75295
30634 | FINDING | Modification in filter of PI application results in "Unhandled Exception Error". | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | PI gives error on modify any of &quot;FILTER&quot; after loading points. Follow the steps to recreate the issue:<br>Run PI application --&gt; Click on &quot;Ovation point browse&quot; button --&gt; Select required filters --&gt; Click on &quot;Start&quot; --&gt; Change any of filter tab --&gt; Click on &quot;OK&quot; --&gt; This will result into &quot;Unhandled exception error&quot;. <br>Quit will terminate the PI. Find the attached snapshot and error detail file. (Jain, Yukta Mar 6, 2013) (Burgoon, Frank J. Mar 6, 2013) | none |  |  | Follow instructions in problem description and observe that problem no longer exists. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Module will be patched to correct this. (Burgoon, Frank J. Mar 6, 2013)<br>---<br>msb - Closed as SDR 19591 @ 07-May-2013 (Benzvi, Mati May 7, 2013) <br> |  | 35 | FINDING | 9514 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75297
30635 | FINDING | "Load filter" in PI do not dilist the deleted filters. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Load filter tab lists all the Filters saved in PI but it do not delist the deleted filters. Follow the steps to recreate the scenario:<br>Open PI --&gt; Click on &quot;Ovation Point Browse&quot; --&gt; Select filter settings --&gt; Save it by clicking on &quot;Save filter&quot; button --&gt; Again open save filter window --&gt; Delete the filter --&gt; Now drop down the &quot;Load filter&quot; List --&gt; Deleted filter will not delist. Same can be seen in new PI window too.<br>Find the attached snapshots. (Jain, Yukta Mar 6, 2013) | none |  |  | Follow instructions in the problem description and observe an error message and subsequently the file name is not in the MRU list. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The MRU list on the Load Filters button and the filter setting files are only losely connected. After a filter setting file is deleted the name still exists in the MRU list. If selected an error will occur, the user will be notified and the name will be removed from the MRU list. (Burgoon, Frank J. Mar 6, 2013) <br> |  | 35 | FINDING | 9515 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75299
30642 | FINDING | In "point Tab" of "Historical Review" data is not showing properly. | Contento, James AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | If we give any &quot;Start Time&quot; and &quot;End time&quot; to see Historical Review, Then it shows only Points on that &quot;Start Time&quot;.<br>It&quot;s not showing data for the whole range (Points between Start Time and End Time) and for End Time. (Kumar, Sudheer Mar 12, 2013) (Contento, James L. Mar 12, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | [JLC 3/12/2013] Please supply additional information and screen grabs of filter selection and results. I attempted a historical point review here for a single point with an absolute start and end time and got a successful result. (Contento, James L. Mar 12, 2013)<br><br>I have added more then 7000 point in the Historian after that I want to see the all points detail in Historical Review. We give any &quot;Start Time&quot; and &quot;End time&quot; to see Historical Review, and then it shows only Points on that &quot;Start Time&quot;. (Kumar, Sudheer Mar 12, 2013)<br><br>Is this still an issue? If so please supply information requested on March 12. (Contento, James L. Nov 4, 2013)<br><br>Its working fine now . (Kumar, Sudheer Nov 26, 2013) <br> |  | 35 | FINDING | 9522 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75314
30646 | FINDING | Help for SIS net repeater firmware upgrade procedure is not available | Maggu, Mukesh EMR SYSS PWS NOIDA | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Help for SIS net repeater firmware procedure is not available. (Pandey, Vijay Mar 13, 2013) |  |  |  | MM 02/4/2014: The required information is added in section 5.16.3 - To upgrade an SIS Net Repeater of OW351_47, SIS User Guide. The user guide is kept at Q:\Communication\TechComm\Share\Validation. The changes will also be reflected in the online help.(Maggu, Mukesh Feb 4, 2014) | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | MM 02/4/2014: Check the required information in 3.5.1 U5 build.(Maggu, Mukesh Feb 4, 2014) (Maggu, Mukesh Feb 4, 2014) <br> |  | 35 | FINDING | 9526 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.1_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | MM 02/4/2014: The required information is added in section 5.16.3 - To upgrade an SIS Net Repeater of OW351_47, SIS User Guide. The user guide is kept at Q:\Communication\TechComm\Share\Validation. The changes will also be reflected in the online help.(Maggu, Mukesh Feb 4, 2014) | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75322
30651 | FINDING | Publish operation generated PDF file does not display data properly. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | At Control options, Publish operation for sheet does not display Sheet name and Sheet number in the generated PDF file properly, if the Sheet number is longer than 4 characters and if the Sheet name is long. (Mitra, Sambuddha Mar 14, 2013)<br><br>Please attach PDF - (Hutchison, Steven B. Mar 19, 2013)<br><br>Please find the attached file &quot;Publish_Test.pdf&quot;. (Mitra, Sambuddha Mar 23, 2013)<br>In the attached file &quot;Publish_Test.pdf&quot;, at Page 1, there is no space between 12345 and TEST_NEW_95. (Mitra, Sambuddha Mar 23, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This pdf seem acceptable to me. The text is clear and no characters the characters do not overlap. In the past the title text would extend beyond the box overwritting the page numbers to the left. In addition all sheet numbers were assumed to be 4 digit numeric strings. <br><br>It is possible even with the patch to get some minor overlap of number and title. Strings are truncated to reduce this in all but the most extreme cases where graphically wide characters are used. In most modern fonts &quot;W&quot; takes more horizontal space than &quot;i&quot; This patch works at a balance for performance reasons. (Hutchison, Steven B. Mar 25, 2013)<br><br>Understand this. Hence, closing the finding. (Mitra, Sambuddha Mar 26, 2013) <br> |  | 35 | FINDING | 9531 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75332
30653 | FINDING | Save Alarm List Configuration error. | Augustine, Lisa EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Procedure- Remove all quick access buttons --&gt; Save the Alarm List Configuration file --&gt; Such configration file donot save.<br>Other observations:-<br>1. Before patch OVA350013, configration file can be saved with no quick access buttons.<br>2. Can Successfully save the configuration seperatly for the Quick Access Toolbar after loading the patch.(Exept the case of &quot;No quick access tool button&quot; as mention above) (Jain, Yukta Mar 15, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Alarms (AL)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Jain, Yukta</p> <p><strong>Responsible:</strong> Augustine, Lisa</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jain, Yukta</p> <p><strong>Entry Date:</strong> 2013-03-15T06:06:58-04:00</p> <p><strong>Modified Date:</strong> 2013-03-15T06:06:58-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9533 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75335
30654 | FINDING | SDR 19388 "SDS firmware upgrade tool crashes if path to firmware contains spaces" failed the validation. |  | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR 19388 &quot;SDS firmware upgrade tool crashes if path to firmware contains spaces&quot; failed the validation.<br>Tested with patch OVA350012, found issue not fixed.<br>For reference screen shot of cmd session is attached. (Pandey, Vijay Mar 19, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Retested the issue with following command line: &quot;c:\tmp\Firmware\S D S\InstallCtlR_MD.udf&quot;. Found issue fixed, hence finding is closed. These steps needs to documented in SIS help. (Pandey, Vijay Mar 20, 2013) <br> |  | 35 | FINDING | 9534 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [7 empty] | Implementation | OVA350012 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75337
30655 | FINDING | Download process is halted after loading Patch OVA350015 | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Download process is halted after loading Patch OVA350015<br><br>Checkboxes are missing in both &quot;Graphic &amp; Network download window&quot; in Developer studio of Ov3.5.0. Also graphics and drops are not download if go with &quot;OK&quot; button.<br> <br>In addition it is observed that individual drop can be downloading properly.<br>Find the attached snapshots for reference. (Kumar, Sudheer Mar 19, 2013) (Kumar, Sudheer Mar 19, 2013) |  |  |  | The affected area is in the software responsible for generating the identified selection dialog in the Ovation Developer Studio. Retest the functionality which failed the initial tests. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Problem was introduced during software changes to address SDR 19269. This will be corrected. (Swartz, Mark E. Mar 19, 2013)<br>---<br>msb - OK in OVA350-015 (27-Mar build) - <br> Download checkboxes are active in System, Network, Unit levels &amp; Graphics download windows. (Benzvi, Mati Mar 27, 2013) <br> |  | 35 | FINDING | 9535 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350015 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75339
30656 | FINDING | Dump CRC in Locked SLS does not give correct error. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | While testing SDR18907:SLS01 is locked from studio, then right click SLS01 and do &lt;dump CRC&gt;<br>it pops up message &quot;can&quot;t communicate with logics solver&quot;(refer attached snapshot).<br>This message is confusing since SLS01 is locked hence we cannot do &quot;dump CRC&quot; so message should indicate about locked SLS like in case of clear, reboot of locked SLS. (Kumar, Shailendra Mar 19, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This issue will be fixed in future release. CRC dump will be possible for Locked SLS.<br>See SDR 18076. (Raciborski, Mikolaj Apr 8, 2013) <br> |  | 35 | FINDING | 9536 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30659 | FINDING | Firmware download to ERVP module fails. | Shaw, Scott External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Currently on the 3.5 Ovation system with patch 14 installed, two files (vxWorks and vxRVP.romfs) show up when attempting to do a firmware download to the ERVP module. When the download was attempted, however, both of these files failed to download giving the message FAILURE:module communications failure. (Wood, Tom Mar 19, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This was caused by validator failing to create a module record for the RVP. Ben went over the procedure for downloading with Tom &amp; they verified that module downloads successfully. (Boehmer, Robert W. Mar 20, 2013) <br> |  | 35 | FINDING | 9539 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75347
30660 | FINDING | SDR#19449(FFISEL algorithm shows Unkown mode in signal diagram viewer) fails. | Pratley, Bob EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR#19449(FFISEL algorithm shows Unkown mode in signal diagram viewer)fails.<br><br>Following steps are performed in Ov3.5.0 ;-<br>1. Patch OVA350014 has been loaded in drop250(DBS).<br>2. Field bus module has been configured in drop32/82.<br>3. 848T has been commissioned in segment.<br>4. A control sheet has been created using FFISEL algorithm &amp; drop32/82 is loaded .<br>5. It is observed when FFISEL function block is in Auto or Manual mode in signal diagram<br> it shows unknown.<br> Please refer attached snapshot for your reference. (Sahay, Madhukar Mar 20, 2013) (Boehmer, Robert W. Mar 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Madhukar, In order for the controller to use the new FFISEL algorithm code, the controller has to be downloaded and rebooted after the patch has been installed on the DBS. Can you confirm that the controller was downloaded and rebooted after the patch was installed? Thanks, Bob. (Pratley, Bob Mar 26, 2013)<br><br>MS : Controller has been downloaded, cleared &amp; loaded after loading the patch.<br> Same is also performed after loading the new patch 014 but result is same.<br> In Developer&quot;s stdio FFISEL block shows it is in Auto mode where as in signal diagram<br> it shows unknown. (Sahay, Madhukar Apr 1, 2013) <br> The patch has been installed in the O&quot;Hara Validation lab and works as expected, i.e. the FFISEL as viewed in signal diagram accurately shows the mode of the ISEL function block. (Pratley, Bob May 21, 2013)<br><br>MS : Rechecked with Patch OVA350-018. Signal diagram correctly showing Auto/Manual mode<br> based on mode of FFISEL function block. (Sahay, Madhukar May 23, 2013) |  | 35 | FINDING | 9540 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350018 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75349
30661 | FINDING | SIS diagnostics Tool always shows global publisher as True. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | In SIS diagnostics tool Navigate to Logics solver ---&gt;General---&gt;Global Publisher:It always shows value as true wahatever may be the setting(publish secure parameter globally) in studio(refer attached snapshot). (Kumar, Shailendra Mar 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This issue will be fixed in future patch (Raciborski, Mikolaj Apr 10, 2013) <br> |  | 35 | FINDING | 9541 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30662 | FINDING | SDR 19396 "SIS events message contains XDB ID and LS slot number instead of SDS or LS name" partially failed | Dhanda, Ashna PROCESS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Now, SIS events message contains SDS name.<br>SIS events message contains LS slot number instead of LS name<br>When message is sent form SDS or controller it contains LS slot number instead of LS name. OvSisEvents service should get LS name of Logic solver device and send it to Historian with proper name. (Pandey, Vijay Mar 20, 2013)<br>1. In attached file, Logic solver not appeared for any events. <br>2. Incorrect LS slot number appeared, while performing Logic solver switch over operation.<br>e.g. Switchover occured from slot#3 to slot#4. SIS events shows &lt;LsEvent: SDS001&gt;: REDIO: Switchover Occurred; card switch 05 -&gt; 07. (Pandey, Vijay Mar 25, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | VP-02/25/14- Issue is being tracked with SDR 19396, hence finding is closed. (Pandey, Vijay Feb 25, 2014) <br> |  | 35 | FINDING | 9542 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Budzynski, Piotr EMR SYSS RS WRSW | Kijkowski, Tadeusz AUTOSOL PSS WRSW | Pandey, Vijay EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [5 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75353
30663 | FINDING | In SIS diagnostics tool, SLS firmware revision shows incorrect error after reboot of SLS and data updation takes time. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | When redundant SLS is rebooted when Logics Solver comes up following discrepency is found in SIS :<br>1)SLS firmware revision shows incorrect error for few seconds after SLS comes up(see attached snapshot).<br>2)Data Updation in tool takes time about 2 minutes but in actual state is different, refresh of diagnostics tool is taking time if we do not touch the tool, suggest refresh button for this. (Kumar, Shailendra Mar 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This issue is connected with networkng.<br>It takes approximately 30 sec to update the information on the network. Second thing is updating that information on the UI. Right now it is refreshed once per 30 sec as well, but the time on actual update can differ from the network update.<br><br>We dont want to make diagnostic software heavy for the netowrk, therefore network update time wont be changed. We will consider changing UI refresh time.<br><br>This is enhancement request. (Raciborski, Mikolaj Apr 17, 2013)<br><br>This will be improved in he next release. (Raciborski, Mikolaj Oct 21, 2013) <br> |  | 35 | FINDING | 9543 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | MNR |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Move to Next Release | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30665 | FINDING | Historian Point Review process is Halted after selected all Historian Points . | Bergey, Steve EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Historian Point Review process is Halted after selected all Historian Points . <br><br>Historian Point Review process is Halted by if we are selected all Historian Points more than 10k points <br><br>After completed Historian Point Review process All Points Description are showing &quot;Time Gap start&quot; and All points Values are showing &quot;False 0&quot; .<br>In addition it is observed If we are select only 32 points than its working properly <br><br>Please see the attached snapshot for your reference (Kumar, Sudheer Mar 21, 2013) (Contento, James L. Mar 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Its working fine in Ov3.5.0+ OPH3.5.0 hance closed this finding. (Kumar, Sudheer Sep 16, 2013) <br> |  | 35 | FINDING | 9545 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | OPH.3.5.0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75359
30666 | FINDING | Some of the International characters in the TT Fields are not encode into the point correctly for the SCSTEP algorithms | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Use the below International characters in the TT fields of SCSTEP algorithms: <br><br>Ã -latin capital letter A with caron <br>&#141; -latin capital letter T with caron<br>DZ -latin small letter Dz with digraph<br>S -latin small letter S with hook<br>Verify characters showing correctly in signal diagram,Point info,controlbuilder etc.. (K, SendhilKumar Mar 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The projects team in poland, tested this and they report the issue resolved.<br><br>Do other characters work? <br>What are the unicode values for a couple that do and a couple that don&quot;t (You can get the values by hovering over the character in the &quot;character map&quot;? <br>Are you sure your font supports the characters?<br>Did you insert these characters via the &quot;Character Map&quot; applications? ... If so, what was the selected font?<br>What is the font used in point info? (Hutchison, Steven B. Mar 25, 2013)<br><br>Steve,Please see my comments are below: <br><br>Do other characters work?<br> YES. <br>What are the unicode values for a couple that do and a couple that don&quot;t (You can get the values by hovering over the character in the &quot;character map&quot;?<br> Unicode Font<br>Ã -latin capital letter A with caron - U+01CD - Arial<br>&#141; -latin capital letter T with caron - U+0164 - Arial<br>DZ -latin small letter Dz with digraph(curl) - U+02A5 - Arial<br>S -latin small letter S with hook - U+0282 - Arial<br><br>Are you sure your font supports the characters?<br> YES.<br><br>Did you insert these characters via the &quot;Character Map&quot; applications?..If so, what was the selected font?<br>NO.we didnot insert the characters via the &quot;Character Map&quot;.we just copy and paste from the &quot;Character Map&quot;.The selected font was &quot;Arial&quot;. <br><br>What is the font used in point info?<br>PI font is &quot;Tahoma&quot; <br><br>Please see the attachement also.(K, SendhilKumar Apr 3, 2013) (K, SendhilKumar Apr 3, 2013)<br><br>Default Font does not support the selected unicode characters. select an appropriate default font.<br>- (Hutchison, Steven B. Aug 30, 2013) <br> |  | 35 | FINDING | 9546 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75361
30667 | FINDING | SDR 19293 "It is not possible to load LS after text incremental import.. node point is not updated" is failed. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Steps performed:<br>1. Verified SIS controller fully loaded then exported the SIS data base. exported file (.lst) is attached.<br>2. Imported the exported SIS data base. For reference, export/Import cmd line details are attached.<br>3. When we tried to load the LS (logic solver1), there was error that node point for SDS and LS are not assigned. <br>4. Opened the node points for the SDS and LS, found points are assigned.<br>Error disappear after the follwing step:<br>Node points for SDS and LS were unassigned and then reassigned. After that LS can be loaded (Pandey, Vijay Mar 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The perceived &quot;failure&quot; is due to a completely unrelated issue.<br>Please look at the output from the import operation (SIS_data_export_and_import-2.txt). This import operation did not complete. It failed because of a bogus attribute for the deluxe analog. As a result, the import operation did not complete and finish the assignments of SIS objects.<br><br>The attributes LOW_REASONABLITY_LIMIT and HIGH_REASONABILITY_LIMIT are not applicable for deluxe analog points -- these are defined separately for each plant mode. How these attributes are currently in your database is unknown -- probably an artifact from an earlier issue.<br><br>Note that there are other such errors in the import file supplied in drop2500321.zip. Please perform an import with the -c switch to &quot;continue in spite of errors&quot; -- this may provide you with the complete list of items which should be removed from the import file.<br><br>The testing of SDR 19293 must be performed with an import file which has no unrelated issues of its own. (Swartz, Mark E. Mar 21, 2013)<br>VP-03/22/13- Performed the SIS data base export and import, found Hardware inconsistency error while performing LS loading. Detailed steps are mentioned. <br>1. Exported the SIS data base. Then, Imported the SIS data base exported file. For reference &quot;SISEXPORT.exp&quot; exported file and &quot;export-import session.txt&quot; cmd line session are attached. <br>Steps and observation after import:1.Performed LS load, it gives Hardware inconsistency error. Screenshot &quot;LS-HW-error.jpg&quot; is attached <br>2. Generated switch configuration file through studio and found &quot;XDBID&quot; of data base server and &quot;XDBID&quot; in DHCP file is mismatched and it is modified from &quot;17&quot; to &quot;11&quot; after import.For reference screenshot &quot;XDBID-Mismatch.jpg&quot;, &quot;XDBID SIS-IO.JPG&quot; is attached <br>3. Upon performing download of controller drop, studio shows number of files to be downloaded the controller since it was fully load / downloaded before the import operation. Screenshot &quot;download ctrl.jpg&quot; is attached. After download of controller LS can be loaded again <br>4. Loaded the LS and controller, all SDS and LS points go BAD 5. Configuration loaded to SIS switches. rebooted the SDS. SDS and LS point become GOOD.Note: All files in &quot;032213.zip&quot; (Pandey, Vijay Mar 22, 2013)<br><br>This SDR deals with the ability of the Engineering Tools to alter the hardware information of process points assigned to LS I/O Channels (specifically, bits 24-31 of the FY field, which contains the XDBID value for the SDS). None of the above attachments or text have yet shown that this has been completely tested. Please reference SDR 19293 Test Recommendation (Swartz, Mark E. Mar 22, 2013)<br><br>As per developer, In an actual Safety system there are more operations which need to be performed (e.g., generate new switch configuration, reboot sds, load Logic Solvers, etc¿.) again following an import operation containing SIS objects. However, that is not the immediate concern of the SDR 19293. If an import operation is performed which contains objects which have XDBID values (e.g., SIS Network Data Servers), the actual XDBID attribute values must be recalculated. Again, this is by design. <br>Followed the Test recommendation and it is verified that After an import operation involving a SIS Network Data Server object, all Ovation point assigned to a SIS I/O Channel in a Logic Solver under the imported SIS Network Data Server object, have its FY field recalculated following an incremental load operation to the SIS Ovation Controller. It is verified via SHC_Demo. Hence Finding is closed. (Pandey, Vijay Mar 28, 2013) <br> |  | 35 | FINDING | 9547 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75363
30669 | FINDING | Help of SDS firmware upgrade needs modification. | Maggu, Mukesh EMR SYSS PWS NOIDA | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Results shown in SDS firmware upgrade in Online manual is different then the actual results.<br>Attached is the actual results in Ov3.5.0. (Kumar, Shailendra Mar 21, 2013) |  |  |  | MM 02/4/2014: The required information is corrected in 5.16.1 To initially load or upgrade an SIS Data Server of OW351_47, SIS User Guide. The user guide is kept at Q:\Communication\TechComm\Share\Validation. The changes will also be reflected in the online help.(Maggu, Mukesh Feb 4, 2014) | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | MM 02/4/2014:Check the required information in 3.5.1 U5 build.(Maggu, Mukesh Feb 4, 2014) (Maggu, Mukesh Feb 4, 2014) <br> |  | 35 | FINDING | 9549 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.1_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | MM 02/4/2014: The required information is corrected in 5.16.1 To initially load or upgrade an SIS Data Server of OW351_47, SIS User Guide. The user guide is kept at Q:\Communication\TechComm\Share\Validation. The changes will also be reflected in the online help.(Maggu, Mukesh Feb 4, 2014) | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75367
30676 | FINDING | VC status doesn"t follow its Host status in Host based redundancy in a particular case | Long, Edward M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | SDR#19418:Remote logged in to Redundant VCH drop226/drop227 &amp; Redundant VC drop156/drop157 on EMILY network in Pgh Lab. Tried different possibilities by rebooting VCH/VCs when they are in Contol/Backup mode to check whether VC follows the status of its host. In most of the cases it follows but for a particular case is doesn&quot;t follow. Please refer the attached snapshot which is self explanatory. (Lal, Ramesh Mar 28, 2013)<br><br>4/01/2013: Retested after download/reboot of Redundant Virtual Controllers and found that VCs follow Host status in that particular case as well which was not ok earlier. Hence finding is closed. (Lal, Ramesh Apr 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9556 |  | FINDING | [10 empty] | Implementation | OVA350014 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75380
30677 | FINDING | SDR#18548 "Module communication disruption during download could render the module inoperative" partially failed. | Christy, Benjamin A PROCESS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | SDR#18548 &quot;Module communication disruption during download could render the module inoperative&quot; partially failed.<br><br>Following steps are performed in Ov3.5.0<br>1. ELC module has been configured in 1.1.5 in drop7/57 (OCR400).<br>2. Modbus TCP configuration has been configured &amp; is working OK. <br>3. Installed patch OVA350014 &amp; download the module firmare through diagnostic.<br>4. Verified the module operate normally after firmware download.<br>5. Now again started firmware download of module through diagnostic &amp; interrrupted the<br> download by reseating the module.<br>6. Verified that module operate normally after reseating.<br>7. After reseating the module firmware download of module fails for a file at which <br> interruption was made at step5 but download for remaining files were successful.<br>8. After repeating step5 several times (4-5) then module firmware download fails<br> with the error FAILED:module file access failure ( please find the attached <br> snapshot). However the modbus operation are working fine. (Sahay, Madhukar Apr 2, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> Firmware (FW)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Christy, Benjamin</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2013-04-02T07:06:29-04:00</p> <p><strong>Modified Date:</strong> 2013-12-03T15:10:30-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9557 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75381
30682 | FINDING | SIS events messages for LS Events are not updated in user level language. | Budzynski, Piotr EMR SYSS RS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | 1. Performed Action- power off Standby LS.<br>Observation: Appeared LS Events are not in user level language. Message &quot;Standby &quot;LS Power off.txt&quot; file is attached.<br>2. Performed Action- Reapplied power to Standby LS. <br>Observation: Appeared LS Events are not in user level language. Message &quot;Repower Standby &quot;LS.txt&quot; file is attached.<br>3. Performed Action- power off both LS card. <br>Observation: Appeared LS Events are not in user level language. Message &quot;Power off-both LS Card.txt&quot; file is attached.<br>4. Performed Action- Reapplied power to both LS.<br>Observation: Appeared LS Events are not in user level language. Message &quot;Repower-both LS card.txt&quot; file is attached. (Pandey, Vijay Apr 3, 2013) (Pandey, Vijay Apr 3, 2013) |  |  |  | Repeat steps from &quot;Description&quot; and verify that none of events is present: &quot;$ls_advise_alerts:10&quot; &quot;$ls_advise_alerts:11&quot; &quot;$ls_comm_alerts:0&quot; &quot;$ls_maint_alerts:10&quot; &quot;$ls_maint_alerts:11&quot; &quot;$ls_maint_alerts:8&quot; &quot;$ss_control_status:7&quot; &quot;$ss_control_status:8&quot; &quot;$ss_redun_status:4&quot; &quot;$ss_redun_status:5&quot; [INTERNAL ERROR: Unable to decode] | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | Observed events:<br>&quot;$ls_advise_alerts:10&quot;<br>&quot;$ls_advise_alerts:11&quot;<br>&quot;$ls_comm_alerts:0&quot;<br>&quot;$ls_maint_alerts:10&quot;<br>&quot;$ls_maint_alerts:11&quot;<br>&quot;$ls_maint_alerts:8&quot;<br>&quot;$ss_control_status:7&quot;<br>&quot;$ss_control_status:8&quot;<br>&quot;$ss_redun_status:4&quot;<br>&quot;$ss_redun_status:5&quot;<br>are DeltaV specific and has been removed from the list of available communicates. (Budzynski, Piotr May 6, 2013) <br> |  | 35 | FINDING | 9562 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30683 | FINDING | Event messages do not come, on power off the both SDS(pri and sec) and Lock/Unlock operation of LS. | Budzynski, Piotr EMR SYSS RS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Steps performed and observation are as follow:<br>1. Performed Action- Powered off Both SDS( Primary and Secondary). <br>Observation: No event message comes in SIS Events. <br>Note: When power off performed with the standby/Active SDS only, event messages appeared normally.<br>2. Performed Action - Performed Lock operation of Logic Solver. <br>Observation: No event message comes in SIS Events. <br>3. Performed Action - Performed Unlock operation of Logic Solver. <br>Observation: No event message comes in SIS Events. (Pandey, Vijay Apr 4, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | As for point number 1 WAD - explanation is given in finding 9573<br>http://uspit-web08.emrsn.org/sdr/ReportsSDRServlet?PrNumber=9573&amp;W=F (Budzynski, Piotr Apr 12, 2013) <br> |  | 35 | FINDING | 9563 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.1_U0 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30685 | FINDING | Backup controller does not come into control mode when disconnect RJ-45 connectors from media converter to N2 & N3. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Controller:- OCR1100 G02<br>Drop:- Drop12/drop62<br>Ov :- OV 3.5.0 (Net#8)<br>Patch used: - OVA350014<br>SFP Part no.: - FTLF1217P2BTL<br>Media Convertor: - EL100T<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1OFF<br>2ON<br>3OFF<br>4OFF<br>5OFF<br>6OFF<br><br>Case1:- <br>1:- Suppose Drop12 is in control mode (GREEN in SSD) &amp; Drop62 (YELLOW in SSD) is in Backup mode.<br>2:- For Drop12, disconnect RJ-45 connectors from media converter end that is attached to N2 &amp; N3 (both).<br>3:- When observed in SSD graphic 1800, drop12 goes into OFF HIGHWAY but drop 62 still remain in Backup mode &amp; do not come into Control mode.<br>Please refer screen Shots &quot; Error log1.jpg&quot; (Error Log details) &amp; &quot;SSD &amp; PI1.jpg&quot; (SSD).<br><br>Case2:- <br>1:- Suppose Drop12 is in control mode (GREEN in SSD) &amp; Drop62 (YELLOW in SSD) is in Backup mode.<br>2:- For Drop12, disconnect RJ-45 connector from media converter end that is attached only to the N3.<br>3:- As seen from the screen shot &quot;SSD &amp; PI2.jpg&quot;, Graphic 1800 shows drop12 is in OFF HIGHWAY mode while K0 &amp; K1 states are Available &amp; Active. However, in this case Graphic 1800 should show drop12 in control mode with N2 link Active. Also, K0 &amp; K1 states should be Active &amp; Unavailable state.<br><br>Case3:- <br>1:- Same thing as observed in case2 but this time disconnect RJ-45 Connector to the media converter attached to the N2 for Drop62. Doing so, Drop62 goes into OFF Highway. (Agarwal, Gaurav Apr 5, 2013) (Burgoon, Frank J. Apr 5, 2013) |  |  |  | A bug in hwy_stat was fixed. Please turn this into an SDR and retest. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A bug in hwy_stat was fixed. (Zaremsky, Mark Apr 24, 2013)<br>---<br>msb - Closed. Converted to SDR 19578 (Benzvi, Mati Apr 24, 2013) <br> |  | 35 | FINDING | 9565 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Burgoon, Frank AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75397
30691 | FINDING | SIS Module event message are not updating properly. | Budzynski, Piotr EMR SYSS RS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Steps are follow<br>1. Created LS DVTR logic.<br>2. Set one of its input to 0, module events message not appeared.<br>As per SRF and SVTP message &quot;message: &lt;param1&gt; voting to trip&quot; needs to be appeared.<br>3. Set other two inputs to 0,module events message not appeared.<br>4. Repeat above steps with Algo &quot;LSCEM&quot;, module events message not appeared.<br>Observation: Message &quot;&lt;SdsEvent: SDS001&gt;: XDB: XDB: rebuilding freq#0&quot; appeared for each occurance of all above mentioned events.<br>For reference Historical sis module events text file &quot;sis_mod_events.txt&quot; is attached. (Pandey, Vijay Apr 9, 2013) |  |  |  | Repeat steps 1-3 from &quot;Description&quot; section. &quot;Voting to trip&quot; events should be back on the list. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | &quot;&lt;param1&gt; voting to trip&quot; messages are originated on the Logic Solver and time stamped there.<br>Message is passed to SDS, then to the Controller.<br>Due to an issue in setting Sis Logger addresses &quot;sis_logger&quot; task was not started on the Controller.<br>It has been fixed. (Budzynski, Piotr Apr 17, 2013)<br><br>Responsible engineer changed to Budzynski, Piotr. I assume that by mistake it was assigned to me. (Pandey, Vijay Jun 3, 2013) <br> |  | 35 | FINDING | 9571 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [7 empty] | Implementation | 3.5.1_U0 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30692 | FINDING | Help for SIS events not available. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Historical SIS events can be accessed via Historical Review -SIS tab.<br>Help for SIS events are not available. (Pandey, Vijay Apr 9, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Documentation (DOC)</p> <p><strong>Subproduct:</strong> Historical Review (HR)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2013-04-09T06:35:00-04:00</p> <p><strong>Modified Date:</strong> 2013-05-13T09:42:23-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9572 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75410
30693 | FINDING | No expected message comes after both SDS rebooted. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Steps performed:<br>Reboot both SDSes from redundant pair. As per SRF and SVTP, expected message &quot;Message: No SIS configuration packets&quot; not updated. Appeared messages &quot;SDS rebooted messages.txt&quot; text file attached. (Pandey, Vijay Apr 9, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is a duplicate of Finding#9563. (Budzynski, Piotr Apr 11, 2013)<br><br>---------------<br><br>Message: &quot;No SIS configuration packets&quot; can be seen in two situations:<br>1. Both Ovation SIS controllers are rebooted at the same time,<br>2. Both Ovation SIS controllers are cleared.<br>This message does not apply to the SDSs being rebooted.<br><br>SVTP 5.5.5 Test must be fixed, please take in account Jakub Czak comment.<br><br>Information about both SDSs not responding is available on the Historian Alarm tab. (Budzynski, Piotr Apr 12, 2013) <br> |  | 35 | FINDING | 9573 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75412
30698 | FINDING | Incorrect Fielbus Module Firmware file for OCR1100 controllers. | Zaremsky, Mark External MZCI | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | After downloading a working Fieldbus module on an OCR1100 controller with Ovatioin 3.5 and patch 14 installed, and then rebooting the module, the module was no longer operational. Further investigation revealed that the ARM-7 firmware that was downloaded to the module as part of the Firmware download process for OCR1100 controllers was incorrect. When the proper version of ARM-7 firmware was installed, the module resumed proper operation. (Wood, Tom Apr 9, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> I/O Module Firmware (IOMF)</p> <p><strong>Subproduct:</strong> Firmware Download (FDWN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Wood, Tom</p> <p><strong>Responsible:</strong> Zaremsky, Mark</p> <p><strong>Notify List:</strong> Ciccozzi, Anthony Wood, Tom</p> <p><strong>Entry Date:</strong> 2013-04-09T13:32:52-04:00</p> <p><strong>Modified Date:</strong> 2013-04-09T13:38:37-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9578 |  | FINDING | Ciccozzi, Anthony AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75421
30699 | FINDING | Need to modified test case 3.2.1, a & b of SFP_SVTP_rev1.0_GAx.doc SVTP. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | It is observed in Test case 3.2.1 a &amp; b of SFP_SVTP_rev1.0_GAx.doc SVTP that extra Row has been added but none of the test case is there. So it should be removed from the SVTP. (Agarwal, Gaurav Apr 10, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 5/7/13 - fixed in rev 1.1 of SFP_SVTP. (Capani, Nooch May 7, 2013) <br> |  | 35 | FINDING | 9579 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75423
30700 | FINDING | In Ov350 "Point Review window" is getting hanged while stopping "Point Initialization". | Burgoon, Frank AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | When click on &quot;point initialization stop button&quot;, Point Review window gets &quot;hanged&quot;.<br>(Highlighted in attached snapshot: &quot; PointReview_error.jpg&quot;).<br>To recreate the Issue:<br>Ovation Application-&gt;Point Review-&gt; Click on Start and let points come-&gt;When Point Initialization begins, Click on Point Initialization Stop Button. (Jha, Rahul Apr 10, 2013) (Jha, Rahul Apr 10, 2013) | none |  |  | Test functionality of point initialization stop button. | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Review (PR)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Jha, Rahul</p> <p><strong>Responsible:</strong> Burgoon, Frank J.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jha, Rahul</p> <p><strong>Entry Date:</strong> 2013-04-10T07:28:10-04:00</p> <p><strong>Modified Date:</strong> 2013-12-30T13:28:16-05:00</p> | 0 |  | Ovation for Windows/General/Software | Point initialization stop button now operates correctly. (Burgoon, Frank J. Sep 24, 2013)<br><br>IC 12/30/13:<br>Per testing by RJ, issued is resolved in 3.5.1_U3. <br>Since issue still exists in 3.5.0, Finding will remain OPEN until Dev requests an SDR so it can be patched or marks it as WIW (no plans to fix). (Capani, Nooch Dec 30, 2013) <br> |  | 35 | FINDING | 9580 |  | FINDING | Jha, Rahul AUTOSOL PWS NOIDA | [10 empty] | 3.5.1_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | none | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75424
30704 | FINDING | Histroical Review is crashed while we search the SIS point. | Contento, James AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Open Historical review window--&gt;selct &quot;SIS&quot; tab --&gt;Now Begin review<br>here Historical review window get crashed.<br><br><br>Error Details are as below mentioned:-<br><br><br>Problem signature:<br> Problem Event Name:APPCRASH<br> Application Name:HistReview.exe<br> Application Version:3.5.0.0<br> Application Timestamp:51304740<br> Fault Module Name:MSVCR100.dll<br> Fault Module Version:10.0.40219.1<br> Fault Module Timestamp:4d5f0c22<br> Exception Code:c0000005<br> Exception Offset:000027a3<br> OS Version:6.1.7601.2.1.0.16.7<br> Locale ID:1033<br> Additional Information 1:0a9e<br> Additional Information 2:0a9e372d3b4ad19135b953a78882e789<br> Additional Information 3:0a9e<br> Additional Information 4:0a9e372d3b4ad19135b953a78882e789<br><br>Read our privacy statement online:<br> http://go.microsoft.com/fwlink/?linkid=104288&amp;clcid=0x0409<br><br>If the online privacy statement is not available, please read our privacy statement offline:<br> C:\Windows\system32\en-US\erofflps.txt (Kumar, Sudheer Apr 16, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | There have been Historical Review fixes for application crashes. Is this specific test failure still an issue? (Contento, James L. Nov 4, 2013)<br><br>Historical Review is not crashing now. (Kumar, Sudheer Nov 18, 2013) <br> |  | 35 | FINDING | 9584 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75433
30712 | FINDING | Disconnect the RJ-45 Connector from media converter, Link is start toggling between RED & Yellow in SSD. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Controller: - OCR1100 G02<br>Drop: - Drop12/drop62<br>Ov: - OV 3.5.0 (Net#8)<br>Patch used: - OVA350014<br>SFP Part no.: - FTLF1217P2BTL<br>Media Convertor: - EL100T<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1OFF<br>2ON<br>3OFF<br>4OFF<br>5OFF<br>6OFF<br><br>When we disconnect the RJ-45 connector from the media convertor attached to the either N2 or N3,Link is start toggling between RED &amp; Yellow in SSD While Error Log is displaying correct error.<br>But when we disconnect either LC Connector or ST Rx or Tx connector, Link is not toggling. it show correct behavior in SSD.<br><br>Observation in Drop DU Record (Using PI) is following.<br>1:- Disconnect the RJ-45 from the Media converter.<br> K0:- Toggling between Available &amp; Unavailable state<br> K1:- Remain in Active state <br>2:- When disconnect the either Tx or Rx connector to the media converter,<br> K0:- Unavailable state<br> K1:- Active state<br><br>Note:- Same observation is observed . When used the SFP (FTLF1323P1BTR) &amp; Media converter (EL100T-20) (Agarwal, Gaurav Apr 17, 2013) |  |  |  | A bug in hwy_stat was fixed. Please turn this into an SDR and retest. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A bug in hwy_stat was fixed. (Zaremsky, Mark Apr 24, 2013)<br>---<br>msb - Closed. Converted to SDR 19577 (Benzvi, Mati Apr 24, 2013) <br> |  | 35 | FINDING | 9592 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75449
30714 | FINDING | Right click options available in studio of Mapped remote network are invalid. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | On drop176,Server2008,Ov3.5.0 (FE350 network) opened studio.<br>Mapped Remote network FENET10 and then opened studio of FENET10.<br>On right clicking any drops of FENET10 it gives options which are invalid at drop level for ex:Update security infrastructure, Run SIS configuration etc (attached is the snapshot).<br>FENET10 is Ov3.2.0 network. (Kumar, Shailendra Apr 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is the way it works per the Ovation Engineering Tools architecture. One cannot engineer a remote Ovation System which is at a different release level. (Swartz, Mark E. Apr 17, 2013)<br><br>Agreed, Basically options available on right click is not valid for ex: in snapshot you can see &lt;run SIS configuration&gt; option, On ov3.2.0 no SIS is present still we get this option. (Kumar, Shailendra Apr 18, 2013)<br><br>Closed as per dev&quot;s comment. (Kumar, Shailendra Apr 19, 2013) <br> |  | 35 | FINDING | 9594 |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75453
30715 | FINDING | Undocumented Fault code:66,b,6,8011 is constantly seen on SIS OCR1100 controller. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-03-11 02:49 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-03-11 02:49 |  |  |  | 2016-03-11 02:49 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | On SIS Controller drop23/drop73(OCR1100) we constantly see fault code 66,b,6,8011.<br>Error log of this controller shows(attached is detail error) :<br>&lt;132&gt; SISIO : XDB: Data packets from host #11 logic solver #3 have timed out<br>&lt;132&gt; SISIO : XDB: Diagnostic data packets from host #11 (freq #0) have timed out (Kumar, Shailendra Apr 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <br> |  | 35 | FINDING | 9595 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | The 8011 means there is a problem with Alarm mapping file for host 11 and LS 6, currently there is no way to investigate this as i am unable to recreate it.<br> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | UNKNOWN |  |  | FINDING | [6 empty] | 93265
30718 | FINDING | LSAVTR algo shows output as BAD if third I/P is not connected. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | LSAVTR algo shows output as BAD if third I/P is not connected.<br>SIS sheet is made in SIS controller drop23/73 (SLS02 , control module -2)containing LSAI and HAI connected to IN1 and IN2 of LSAVTR algo.<br>Values of IN1 and IN2 is changing GOOD quality and third pin is not connected.O/P is seen as BAD.If allthe three I/Ps are connected O/P shown is GOOD.<br>For reference attached the SIS sheet used and snapshot showing BAD quality.<br>Also attached is the SIF data for reference. (Kumar, Shailendra Apr 22, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <br> |  | 35 | FINDING | 9598 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
30721 | FINDING | OSM doesnot display Networks names when more than 90 networks are configured | Burgoon, Frank AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | On Ov-3.5.0 - Glenn network - Drop100:<br> - 299 Remote networks are configured in: System - External system Interface.<br> - 99 Remote networks were imported in: Network - External Network Connections<br> - 99 Remote networks were imported in: <br> Network - Local Alarm Collectors - drop100 - External Alarm Collector Networks.<br>When the drop is downloaded and restarted the Ovation Session Manager shows the network <br>name of the 1st 89 networks and the last 10 networks remain blank.<br>The correct data seems to be in the Registry: config.shc &amp; alarm_config.dat (Benzvi, Mati Apr 22, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Ovation Session Manager (OSM)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Benzvi, Mati</p> <p><strong>Responsible:</strong> Burgoon, Frank J.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Benzvi, Mati</p> <p><strong>Entry Date:</strong> 2013-04-22T09:35:34-04:00</p> <p><strong>Modified Date:</strong> 2013-04-22T09:35:34-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9601 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75464
30725 | FINDING | Downloading a Fieldbus port crashes studio. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | After adding a new fieldbus device and creating a control sheet using an algorithm from the new device, the controller was loaded. It was then attempted to download the port containing the new device and at that point the studio crashed. (Wood, Tom Apr 23, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Converted to SDR 19588 for tracking in patch OVA350017<br>- (Hutchison, Steven B. May 6, 2013) <br> |  | 35 | FINDING | 9605 |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75472
30726 | FINDING | Controller can not communicate properly with FFMDO and FFISEL Fieldbus Algorithms | Pratley, Bob EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | When using either an FFMDO or FFISEL algorithm from a Fieldbus device on a control sheet the algorithm&quot;s value is not handled properly by the controller and is always shown as 0B. (Wood, Tom Apr 23, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The device used in this configuration in the validation lab was a Rosemount 848T. The Input Selectors in this device are compatible with our FFISELX algorithm but our FFISEL algorithm was configured in the control sheet. Once the FFISEL was deleted and replaced by FFISELX, the Fieldbus segment operated correctly. (Pratley, Bob May 14, 2013) <br> |  | 35 | FINDING | 9606 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | User Error | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75474
30733 | FINDING | If any menu of Device Manager is clicked during controller failover then error message appears. | James, Matt AUTOSOL PSS AUS | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Following steps are performed in Ov3.5.<br><br>1.AMS DM server &amp; client has been installed in drop247(EWS) &amp; drop250(DBS) respectively.<br>2.Field bus module has been configured in 1.2.1 in drop32/82 &amp; 848T &amp; 3144MV device<br> has been configured at segment1 &amp; 2 repectively.<br>3. It is observed that if any context menu (e.g configure/setup etc) of Device Manager is <br> clicked during controller failover then ¿Unable to connect live device¿ error message<br> appeared. However if menu is clicked after few secs (10-15 secs) of failover then <br> it open correctly. (Sahay, Madhukar Apr 24, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Asset Management System (AMS)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> James, Matthew</p> <p><strong>Notify List:</strong> James, Matthew Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2013-04-24T07:43:42-04:00</p> <p><strong>Modified Date:</strong> 2013-04-24T07:43:42-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9613 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75487
30739 | FINDING | TR "3.5_SRF1361_SVTP_rev1.0.doc" needs some modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | AMS context menu will be visible if user is not configured in AMS,<br>so test case 5.2.3 of TR &quot;3.5_SRF1361_SVTP_rev1.0.doc&quot; should be <br>&quot;Verify the user cannot access the device using the Ovation Device right-click context menu if they are not configured in the AMS User Manager&quot; instead of <br>&quot;Verify ¿Device Manager¿ context menu is hidden if Ovation user is not configured in AMS&quot; (Sahay, Madhukar Apr 26, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2013-04-26T06:47:46-04:00</p> <p><strong>Modified Date:</strong> 2013-04-26T06:47:46-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9619 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75498
30746 | FINDING | TR "3.5_SRF1361_SVTP_rev1.0.doc" needs some modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | (a). In test case 5.4.3 for procedure 14 it is mentioned to &quot;See comment for steps <br> verification&quot; but text verification for step 12 is written twice later one is for<br> procedure 14 so it should be replaced to verification for step14.<br><br>(b). In test case 5.4.7 &quot;Verification for Step8&quot; is for procedure 9 so in TR<br> it should be mentioned &quot;Verification for Step9&quot; instead of &quot;Verification for Step8&quot;.<br><br>(c). In test case 5.4.8 for procedure 5 it is mentioned to &quot;See comment for steps <br> verification&quot; but text verification for step 3 is written twice later one is for<br> procedure 5 so it should be replaced to verification for step5.<br> <br>(d). In test case 5.4.12 for procedure 18 it is mentioned to &quot;See comment for steps <br> verification&quot; but text verification for step 7 is written twice later one is for<br> procedure 18 so it should be replaced to verification for step18. (Sahay, Madhukar Apr 29, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2013-04-29T07:19:49-04:00</p> <p><strong>Modified Date:</strong> 2013-04-29T07:19:49-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9626 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75511
30747 | FINDING | SVTP ¿3.5_SRF1516_SVTP_rev1.1_VP.docx¿ needs to be modified | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Following test cases of SVTP ¿3.5_SRF1516_SVTP_rev1.1_VP.docx¿ needs to be modified.<br>1.Test case 5.5.7 statement &quot;Verify that the message for these events are in the OPH and are viewable in the Historical Review&quot; needs to be replaced with &quot;Verify that these messages are available in Historical Review in Operators Events subsystem.&quot;<br>2.Events mentioned in Test case 5.5.5 needs to be referred as ¿LS Events¿ instead of ¿SDS Events¿. (Pandey, Vijay Apr 30, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2013-04-30T01:03:19-04:00</p> <p><strong>Modified Date:</strong> 2013-04-30T01:03:19-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9627 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75512
30748 | FINDING | In¿3.5_SRF1516_SVTP_rev1.1_VP.docx¿SVTP,expected message does not apply for test case 5.5.5(c) | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Message: &quot;No SIS configuration packets&quot; can be seen in two situations:<br>1. Both Ovation SIS controllers are rebooted at the same time,<br>2. Both Ovation SIS controllers are cleared.<br>As per developer explanation in Finding# 9573, this message does not apply to the SDSs being rebooted. Hence Test case5.5.5 (c) needs to be removed. (Pandey, Vijay Apr 30, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Controller (Ctlr)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Pandey, Vijay</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Pandey, Vijay</p> <p><strong>Entry Date:</strong> 2013-04-30T01:19:37-04:00</p> <p><strong>Modified Date:</strong> 2013-04-30T01:19:37-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9628 |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75513
30763 | FINDING | PI is not showing [Standard] value of [Analog Point] after 8 digits. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Analog Point is configured as &quot;Standard&quot; &amp; number of digits 10 in developer studio of Ovation 3.5.0.<br>In PI, [AV] field shows &quot;Standard&quot; value of analog point up to 8 digits only. Beyond 8 digits value, PI is showing value in &quot;Exponential&quot; notation. Similarly Trend is also showing value in &quot;Exponential&quot; notation beyond 8 digits.<br>Please find the attached snapshot. (Jain, Yukta May 1, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Operator Station programs only show so many digits in their displays. If they cannot display the number it will revert to exponential. By the way your example has nothing to do with 10 decimal places being configured. It is 1E8 because it is too large for 8 digits (McMaster, James May 13, 2013) <br> |  | 35 | FINDING | 9643 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75543
30773 | FINDING | deviceHierarchy.xml error appeared sometimes in controller which has field bus device. | Morris, Gilbert L AUTOSOL PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Following steps are performed.<br><br>1. Field bus device has been configured 1.1.5 in drop32/82 (OCR400).<br>2. It is observed that if any operation e.g drop load,adding foundation field bus <br> device, unload/download function block, port download etc then sometimes error error <br> message appeared &quot;Failed to load deviceHierarchy.xml&quot;. (Please refer the attached snapshot)<br> However upon pressing the &quot;OK&quot; button operation complete. (Sahay, Madhukar May 3, 2013)<br><br>1. Is this repeatable on your system?<br>3. Can we have access to the effected system?<br>2. Can you please provide us with the deviceHierarchy.xml file on the effected system?<br> It will be located in OvPtSvr\FoundationFieldbusDevices. (Morris, Gilbert L. May 3, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1. I tried to reproduce this error but I couldn&quot;t, However it was appeared many times on 05/03.<br>2. deviceHierarchy.xml file has been attached for your review.<br>3. Remote log in steps are below :<br> Login to drop250 with the following credentials<br> Ip address for remote login from Pgh: 10.132.153.96<br> Username : administrator<br> Password : Welcome@1234<br> Domain : Val9Dc9<br>(PS : Field bus module has been configured in 1.2.1 in drop32/82(OCR400)&amp; drop250 is DBS)<br> I am changing the finding state to MIS. (Sahay, Madhukar May 6, 2013) (Sahay, Madhukar May 6, 2013) <br> This error not seen afterwords, I am keeping this finding in monitorig state. (Sahay, Madhukar May 14, 2013) |  | 35 | FINDING | 9653 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75563
30775 | FINDING | Special character like "@" is not accepted in the Password for Security Database Users & window closes after that | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Thru Ovation Security Manager --&gt; Manage Database User, to reset the password of &quot;ptadmin&quot; user other than the default, if a special character say &quot;@&quot; is specified then while applying it gives error message &quot;ORA-00922: missing or invalid option&quot; as seen in the attached file database-user-password.jpeg. I was giving the password &quot;welcome@1234&quot;.<br>This issue has been shown to Sunil Sharma also. (Gupta, Chandresh May 3, 2013)<br><br>cg (05/07/13) - When the error message appears with invalid special characters entry, upon clicking [OK] button the Security Manager window closes on its own. Hence state of this finding has been changed from WIW to DRR. (Gupta, Chandresh May 7, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | No plans to address this special character.<br>If any other special characters do not function as expected, include in this same SDR. Documentation will be changed to indicate special characters which are supported or not supported as Ovation database passwords. (Swartz, Mark E. May 3, 2013)<br><br>The error dialog will be changed to permit the user to choose between closing the application and continuing. (Swartz, Mark E. May 7, 2013)<br><br>cg (05/09/13) - SDR#19597 entered against this finding hence this is closed. (Gupta, Chandresh May 9, 2013) <br> |  | 35 | FINDING | 9655 |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75567
30781 | FINDING | Historical review does not save the "Historian Configuration" | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | Please follow the steps to recreate:<br>Open Historical Review (version-1.0.0) of Ovation 3.5.0 &quot;-&gt; Go to [Ovation Historical Review] Button &quot;-&gt; Select [Historical Review option] &quot;-&gt; Select [Historian] &quot;-&gt; Add Host Name &amp; IP address -&quot;&gt; Click [ok] &quot;-&gt; New configured historian can be seen in list of [Historian] tab in Ribbon bar. Now Close the application &quot;-&gt; Reopen Historical Review &quot;-&gt; Newly added historian drop is no longer found in [Historical] tab in Ribbon bar. Every time we need to add new historian drop.<br>Also Historian drop already added in [Historian] cannot be deleted. (Jain, Yukta May 7, 2013) (McMaster, James May 7, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Documentation (DOC)</p> <p><strong>Subproduct:</strong> Historical Review (HR)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Jain, Yukta</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jain, Yukta</p> <p><strong>Entry Date:</strong> 2013-05-07T00:09:00-04:00</p> <p><strong>Modified Date:</strong> 2013-05-13T09:28:02-04:00</p> | 0 |  | Ovation for Windows/General/Software | 1) You have to save Historian Preference for it to be retained.<br>2) To delete, select and hit Delete key on your keyboard. (McMaster, James May 7, 2013)<br><br>YJ:<br>The finding was WAD, changing it to DRR.<br>Issue is resolved. I can add &amp; delete historian by follow procedure provided by you.<br>But there is no information/procedure (As you explain in resolution) found in [Help] regarding-&quot;how to Configure &amp; delete Historian in [Historical Review option]&quot;<br>I believe this information can be documented for future reference (Jain, Yukta May 8, 2013) <br> |  | 35 | FINDING | 9661 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75578
30782 | FINDING | Ovation document needs to be update to include applicable special characters for Security Database User Passwords | Maggu, Mukesh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 | [7 empty] | USPITTFSService | 2015-06-12 04:05 |  | As per Oracle password rules (obtained from the website (http://docs.oracle.com/cd/E12547_01/books/SalesComV2.0/index.htm?toc.htm?AboutPasswordRuleshelp.html), the special characters that are accepted are @, -, _, :, &quot;, *, !, $, ., ,, #, / and \.<br>However, the Ovation Security Database User Password accepts only 3 special characters viz. &quot;_&quot;, &quot;$&quot; and &quot;#&quot;. The same needs to be updated in the Ovation document. Please also refer F#9655. (Gupta, Chandresh May 7, 2013) | MM (6-Dec-2013): A note has been added at step 4 in the section 13.2: To reset the database user password. You can check ir in the manual (OW351_40.pdf) atQ:\Communication\TechComm\Share\Validation\Mukesh(Maggu, Mukesh Dec 6, 2013). (Maggu, Mukesh Dec 6, 2013). also, online help will be avialable in U3 build. |  |  | MM (6-Dec-2013): A note has been added at step 4 in the section 13.2: To reset the database user password. You can check ir in the manual (OW351_40.pdf) atQ:\Communication\TechComm\Share\Validation\Mukesh(Maggu, Mukesh Dec 6, 2013). (Maggu, Mukesh Dec 6, 2013). also, online help will be avialable in U3 build. | 0 |  |  |  | <p><strong>Product:</strong> Documentation (DOC)</p> <p><strong>Subproduct:</strong> Developer Studio (DS)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Gupta, Chandresh</p> <p><strong>Responsible:</strong> Maggu, Mukesh</p> <p><strong>Notify List:</strong> Capani, Nooch Gupta, Chandresh</p> <p><strong>Entry Date:</strong> 2013-05-07T00:09:45-04:00</p> <p><strong>Modified Date:</strong> 2013-12-05T22:32:17-05:00</p> | 0 |  | Ovation for Windows/General/Software | LC 05/08/2013: Re-assigned to Puneet Sharma. This fix is for the Managing Ovation Security Manual. Fix will be made in the Ovation 3.5.1 release. (Casteel, Linda May 8, 2013)<br><br>PS (27-Aug-2013): Changing the responsible engineer to Mukesh Maggu because<br>Managing Security 351 manual is assigned to him. (Sharma, Puneet Aug 27, 2013)<br><br><br>MM (19-Oct-2013): A note has been added at step 4 in the section 13.2: To reset the database user password. You can check ir in the manual (OW351_40.pdf) atQ:\Communication\TechComm\Share\Validation\Mukesh(Maggu, Mukesh Oct 19, 2013). (Maggu, Mukesh Oct 19, 2013)<br>cg (11/8/13) - Finding retested in U2. The note is available in OW351_40.pdf located at Q:\Communication\TechComm\Share\Validation\Mukesh. However, when we open the online help it is opening OW350_40.pdf and it does not contain the mentioned note. It seems that the .chm is not updated in U2. Based on this observation the finding is Open (Failed Retest). (Gupta, Chandresh Nov 7, 2013)<br><br>MM (6-Dec-2013): A note has been added at step 4 in the section 13.2: To reset the database user password. You can check ir in the manual (OW351_40.pdf) atQ:\Communication\TechComm\Share\Validation\Mukesh(Maggu, Mukesh Dec 6, 2013). (Maggu, Mukesh Dec 6, 2013). also, online help will be avialable in U3 build. (Maggu, Mukesh Dec 5, 2013) <br> |  | 35 | FINDING | 9662 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75579
30827 | FINDING | Output of FFMAI algorithm is BAD when it is in Manual mode. | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Following steps are performed in drop32/82 (OCR400) :-<br>1. Foundation fieldbus module has been configured at 1.2.1.<br>2. 848T device has been connected in its segment1.<br>3. Control sheet has been configured using FFMAI algorithm.<br>4. It is observed that FFMAI block is in Manual mode then all its ouput become BAD quality.<br> (Please refer the attached snapshot f#9707.jpg.) <br> However it is working fine in AUTO mode i.e it is updating sensor values. (Sahay, Madhukar May 15, 2013)<br><br>By mistake I attached F#9708.jpg , please ignore it. (Sahay, Madhukar May 15, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can you provide remote access details to the effected system for further investigation? (Morris, Gilbert L. May 23, 2013)<br><br><br>Remote Log in details has been attached :-<br>Control sheet containing FFMAI algorithm is created in : Task2 Sheet Name 848TT, <br>Sheet no:10 (002D.svg)<br><br>PS : Please ignore step2 in remote log in step2. (Sahay, Madhukar May 24, 2013) <br> Thank you for the remote acesss to this machine. I have completed my investigation into this issue and yes your system is effected. I have also looked into this issue on 2 different systems in Pittsburgh; 1 in Validation Lab and 1 in the Tools Group lab. Neither of these two systems are effected with what is described in this finding. I am marking this as &quot;Can Not Duplicate&quot;. (Morris, Gilbert L. May 28, 2013) |  | 35 | FINDING | 9707 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75669
30828 | FINDING | AMODE of FFMAI algorithm always remain 0. | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:05 | [11 empty] | USPITTFSService | 2015-06-12 04:05 |  |  |  | 2015-06-12 04:05 |  |  |  | USPITTFSService | 2015-06-12 04:05 |  | Following steps are performed in drop32/82 (OCR400) :-<br>1. Foundation fieldbus module has been configured at 1.2.1.<br>2. 848T device has been connected in its segment1.<br>3. Control sheet has been configured using FFMAI algorithm.<br>4. It is observed that Y0 field (AMODE) of its LC record always remains &quot;Zero&quot;<br> irrespective its mode is Auto or Manual.<br> Please refer attached snapshot for your reference. (Sahay, Madhukar May 15, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can you provide remote access details to the effected system for further investigation? (Morris, Gilbert L. May 23, 2013)<br><br>Remote Log in details has been attached :-<br>Control sheet containing FFMAI algorithm is created in : Task2 Sheet Name 848TT, <br>Sheet no:10 (002D.svg) (Sahay, Madhukar May 24, 2013) <br> Thank you for the remote acesss to this machine. I have completed my investigation into this issue and yes your system is effected. I have also looked into this issue on 2 different systems in Pittsburgh; 1 in Validation Lab and 1 in the Tools Group lab. Neither of these two systems are effected with what is described in this finding. I am marking this as &quot;Can Not Duplicate&quot;. (Morris, Gilbert L. May 28, 2013) |  | 35 | FINDING | 9708 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75671
30837 | FINDING | SDR # 19505 failed in the System Viewer. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Recreated the SDR.After loading the patch, The SDR # 19505 failed to resolve the issue in the System Viewer. ie, The Hierarchy Search default selections for the Status Filter, Fieldbus Commissioned are not blanks &amp; shows checked in. Fieldbus commissioned from uncommissioned (UC) to nothing selected is not happening.(not UC,CO) <br> the default for alert from failed(FS), maintenance (MS), advisory(AS), communication (CS) to nothing selected is again not happening. The SDR fails to fix the above issues. Verified in the drops of both the Net #7 &amp; NET#8 of DBS &amp; EWS drops of Ovation 3.5.0 (N, Thamaraiselvi May 16, 2013).<br><br>I checken in again to see the same details.<br><br>Please find the remote log-in details.<br><br>Sorry we had loaded the earlier patch by mistake. After loading the latest patches, found the SDR is fixed. Observed to see the mentioned fields in the SDR is blanks by sefault. Thus confirmed the SDR is fixed &amp; closing the finding.<br><br>Login to Ovation gateway drop250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username :administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9 . (N, Thamaraiselvi May 17, 2013)<br><br>This should be fixed when the latest patch is loaded. (Diane Wozniak May 17, 2013) (Wozniak, Diane M. May 17, 2013) (N, Thamaraiselvi May 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9717 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75689
30838 | FINDING | Exported file does not contains the time along with date. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | exported any or all grids as a text file.<br>opened up the text file to see the date and time .<br>exported as other formats does not contain the time along with date in all of them.<br>Thus failed the SDR#19506. (N, Thamaraiselvi May 16, 2013).<br><br>I checked in again to observe the same.<br><br>Please find the Remote log -in details.<br>Login to Ovation gateway drop250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9 . (N, Thamaraiselvi May 17, 2013)<br><br>This should be fixed when the latest patch is loaded. (Diane Wozniak May 17, 2013) (Wozniak, Diane M. May 17, 2013).<br><br>Sorry we had loaded the earlier patch by mistake. After loading the latest patches, found the SDR is fixed. Observed to see the time also along with the date in the exported file. Thus closing the finding. (N, Thamaraiselvi May 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9718 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75691
30841 | FINDING | "System Viewer" application needs an icon. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Click on Ovation application folder and see the &quot;System viewer&quot; application.<br>Here System viewer application doesn¡¦t have a specific icon.<br>Use the start--&gt; all programs--&gt;ovation--&gt;ovation application folder to see the icon.<br>Minimize the program and see the icon of system viewer. (Singh, Rajan May 17, 2013) (Singh, Rajan May 17, 2013)<br><br>This should be fixed when the latest patch is loaded. (Diane Wozniak May 17, 2013) (Wozniak, Diane M. May 17, 2013)<br>---<br>msb - Please retest with OVA350-020-05142013113025 (Benzvi, Mati May 20, 2013)<br>RS: Tested after loading new patch and found everything is working fine. Now issue is fixed. (Singh, Rajan May 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9721 |  | FINDING | [10 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75696
30842 | FINDING | Exporting operation shows unhandled exception error after loading the patch OVA350020. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Exporting operation in the DBS drops shows pop up error of unhandling exception &amp; file not saved after loading the patch OVA350020. This behaviour is observed in both the DBS drops of #176 in net 8 &amp; drop#250 in net 7.<br>Please find attached the jpg &amp; errordetails notepad files.<br>Please find the Remote log -in details.<br>Login to Ovation gateway drop250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9.<br>(Diane Wozniak May 17, 2013)<br><br>Once the latest patch is loaded, please try this again.<br>I do not believe the latest patch will fix this. <br>Mati and I could not recreate the problem on drop 176 or drop250.<br><br>I was able to log on to drop125 in Mati&quot;s lab and run the following test with no problem:<br>1. select the ovation applications folder<br>2. select system viewer (wait till it loaded)<br>3. right mouse on emnet (the network) and select expand all<br>4. scroll in the hierarchy list to get to drop 20/drop20 then select <br>5. select the icon in the upper left of the screen to display the load, search, print, export, preferences menu<br>6. select export<br>7. select export as<br>8. then choose a directory and a file name and file type (I picked c:\dmwtest\Friday.txt and text files(*.txt))<br>9. go to the specified directory. check out the new file.<br><br><br>If the problem persists, please provide the following information:<br>1.is this also a problem with the exporting in Point information or Point Review?<br>2. what are the exact steps to recreate the error?<br><br>Observed this behaviour randomly anytime when the system is &quot;ON&quot;.Also observed in the Print Command also.<br><br>-Yes.this is also the problem with the exporting &amp; printing operations in Point information and Point Review. While this is persisting in System viewer,sometimes the export operation works fine for PI &amp; PR where as the print operation throws error.<br>This is happening only after loading the latest Ova350020 patch &amp; only occuring in the DBS server drops of #176 &amp; 250 of net 8 &amp; net 7 respectively.Both are configured as Windows 2008 R2,64 bit.<br>exact steps to recreate the error-<br>when the system is &quot;ON&quot; anytime randomly, open OSV application.Once it ie ready, select any drop, allthe grid info appears. Menu-&gt;export-&gt;click export as then give the path in tne window.<br>Or from the Pi-menu-&gt;print-&gt; set up ok. throws error. The print operation sometimes crash thew application. <br>Please find the snapshots.<br>Please find the Remote log -in details.<br>Login to Ovation gateway drop#250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9.<br>From drom drop250, remote log-in #176.<br>Please find the Remote log -in details.<br>Login to Ovation gateway drop176 with the following credentials<br>Ip address for remote login drop176: 192.168.12.176<br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9.<br>(N, Thamaraiselvi May 21, 2013) (Benzvi, Mati May 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | dmw: Thank you for the information for finding 9722. I believe that the information you provided has enabled me to figure out what is going on.<br><br>It appears that the export and print functions for system viewer do not work correctly if a printer is not attached.<br>Please run the following tests (and any others you can think of) and let me know the results.<br>If any of these result in a run time exception (except for 1.), please be sure to dump the details file for me again.<br>1.Printer does not exist - try to print and export<br>2.Printer does exist and it is turned off - try to print and export<br>3.Printer does exist and it is offline - try to print and export<br>4.Printer does exist and is online - try to print and export<br><br>Please run the same tests on point information and point review. I would not be surprised if their tests have the same results as the systemviewer.<br>If they are in error, please make a separate finding for each of these programs. (Benzvi, Mati May 21, 2013).<br>Thanks for detailed info.<br>The system is under observation. I get error randomly. Shall post all the details once I finish detaily all the tests. (N, Thamaraiselvi May 22, 2013) <br> |  | 35 | FINDING | 9722 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75698
30843 | FINDING | SDR #19517 fails partially for the Hierarchy drop (drop type). | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | SDR #19517 fails partially for the Hierarchy drop (drop type) after loading the patch.<br>The grid fly over still appears for the Hierarchy drop (drop type) when the mouse is moved out of their window. It improves a bit &amp; passed for the drop Id, drop status &amp; fault codes.<br>Please find the attached snapshot for the reference. (N, Thamaraiselvi May 17, 2013)<br><br>This should be fixed when the latest patch is loaded. <br>The time outs for the hierarchy and summary grid fly overs are the same.(Diane Wozniak May 17, 2013) (Wozniak, Diane M. May 17, 2013).<br><br>After loading the latest patch, found the SDR is fixed.Thus closing the finding. (N, Thamaraiselvi May 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9723 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75700
30844 | FINDING | Primary controller goes into failed mode when backup controller comes into backup mode. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Controller: - OCR1100 G02<br>Drop: - Drop12/drop62<br>Ov: - OV 3.5.0 (Net#8)<br>Patch used: - OVA350018- 05152013111309<br>SFP Part no.: - FTLF1323P1BTR<br>Media Convertor: - EL100T-20<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1OFF<br>2ON<br>3OFF<br>4OFF<br>5OFF<br>6OFF<br><br>Step followed:-<br>1:- Initially both the controller are Power OFF.<br>2:- In Primary controller, unplugged the SFP from N2 Port . <br>3:- Power ON the controller &amp; Communication is established with the N3 port &amp; Controller is in control mode. In Status tab of Drop point (Drop12.unit0@FE350), Status of K0 is unavailable &amp; K1 is Unknown.<br>4:- In Backup controller, LC connector (Fiber cable) is not connected from the N3 port. <br>5:- Power ON the Controller.<br>6:- When Backup controller comes into backup mode, Primary controller goes into failed mode &amp; Backup controller comes into control mode.<br> Status tab of Drop point (Drop62.unit0@FE350), Status of K0 is Active &amp; K1 is unavailable.<br><br>Note:- Same issue is observed in OCR1100 G01 also. (Agarwal, Gaurav May 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed. Converted to SDR 19642 (Benzvi, Mati Jun 11, 2013) <br> |  | 35 | FINDING | 9724 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75702
30845 | FINDING | Link of the N3 port is not available in SSD Graphic 1800 if unplugged the SFP from N2 Port. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Controller: - OCR1100 G02<br>Drop: - Drop12/drop62<br>Ov: - OV 3.5.0 (Net#8)<br>Patch used: - OVA350018- 05152013111309<br>SFP Part no.: - FTLF1323P1BTR<br>Media Convertor: - EL100T-20<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1OFF<br>2ON<br>3OFF<br>4OFF<br>5OFF<br>6OFF<br>Step followed:-<br>1:- Initially both the controller are Power OFF.<br>2:- In Primary controller, unplugged the SFP from N2 Port . <br>3:- Power ON the controller &amp; Communication is established with the N3 port &amp; Controller is in control mode. In Status tab <br> of Drop point (Drop12.unit0@FE350), Status of K0 is unavailable &amp; K1 is Unknown.<br><br>In SSD Graphic 1800, Link of N2 port is red But Link of N3 port is not available.<br><br>For more information, please find the attached screen shot (Unknown Link .jpg). (Agarwal, Gaurav May 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed. Converted to SDR 19643 (Benzvi, Mati Jun 11, 2013) <br> |  | 35 | FINDING | 9725 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75704
30846 | FINDING | SDR19512 fails as: In OSV, Hierarchy Search, the Fly over for the device types is missing for FM,PM and DM. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | SDR19512 fails as: In OSV-&gt; Hierarchy Search-&gt; the Fly over for the device types is missing for FM,PM and DM. (Sachan, Pallavi May 17, 2013)<br><br>This should be fixed when the latest patch is loaded. (Diane Wozniak May 17, 2013) (Wozniak, Diane M. May 17, 2013)<br>---<br>msb - Please retest with OVA350-020-05142013113025 (Benzvi, Mati May 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | PS: Retested with OVA350-020-05142013113025 and found fixed. Hence Finding is Closed. (Sachan, Pallavi May 27, 2013) <br> |  | 35 | FINDING | 9726 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75706
30847 | FINDING | SDR19429 partially fails as in OSV, when viewing drop number sequence is not in numeric order. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | SDR19429 partially fails as in OSV, when viewing drop number sequence is not in numeric order.<br>The Q-Line -&gt; Crate -&gt; Slots are now seen in proper numeric oredr.<br>Whereas, <br>1&gt; Under Drop ID, the drop numbers are not in numeric order.<br>2&gt; Under Hierarchy search, the Drop number to be selected are also not in numeric order.<br>3&gt; In Search Results, the IOIC number, Branch Numbers are not in numeric order. (Sachan, Pallavi May 17, 2013)<br><br>Additional information:<br>1&gt; Under Drop ID, the drop numbers are not in numeric order.<br> Response: <br> on the drop summary grid : The drops are sorted on primary drop number. <br> The partners automatically follow but are indented.<br><br>2&gt; Under Hierarchy search, the Drop number to be selected are also not in numeric order.<br> Response: <br> the hierarchy search/drops tab: the drops are listed as primary[/partner]<br> where[/partner] is optional. The drops are <br> sorted on primary drop number.<br><br>3&gt; In Search Results, the IOIC number, Branch Numbers are not in numeric order. <br> Response: <br> I made no attempt to sort this list. <br> This is the result of an sql query that can vary and I had no idea what to sort on. (Wozniak, Diane M. May 17, 2013)<br>---<br>msb - Please retest with OVA350-020-05142013113025 (Benzvi, Mati May 20, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Retested with OVA350-020-05142013113025 and issues reported in Point &lt;1&gt; &amp; Point &lt;2&gt; found fixed. SDR Passed Validation. But Issue in Point &lt;3&gt; needs to be addressed. (Sachan, Pallavi May 27, 2013) <br> |  | 35 | FINDING | 9727 |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75708
30849 | FINDING | SDR#19588 "Downloading a Fieldbus port crashes studio" fails. | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 6 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Following steps are performed to test SDR#19588.<br><br>1. Patch OVA350017 has been loaded in DBS &amp; all EWS in Ov3.5.<br>2. Field bus module has been configured at 1.2.1 in drop32/82<br>3. As per affected area of of this SDR automatically updating statistics <br> (15 Second interval) window is opened on multiple operator stations (e.g drop247,<br> drop251 &amp; drop237) of port2.<br>4. Now tried downloading the port2 on DBS (drop250) then download failed.<br> (Please refer attached snapshot SDR#19588_Error-DBS.jpg) &amp; in all EWS (where statistics <br> window is opened) lock violation error appeared ( Please refer attached snspshot <br> SDR#19588_Error-1-EWS.jpg) &amp; pressing the OK button error appeared &quot;Hse is not <br> communicating&quot; ( Please refer attached snspshot SDR#19588_Error-2-EWS.jpg). (Sahay, Madhukar May 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1. The first image shows a valid response to a busy port.<br>2. The second image could show a transient error resulting from activity. If the error is acknowldeged does the statistic window update properly at the next automatic interval? If it does, this works as designed.<br>3. Please send me the complete error message. (Hutchison, Steven B. May 21, 2013)<br><br>MS : I performed steps many times &amp; following are observation :-<br> 2. Statistic window updtae properly if error is acknowledged when Port download failed<br> meesage not appeared on DBS.<br> 3. Port download failed error message appeared approx 2 out of 5 time &amp; when this occur<br> Developer&quot;s studio crashed on EWS (After acknowledgement of transient error appeared on <br> EWS). Please refer attached snahsot SDR#19588 Error1_DBS.jpg &amp; Studio Crashed on EWS.jpg.<br> Further it is noticed for successfull port download ff module needs reboot. (Sahay, Madhukar May 22, 2013)<br><br>Please provide loging information. - (Hutchison, Steven B. May 22, 2013)<br><br>Loging information has been attached. (Sahay, Madhukar May 24, 2013) <br> It was found that Developer Studio would crash on any Ovation Station that has the Fieldbus Port Statistics Window open and on an automatic refresh every 15 seconds, if a Port Download operation was performed from a different Ovation Station for the associated port.<br><br>This finding will be converted to an SDR. (Morris, Gilbert L. Jun 13, 2013) |  | 35 | FINDING | 9729 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75712
30851 | FINDING | Quality info is not showing if user wants to filter Good Quality points in Historical Review. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | If user selects &quot;Fair&quot;,&quot;Poor&quot;,&quot;Bad&quot;,&quot;Timed out&quot; quality points to Filter in Historical Review then info is properly updating under Quality Tab. Whereras for &quot;Good&quot; filter selection info is not showing under &quot;Quality&quot; for searched points.<br><br>Please see the attached snapshot for your reference. (Kumar, Sudheer May 21, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | In Ovation a G is usually not shown for Good quality. You can see the GQ in the Point Status columen at the right to see that it matched the search for Good Quality (McMaster, James May 21, 2013) <br> |  | 35 | FINDING | 9731 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75716
30852 | FINDING | Discrepency of displaying drop hiererchy with the Studio details. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Observed the the Discrepency of displaying drop hiererchy between the System viewer &amp; the drop hiererchy in the Developer studio. <br>For e.g.1.Drop#151 configured as controller in the Studio is missing in the drop hiererchy of System viewer. Observed this behaviour in both the networks of net 7 &amp; net8. <br>2.aditional drop which is not configured in the studio is displayed in the drop hiererchy of System viewer.This behaviour is observed in net#8 only. Please find the snapshots for the reference. (N, Thamaraiselvi May 21, 2013)<br><br><br><br>This is an interesting observation that requires a detailed response.<br>The systemviewer reads in xml files that describe each drop. These files are<br>located under Ovation\mmi\systemviewer. Each drop will have a dropxx-attribute.xml and<br>dropxx-hierarchy.xml. there is an optional dropxx-packedchannels.xml file. If these files are<br>missing for a particular drop, the systemviewer has nothing to display. The question then<br>becomes why there is no files for that drop. So as a first step, we need to check if these files<br>are present. (Wozniak, Diane M. May 21, 2013)<br>Note:<br>1. The controller files are created when a drop load occurs.<br>2. The partner drop does not have its own xml files. The partner information is inside the primary drop&quot;s xml files. (Wozniak, Diane M. May 21, 2013)<br><br>Thanks Diana for the information. You are correct. <br>I observed the missing as well as aditional drop info in the path you have given &amp; noticed that those drop files are missing for the missing drop &amp; aditional drop files are also there. <br>Please find attached the snapshots for the same. (N, Thamaraiselvi May 22, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please note that any deleted drops are removed from the ovation\mmi\systemviewer directory once any drop is loaded. Today I did not see &quot;extra&quot; drop in this directory. I am assuming that a load had occured.<br><br>Can you give me login instructions so I can see the drops listed above that are in error. <br><br>I logged into 10.132.153.96 today and did not see any discrepencies.<br>From there I logged into 192.168.12.176. The discrepencies I saw today were with drops that could not be loaded. <br><br>These are the instuctions I used to get to 10.132.153.96 and 192.168.12.176.<br>Login to Ovation gateway drop#250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9.<br>From drom drop250, remote log-in #176.<br>Please find the Remote log -in details.<br>Login to Ovation gateway drop176 with the following credentials<br>Ip address for remote login drop176: 192.168.12.176<br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9. (Wozniak, Diane M. May 22, 2013).<br><br>Thanks once again for the info.<br>With your guidance,I have understood that the drops which are loaded are displayed in the System viewer. So I found the aditional drops in the studiowere dummy, deleted, &amp; refreshed it. At present the discrepency of missing drops between the studio &amp; system viewer is clear in both the nets.. I am just wondering about 2nd point of aditional drop#99 in the net#8 DBS drop176. In the Studio again I found the drop#3 was dummy, &amp; deleted. But still in the SYStem viewer files in the C path &amp; the application reflects the drop. I just wonder from where it takes?<br><br>Please remote log-in drop#176 through gateway drop#250 with the previous steps. (N, Thamaraiselvi May 23, 2013).<br>Found there is no issue. Thus closing the finding. (N, Thamaraiselvi Nov 22, 2013) <br> |  | 35 | FINDING | 9732 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75718
30855 | FINDING | Historical edit/annotate feature showing incorrect date and timestamp when openend in OV 3.5.0 | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Steps to recreate:-<br>Historical review:-<br>1) Open historical review and browse a point. Set a time period (eg. 1hr)<br>2) Now right click on any point and open history edit/annotate<br>Observation: The date and time stamp range in history edit tool is different from that in historical review .<br><br>Trend:-<br>1) open trend and browse a point . Set a time period (eg. 1hr)<br>2) Now right click on any point and open history edit/annotate <br>Observation: The date and time stamp in history edit tool is different from that in historical review .When default time zone is &quot;Local&quot; it shows +5:20 hrs , whereas , when default time zone is &quot;GMT&quot; it shows correct time but shows no data in either time zone.<br><br>The same steps when done in OPH 3.5.0 with OV 3.3.1 and OV 3.1.3 shows synchronized time with historical review and trend.Please find the remote login details of drop 230 attached. (Kakroo, Tanisha May 21, 2013) |  |  |  | Retest. This issue has been fixed via SDR 19845. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is actually an issue with OVATION 3.5.0 Historical Review and Trend.<br><br>I am changing the product information accordingly for this finding (OPH 3.5.0 -&gt; OVATION 3.5.0).<br><br>The fix will be made available in OVATION 3.5.1. (Bargaje Prashant Jun 27, 2013) <br> This issue has been fixed via SDR 19845. (Bargaje Prashant Apr 20, 2015) |  | 35 | FINDING | 9735 |  | FINDING | Contento, James AUTOSOL PWS PITT | Kakroo, Tanisha EMR SYSS PWS NOIDA | Matreja, Shyam EMR SYSS PWS PITT | [7 empty] | Implementation | 3.5.1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75724
30856 | FINDING | The Popup window name shows up in lower case. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 | [7 empty] | USPITTFSService | 2015-06-12 04:06 |  | The Popup window the name shows up in lower case once called through a graphics. (Singh, Ghanshyam May 21, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Graphics (GR)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Singh, Ghanshyam</p> <p><strong>Responsible:</strong> Spillane, Donal A.</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Singh, Ghanshyam</p> <p><strong>Entry Date:</strong> 2013-05-21T07:03:11-04:00</p> <p><strong>Modified Date:</strong> 2013-05-23T07:06:41-04:00</p> | 0 |  | Ovation for Windows/General/Software | Can you give me the exact patches loaded on this drop. (Spillane, Donal A. May 21, 2013)<br>Also, what system variable are you using to verify the case of the window file name. (Spillane, Donal A. May 21, 2013)<br><br>GS:Installed patches are OVA350002,OVA350003,OVA350004,OVA350006,OVA350007,OVA350008,OVA350009,<br>OVA350010,OVA350012,OVA350013,OVA350015,OVA350017and OVA350020.Issue was expected to get resolved in Patch OVA350020 .We have graphics [GS_TEST_OL.diag] as main graphics. In the main graphics [pop up link] is the name of poke which calls the popup [GS_350_WIN_GB_2.diag].<br>Remote login details [Remote_Login_Details_drop174]is attached with finding. (Singh, Ghanshyam May 22, 2013) <br> I have looked at the diagrams you created and I am not able to understand the test you are performing. <br>Diagram GS_TEST_OL is a main diagram which has a poke to display GS_350_WIN_GB which is also a main diagram not a window. <br><br>The problem resolved in SDR 19545 addresses the storing of the Window Name in the system variable location &quot;S:diagram_name&quot;. Users can access this variable and do a check comparing it to a certain name, for example, the user may have an IF statement IF(S:diagram_name = &quot;GS_350_WIN_GB_2&quot;). This statement would fail if the variable S:diagram_name was stored in lower case. The fix was to always store the diagram name in uppercase.<br><br>I hope this explains a little better what the problem is. (Spillane, Donal A. May 22, 2013)<br><br>GS:I am not able to recreate the issue as you said. Please provide me sample graphics. (Singh, Ghanshyam May 23, 2013) |  | 35 | FINDING | 9736 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Singh, Ghanshyam EMR SYSS PWS LEIC | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Singh, Ghanshyam EMR SYSS PWS LEIC | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75725
30861 | FINDING | Simcommand.exe not starting on Virtual Controller Host machines. | Brown, Rick P EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | After installing patch OVA350021, the simcommand process is not starting on Ovation stations configured as Virtual Controller Hosts. (Perdeus, Matthew May 22, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Added virtual controller host to the startup task. Issue was due to an inconsistancy in the functional spec. Patch has been updated. (Brown, Richard P. May 23, 2013)<br><br>OK in updated OVA350021. (Perdeus, Matthew May 28, 2013)<br><br>Backed out the previous change as SIMCommand conflicts with vcoordinator. Functional spec needs updated for consistancy. (Brown, Richard P. May 31, 2013) <br> |  | 35 | FINDING | 9741 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | [9 empty] | Implementation | OVA350021 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75735
30863 | FINDING | Trend Tab disappears when mouse clicks away from the application | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Ovation Trend Application --When user takes a main trend tab and moves it to its own location (disconnected from the trend application), then clicks an empty space on the desktop (loss of focus), the application window is still there, but the trend tab removed from the application disappears. When you click back on the trend application it reappears, but then it will disappear if one mouse clicks away from the application. (Kumar, Sudheer May 23, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This looks like almost the exact same words that are in SDR 19490 which was fixed in OVA350020. Are you trying to say that you are failing the fix we made in patch 20? If so, I would like you to retry because I was able to go to a W7 and 2008 machine in Validation lab and SDR 19490 works as expected now (McMaster, James May 23, 2013) <br> |  | 35 | FINDING | 9743 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350020 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75739
30867 | FINDING | "Load Filter" error in PI application of Ovation3.5.0 | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | &quot;Load Filter&quot; Tab gives error when we try to load the newly saved filter configurations. <br>Please follow the steps to recreate the issue:<br>Open PI &quot;-&gt; Click on Browse Point --&gt; Set filters &quot;Save it &quot;-&gt; Saved filter configuration will now appear in &quot;Load filter tab&quot; at upper left corner of PI window (Refer to snapshot-1)&quot;-&gt; Click on currently saved filter listed in Load Filter Tab -&quot;&gt; Error popup will come (Refer to snapshot-2) &quot;-&gt; after acknowledging massage configuration gets disappeared from &quot;Load Filter&quot; drop down. &quot;-&gt; Same filter configuration does exist in &quot;Load Filter Template&quot; Window. (Refer to snapshot-3)<br>Also Deleted Filter configurations do not lilisted from &quot;Load Filter&quot; Tab automatically. It goes after clicking on it followed by an error massage. (Jain, Yukta May 23, 2013) (Burgoon, Frank J. May 23, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | These behaviors are what were reported in SDRs 19591 and 19592. These two SDRs were addressed in patch OVA350020. (Burgoon, Frank J. May 23, 2013)<br><br>YJ: Issue reported as SDR 19592 found fixed. Above mentioned issue is observed after patch 350020. In which we are unable to load latest saved filter. <br>Should i close the finding? Please suggest. (Jain, Yukta May 23, 2013) <br> I was able to reproduce your complaint. We will correct this for 3.5.1. Close this finding and submit and SDR. (Burgoon, Frank J. May 23, 2013)<br>---<br>msb - Closed. Converted to SDR 19619 (Benzvi, Mati May 28, 2013) |  | 35 | FINDING | 9747 |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75747
30870 | FINDING | OCR400 having a large number of points often gets stuck in Startup Mode. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | G02 OCR400 Controller 44/94 (EMILY) was previously operating as expected with 1,048 points. 30,000 points were added to the controller in order to test OVA350018/SDR19474.<br><br>The controllers appear to operate normally after being loaded with the new number of points, but will often report the following during startup following a reboot:<br>Local Memory Manager : Error allocating local memory : Fail to get VN number (0xfffffff3)<br>Error in initializing local memory, Controller functionality unavailable<br><br>This problem usually occurs in the controller expected to go into Backup, but it has happened to both controllers at the same time.<br><br>The problem was not observed when the point count in the controller was lowered to 26,000.<br><br>The problem was also observed when OVA350018 was temporarily removed.<br><br>Mark Zaremsky has been investigating the issue. (Brown, Sean May 23, 2013) |  |  |  | This should be resolved by the sid/lib (aka gni3_sync) patch contained in OVA350036. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | msb - Closed as SDR 19895 (Benzvi, Mati Oct 7, 2013) <br> |  | 35 | FINDING | 9750 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75753
30882 | FINDING | OVA350018/SDR19474: OPP error still occurs following clear-load-reboot. | Zaremsky, Mark External MZCI | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 | [7 empty] | USPITTFSService | 2015-06-12 04:06 |  | G02 OCR400 Controller 44/94 (EMILY) is configured with 20,000 points in order to test SDR 19474. When the recommended test actions are performed the controller goes to Failed Mode (instead of Backup).<br><br>The following error messages were observed:<br>&lt;129&gt; Controller Error : OPP Subsystem Error : OPP System Error - Fatal : 0x8 : 0x38001a : 0x0 : 0x0<br>&lt;129&gt; Controller Error : OPP error reading or writing flash<br><br>The following error messages were reported when the controller was rebooted:<br>&lt;129&gt; Controller Error : OPP Subsystem Error : OPP System Error - Fatal : 0x12 : 0xffffffff : 0x1 : 0x0<br>&lt;129&gt; Controller Error : OPP couldn&quot;t get pointers to 0x1 dynamic and static data (Brown, Sean May 29, 2013) |  |  |  | Please retest after installing OVA350036. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9762 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Need More Information to Duplicate | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75777
30893 | FINDING | About displays old version regarding Ovation Session Manager. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | In Ovation 3.5.0 Session Manager Options, About displays &quot;3.4.0&quot;. It should display &quot;3.5.0&quot;.<br>Please find the attached JPEG file &quot;OSM_350&quot; for reference. (Mitra, Sambuddha Jun 5, 2013)<br><br>Verified in Ovation 3.5.1_U0. This is corrected. So, closing the finding. (Mitra, Sambuddha Aug 28, 2013) | None |  |  | Examine data and verify. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Changed for Ovation 3.5.1. (Burgoon, Frank J. Jun 5, 2013) <br> |  | 35 | FINDING | 9773 |  | FINDING | [10 empty] | Implementation | 3.5.1_U0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75799
30894 | FINDING | Mouse hover does not display correct description at Ovation Alarm System. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | In Ovation 3.5.0 Alarm System at Value section, mouse hover at Test Mode ON displays &quot;Set Test Mode Off&quot;. Please find the attached JPEG file &quot;OAS1&quot; for reference. (Mitra, Sambuddha Jun 5, 2013)<br><br>Verified in Ovation 3.5.1_U0. This is corrected. So, closing the finding. (Mitra, Sambuddha Aug 29, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The header for the tooltip will be fixed. It will be changed to &quot;Set Test Mode On&quot; and released in Ovation 3.5.1. (Augustine, Lisa Jun 5, 2013) <br> |  | 35 | FINDING | 9774 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75801
30896 | FINDING | No description shows if mouse hover on Memorize. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | In Ovation Historical Reviews--&gt; Home--&gt; Time Span, mouse hover at Memorize does not show any description. Please find the attached JPEG file &quot;OHR1&quot; for reference. (Mitra, Sambuddha Jun 5, 2013)<br><br>The problem is resolved in Ovation 3.5.1. So, closed the finding. (Mitra, Sambuddha May 22, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9776 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75804
30897 | FINDING | No description displays when mouse hover at Network/Unit. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | In Ovation Historical Reviews--&gt; Filter--&gt; System, mouse hover at Network/Unit does not display any description. Please find the attached JPEG file &quot;OHR2&quot; for reference. (Mitra, Sambuddha Jun 5, 2013)<br><br>Verified this in Ovation 3.5.0 and it is corrected now. So, closing the finding. (Mitra, Sambuddha Nov 6, 2013) (Mitra, Sambuddha Nov 6, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9777 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75806
30959 | FINDING | Unable to open help for point groups | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Unable to open help for point groups. Please find the snapshot attached. (Kakroo, Tanisha Jun 17, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 08/16/2013: No plans to fix. Based on the screen capture attached to this Finding, it shows accessing point groups for an eDB which is a product that is no longer supported. Also, eDB information was in a separate manual. For the upcoming release of Ovation (3.5.1), we cannot add eDB information to the Developer Studio manual because it would not be relevent. (Casteel, Linda Aug 16, 2013) <br> |  | 35 | FINDING | 9839 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kakroo, Tanisha EMR SYSS PWS NOIDA | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75931
30975 | FINDING | Template.tft and RAMPGEN symbol are not loaded with patch 022 on EWS drops. | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | After loading the patch OVA350022 in DBS, it is observed that Template.tft and RAMPGEN symbol are not loaded with patch 022 on EWS drops.<br>As per the developer&quot;s mail, followed the procedures after installing the patch, but the .<br>Template.tft and RAMPGEN symbol are not loaded on EWS drops. (N, Thamaraiselvi Jun 20, 2013)<br><br>Observed the issue is solved in 3.5.1_U1.<br>Template.tft and RAMPGEN symbol are loaded with 3.5.1_u1 on EWS drops.<br>Tested the algo &amp; passed the SDR also. Hence closing the finding. (N, Thamaraiselvi Sep 24, 2013) (N, Thamaraiselvi Sep 24, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 9855 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | 3.5.1_U1 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 75963
30976 | FINDING | The help file of the RAMPGEN algorithm directs to transfer Algorithm wrongly. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-09 03:47 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-09 03:47 | 65849 |  |  | 2017-05-09 03:47 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | After loading the patch OVA350022, the RAMPGEN algorithm is seen listed in the symbols. But by clicking &amp; right click with help directs to transfer Algorithm wrongly. (N, Thamaraiselvi Jun 20, 2013) | <p>AA 12/01/2015: The particular finding was fixed by Linda. </p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">AA 12/04/2015: Reassigning the algorithm to&nbsp;Linda as she is assigned the algorithms manual for 3.6 release.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  | <p>LC 11/22/2013: Check the RAMPGEN algorithm in the 3.5.1 Ovation Algorithm Reference manual - print and online help.</p><p>AA 12/01/2015: The issue related to the RAMPGEN algorithm has been resolved by Linda. The same will be visible in the latest online help.</p><p><br></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">AA 12/04/2015: Reassigning the algorithm to&nbsp;Linda as she is assigned the algorithms manual for 3.6 release.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>LC 06/20/2013: RAMPGEN will be included in the Ovation 3.5.1 print and online documentation. (Casteel, Linda Jun 20, 2013)<br><br>LC 11/22/2013: RAMPGEN algorithm is now part of the Ovation 3.5.1 print and online documentation. This fix will be available in the Ovation 3.5.1 U4 build and in OW351_R1100.pdf on Q:\Communication\Tech\Comm\Share\Validation. (Casteel, Linda Nov 22, 2013) (Casteel, Linda Dec 10, 2013) <br></p><p><br></p><p>AA 12/01/2015: The issue related to the&nbsp;RAMPGEN algorithm has been resolved by Linda.&nbsp; The latest updated manual is kept at: Q:\Communication\TechComm\Share\Abhinav_Ovation 3.6.0 manuals\Ovation Algorithms Reference Manual (OW360_R1100). This is visible in 3.6.0_U1 build.</p><p>TN:05/09/17 : Verified the issue is fixed in 3.6.0. Thus closing the finding.</p> |  | 35 | FINDING | 9856 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Casteel, Linda EMR SYSS PWS PITT | Bush, Kirt T EMR SYSS PWS PITT | [7 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>LC 11/22/2013: Added the new RAMPGEN algorithm to the Ovation 3.5.1 Algorithm Reference Manual.</p><p><br></p><p>AA 12/01/2015: The issue related to the RAMPGEN algorithm has been resolved by Linda. </p><p><br></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">AA 12/04/2015: Reassigning the algorithm to&nbsp;Linda as she is assigned the algorithms manual for 3.6 release.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">LC 01/29/2016: <font color="#000000">Added the new RAMPGEN algorithm to the Ovation 3.6.0 Algorithm Reference Manual. Check online help and V:\Tests\3.6.0\DOCS_for_Validation</font></font></span></p><p><font face="Times New Roman" size=3> <br></font></p> | 9 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation | n/a |  |  | FINDING | [6 empty] | 112432
31029 | FINDING | MMI config---&gtDisplay fully qualified point name, false option not working properly. | Contento, James AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | While testing SDR 19048 on Ov3.5.0 + OPH drop observation was :<br>Under MMI configuration if [Display fully qualified point name] is false, then following erratic behaiour is observed:<br>1)In Trend if browse point is done and Data Source selection is Historian , fully qualified point name is displayed( refer attched display_unqualified_History.jpg).<br><br>2)In Trend if browse point is done and Data Source selection is Ovation Point Directory , fully qualified point name is displayed if network selection is not local.<br><br>3)In Trend if browse point is done, Data Source selection is Ovation Point Directory then for point which exists in database and is not online, Point name is not displayed instead SID is displayed(refer attached browse point_off highway.jpg)<br><br>Above problem is seen on Non OPH ovation drop also.<br>Remote login steps for Drop237 where this is done is attached. (Kumar, Shailendra Jul 9, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | 1) Since OPHs can connect to multiple networks it really needs to show fully qualified<br>2) A user wouldn&quot;t set to not display if they had multiple networks so this is fine<br>3) This has nothing to do with fully qualified configuration. If for some reason it cannot obtain the Point Name it will display SID (McMaster, James Jul 9, 2013) <br> |  | 35 | FINDING | 9909 |  | FINDING | Bargaje, Prashant C EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76065
31030 | FINDING | Live trend is slow for duration greater than 100 minutes. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | On drop250(DBS,server2008 R2) Live trend is done for 10 minutes for 3 points , then browsed few point and added it in already running trend, changed duration to 24 now trend shows &quot;bacfilling data from historian &quot; and after this for about 2 minutes could not see the cuurent value of newly added point(refer attached snapshot). (Kumar, Shailendra Jul 9, 2013)<br>Live update selection is of 2 seconds. (Kumar, Shailendra Jul 9, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | For a 24 hour trend there are 600 samples, one every 2.4 minutes. Depending on when the request is made you may wait up to 2.4 minutes to get the first sample. I have to assume that the points in question are not collected in the OPH or the data would have backfilled. This is how trend and trend collect have always worked, you would have seen this on pre3.5 trend also (McMaster, James Jul 9, 2013) <br> |  | 35 | FINDING | 9910 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76067
31031 | FINDING | OCR400/1100 controller will fail is 5 of more SOE points are defined for GE MARK VI Third Party driver. | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | While testing SRF 18822 added I/O Device GE Mark VI and defined I/O Driver Type GE Mark VI in the Developer Studio.In OCR400 controller added SOE point and in its Hardwatre tab defined I/O Type:Third Party, I/O Module:GE MARK VI. Performed Download/Clear/Load of the controller. It was observed that the controller can be loaded successfully only if number of SOE points so defined is less than 5. For 5 or more SOE points controller will fail.<br>The problem was duplicated in OCR1100 controller as well. (Lal, Ramesh Jul 10, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This can be reproduced. When the drop is loaded a page fault occurs but the page fault is not caused by the GE driver This may be related to another problem with the GE driver that was caused by a 16 bit point being used for the hardware (HD) field instead of a 32 bit pointer.<br><br><br>Page Fault<br>Page Dir Base : 0x0067a000<br>Esp0 0x020d85d0 : 0xffffffff, 0x00536788, 0x020d8604, 0xeeeeeeee<br>Esp0 0x020d85e0 : 0x00fcfc58, 0x01412740, 0x0144faa0, 0xeeeeeeee<br>Program Counter : 0x00fd5986<br>Code Selector : 0x00000008<br>Eflags Register : 0x00010246<br>Error Code : 0x00000000<br>Page Fault Addr : 0x000000c2<br>Task: 0x20d88c0 &quot;CTTask#1&quot;<br>0x20d88c0 (CTTask#1): task 0x20d88c0 has had a failure and has been stopped.<br>0x20d88c0 (CTTask#1): fatal kernel task-level exception!<br><br>Page Fault<br>Page Dir Base : 0x0067a000<br>Esp0 0x020d85d0 : 0xffffffff, 0x00536788, 0x020d8604, 0xeeeeeeee<br>Esp0 0x020d85e0 : 0x00fcfc58, 0x01412740, 0x0144faa0, 0xeeeeeeee<br>Program Counter : 0x00fd5986<br>Code Selector : 0x00000008<br>Eflags Register : 0x00010246<br>Error Code : 0x00000000<br>Page Fault Addr : 0x000000c2<br>Task: 0x2104fc0 &quot;DPU Monitor&quot; (Ritchie Mark A. Dec 6, 2013) <br> This is the same problem that was reported in SDR 19975 and SDR 19992.<br>The problem exists in the SOE library and not the GE driver and should be tracked by SDR 19992. (Ritchie Mark A. Dec 6, 2013) |  | 35 | FINDING | 9911 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | USPITTFSService | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76069
31038 | FINDING | OVA Patches (350 & 331) built in July do not delete all files when Patch is removed | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | OVA Patches (350 &amp; 331) built in July do not delete all files when Patch is removed.<br>Upon removal of patches the following directories and the backup files remain on the client computer:<br>32b: C:\Program Files\Emerson Process Management\OVA331XXX<br> C:\Program Files\Emerson Process Management\OVA331XXX\_backup<br>---<br>64b: C:\Program Files (x86)\Emerson Process Management\OVA350XXX<br> C:\Program Files (x86)\Emerson Process Management\OVA350XXX\_backup (Benzvi, Mati Jul 15, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed 3.3.1 : OVA331-121,122,164,174,176<br>3.5.0 : OVA350-023,024,025 (Matreja Shyam Jul 16, 2013)<br>---<br>msb - Ok with all rebuilt OVA331 &amp; OVA350 patches @ 22-Jul-2013 (Benzvi, Mati Aug 6, 2013) <br> |  | 35 | FINDING | 9918 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | OVA |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76083
31039 | FINDING | postremove.vbs files is not found error when patch 006 is removed | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | When Patch OVA350-006 is removed, a popup error is displayed:<br> Script: postremove.vbs<br> Error: File not found (Benzvi, Mati Jul 16, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: Fixed the postremove.vbs and rebuild the patch again. So now next monthly update will take this fix. (Matreja Shyam Jul 16, 2013)<br>---<br>msb - Ok in OVA350 Aug13 Update @ 30-Aug-2013 (Benzvi, Mati Sep 8, 2013) <br> |  | 35 | FINDING | 9919 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | OVA350-Aug13 Update |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76085
31107 | FINDING | Patch OVA350-025 can not be installed on Base Station | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Patch OVA350-025 can not be installed on a Base Station<br>Error:<br> OVA350025 - InstallShield Wizard<br> ======================================================================<br> Patch dependency validation Failure. Following patches are required to<br> be installed before installing this patch<br> OVA350017<br> ====================================================================== (Benzvi, Mati Aug 2, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Can we close this now?<br>- (Hutchison, Steven B. Aug 30, 2013)<br>---<br>msb - OK in OVA350-Aug13 Update @ 30-Aug-2013 (Benzvi, Mati Sep 8, 2013) <br> |  | 35 | FINDING | 9987 |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Matreja, Shyam EMR SYSS PWS PITT | [8 empty] | Implementation | OVA350-Aug13 Update |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76219
31112 | FINDING | PWTTS - Developer Studio crashed when adding new place holder for RA 1066 CT FF device | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Install new DD (Device Description) for Rosemount Analytical 1066 CT Rev 1 via AMS completed successful.<br>However, when try to add new place holder for this device on FF port, Ovation DS crashed and complain about run time error. (see attached screenshot for detail)<br><br>Steps to reproduce:<br>On AMS Server Plus station, install new DD for FF 1066 CT Rev 1. (see attached for DD package)<br>Once completed, go to DS and add a place holder under a FF port<br>DS will crash when Rev 1 is selected in Revision field. (Phan, Quang Aug 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The problem appears to be the support of a new type of Fieldbus alarm. In the XML file used by Ovation, if the following block of code is commented out, the insert works just fine.<br><br> &lt;device_alarm name=&quot;CHKFNC_ALM&quot;&gt;<br> &lt;fd_alm_index&gt;1058&lt;/fd_alm_index&gt;<br> &lt;fd_pri_index&gt;1062&lt;/fd_pri_index&gt;<br> &lt;fd_active_index&gt;1046&lt;/fd_active_index&gt;<br> &lt;fd_map_index&gt;1050&lt;/fd_map_index&gt;<br> &lt;fd_mask_index&gt;1054&lt;/fd_mask_index&gt;<br> &lt;priority_default&gt;LOG&lt;/priority_default&gt;<br> &lt;/device_alarm&gt;<br><br>Please convert this to an SDR (Morris, Gilbert L. Sep 27, 2013) <br> It appears that newer device install kits are being compiled and published containing a Fieldbus Alarm that Ovation currently doesn&quot;t support. This alarm is shown in the description above (&quot;CHKFNC_ALM&quot;). When an insert new operation is performed, for devices that support this new alarm, the software responsible for updating the object with all relevant information will simply ignore this particular alarm.<br><br>This will also be backfitted into a future Ovation 3.5.0 patch. (Morris, Gilbert L. Oct 3, 2013)<br><br>IC 10/17/13 - closed finding, track as SDR 19879. (Capani, Nooch Oct 17, 2013) |  | 35 | FINDING | 9992 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | SDR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76228
31113 | FINDING | PWTTS - FF device 3144 Rev 2 keep flashing back and forward between GOOD and NO_COMM | Wood, Thomas T AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Rosemount Temperature device 3144 Rev 2 when commission on FF segment, its status on Alarm system keep flashing between GOOD and NO_COMM constantly. <br>There are 2 AI function blocks from this device configure on control sheet and they both show good status and correct reading. (see screenshot for detail)<br><br>DD package for this device is available if needed. Or, system with this device commission is available to remote in for troubleshoot purpose. (Phan, Quang Aug 6, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Tom - Please work with Quang to resolve this issue. (Costlow, Kimberly A. Aug 8, 2013)<br>After overnight soak test doing port download (144 performed every 5 minutes),<br>alarm cleared out. Close as one time incident and can&quot;t reproduce. (Phan, Quang Aug 15, 2013) <br> |  | 35 | FINDING | 9993 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Plymire, Alvan AUTOSOL PWS PITT | [7 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76230
31123 | FINDING | Point review throws exception error in column tab. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Steps to recreate: Open the Point Review. Select the filter menu. Click the select the column in the Column tab. Exception error displays. Observed the same in DBS &amp; EWS drops of both net#7 &amp; net#8. Please find enclosed the snapshot &amp; the notepad details. (N, Thamaraiselvi Aug 8, 2013) | none |  |  | Point Review column chooser functionality will now work correctly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please list the Ovation patches that have been applied to the workstations. (Burgoon, Frank J. Aug 8, 2013).<br><br>Please find the list of patches installed in drop#250, where I recreated the finding again.<br>OVA350002,OVA350003,OVA350004,OVA350006,OVA350007,OVA350008,OVA350009,OVA350010,OVA350012,OVA350013,OVA350014,OVA350015,OVA350016,OVA350017,OVA350018,OVA350020,OVA350021,OVA350022,OVA350023 &amp; OVA350025.<br><br>Please find the Remote log in details.<br>Step<br>Login to Ovation gateway drop250 with the following credentials<br>Ip address for remote login from Pgh: 10.132.153.96 <br>Username : administrator <br>Password : Welcome@1234 <br>Domain : Val9Dc9 (N, Thamaraiselvi Aug 9, 2013)<br>Found the finding is fixed. Thus closing the finding. (N, Thamaraiselvi Nov 22, 2013) <br> |  | 35 | FINDING | 10003 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | 3.5.1_U0 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | ReviewableProperty was added to DU records in OvPointDirObjects.dll incorrectly. When adding a ReviewableProperty a new string must be added in strings.resx. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76248
31128 | FINDING | PWTTS - NO_COMM alert from DVC6000 device present while it"s function as expected else where | Wood, Thomas T AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | DVC6000 Rev 1 was commission successful in DS. Function block configured and working in Signal Diagram. However, in Alarm System, there is an alert that show device with NO_COMM.<br>Controllers status on Graphic 1800 shows there is no alert in controllers.<br><br>Perform the following but was unable to clear this alert:<br>- Download FF Port (see attached Hyper Terminal capture)<br>- Download/Clear/Load both controllers<br><br>Not sure how to reproduce this issue. (Phan, Quang Aug 8, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Tom - Please work with Quang to resolve this issue. (Costlow, Kimberly A. Aug 8, 2013)<br>After overnight soak test doing port download (144 performed every 5 minutes), alarm cleared out. Close as not reproducible. (Phan, Quang Aug 15, 2013) <br> |  | 35 | FINDING | 10008 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Plymire, Alvan AUTOSOL PWS PITT | [7 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76258
31145 | FINDING | Configuring SOE points on channels higher than 16 may not work properly. | Swartz, Mark EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 | [7 empty] | USPITTFSService | 2015-06-12 04:06 |  | During testing of SDR 19688 in Patch 25, it was seen that configuring a point for SOE one shot enable on channel 17, even with channel 17 configured for event reporting on the module, consistency check would report that the channel was not configured. Channel 1 was not configured for event reporting. Enabling channel 1 for reporting, allowed channel 17 to pass. The issue may exist on other channels above 16 also. (Perdeus, Matthew Aug 20, 2013) |  |  |  | The affected area is in the SOE Module Consistency Check. The software will now retrieve both Event Enable attributes from the SOE module, and use the proper attribute based on the digital point&quot;s channel value. No new test recommendations -- original tests should be sufficient. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This particular consistency check is only retrieving the Event Enable attribute applicable to the first 16 channels. Note that the issue also exists for the other channels 18-32 (the check only looks at the Event Enable attribute applicable to the first 16 channels).<br><br>The check will be changed to also retrieve the Event Enable attribute applicablle to channels 17 through 32 -- and use that value for channel checks between 17 and 32. (Swartz, Mark E. Aug 20, 2013) <br> |  | 35 | FINDING | 10025 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | [9 empty] | Implementation | OVA350025, 3.5.1_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76291
31151 | FINDING | SDR 19787 fails partially for conditional erase color. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | While testing the SDR #19787 in 2 different drops, followed the procedures in the affected area &amp; after loading the patch, &amp; verified the SDR has been passed for conditional background color &amp; fails for conditional erase color. Tested the SDR in Ov 3.3.1 &amp; verified the same.<br>Mailed the observations to Mati &amp; developer. (N, Thamaraiselvi Aug 23, 2013).<br><br>After the clarification mail from the developer, when I used the standard other colors than the new added color, I observed the SDR fixed the issue. Thus with the patch OVA350027, the issue is solved &amp; thus closing the finding. (N, Thamaraiselvi Aug 27, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10031 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76303
31161 | FINDING | TR "3.5_SRF1361_SVTP_rev1.0.doc" needs some modification. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 | [7 empty] | USPITTFSService | 2015-06-12 04:06 |  | (a). In test case 5.4.6 for note 3 it is mentioned to refer case 4 , however text step4<br> should be replaced with text step6.<br> <br>(b). In test case 5.4.8 note 3 it is mentioned to refer case 6 , however text step 7<br> should be replaced with text step6. (Sahay, Madhukar Aug 29, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> SW Val Test Procedure (SVTP)</p> <p><strong>Subproduct:</strong> Basic Functions (BF)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Sahay, Madhukar</p> <p><strong>Responsible:</strong> Capani, Nooch</p> <p><strong>Notify List:</strong> Capani, Nooch Sahay, Madhukar</p> <p><strong>Entry Date:</strong> 2013-08-29T01:34:38-04:00</p> <p><strong>Modified Date:</strong> 2013-08-29T01:34:38-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10041 |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76321
31247 | FINDING | Status Indicator of active input for MEDIAN SELECT Algorithm is not showing properly. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | When input switches from &quot;XA&quot; to &quot;XC&quot; or &quot;XB&quot; to &quot;XC&quot; for appropriate output. The status indicator doesn&quot;t jump on &quot;XC&quot; input.<br>Please find attached snapshot for reference. (Baghel, LekhrajSingh Sep 20, 2013) |  |  |  | Repeat test presented in associated document ModSel.jpg. Also please perform other tests for different combination of tuning parameter values and different combination of input values - please verify the the signals which are being used in output calculations are set correctly. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This appears to be an operational issue in the algorithm. The Y0 field in the algorithm record is 2 if XB or XC is selected. If XC is selected, it should be 4.<br>- (Hutchison, Steven B. Oct 14, 2013)<br><br>The Y0 field was set incorrectly, now it is fixed (Plamowski, Sebastian Dec 16, 2013)<br><br>LB:I have checked the above issue in 3.5.1_U3 and found working properly. Hence closed. (Baghel, LekhrajSingh Dec 27, 2013) <br> |  | 35 | FINDING | 10127 |  | FINDING | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | [8 empty] | Implementation | Ovation 3.5.1_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76491
31256 | FINDING | Details about compare operations under Tools menu is missing in online help. | Antony, Leena PROCESS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | Details about compare operations under Tools menu is missing in online help of Ov_80 manual.<br>The same has to be incorporated in Ovation 3.5.1 also. (N, Thamaraiselvi Sep 25, 2013) | LA 12/10/2013:A row has been added in the Tools menu items table for Compare Sheets and its description. |  |  | LA 12/10/2013: A row has been added for Compare Sheets with description in the Tools menu items table. Please navigate to section 5:Understanding Control Builder windows, menus, and toolbars -&gt; 5.2: What are the Control Builder menus?-&gt;5.2.5: Tools menu on the Control Builder main window. A copy of the manual is placed at: \\Uspit-fp05\ohara\Communication\TechComm\Share\Validation\Leena\OVATION 3.5.1\Control Builder 3.5.1\Draft 4\Draft4_OW351_80.pdf The name of the pdf file is Draft4_OW351_80.pdf. These changes will reflect in the U3 build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LA 12/10/2013: A row has been added for Compare Sheets with description in the Tools menu items table under section 5.2.5 Tools menu on the Control Builder main.<br><br>A copy of the manual is placed at: <br>\\Uspit-fp05\ohara\Communication\TechComm\Share\Validation\Leena\OVATION 3.5.1\Control Builder 3.5.1\Draft 4\Draft4_OW351_80.pdf<br><br>The name of the pdf file is Draft4_OW351_80.pdf. These changes will reflect in the U3 build. (Antony, Leena Dec 10, 2013).<br><br>COnfirmed the same setails in the manual. Thus closing the finding. (N, Thamaraiselvi Jan 13, 2014) <br> |  | 35 | FINDING | 10136 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | N, Thamaraiselvi AUTOSOL PWS NOIDA | [8 empty] | Implementation | OW351_80_U3 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76508
31264 | FINDING | SDR19730/OVA350032: GE Mark V ALARM points sometimes acknowledge without operator action. | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:06 | [11 empty] | USPITTFSService | 2015-06-12 04:06 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | SDR19730/OVA350032: If a Mark V ALARM point that has been acknowledged in Ovation leaves and enters an alarm state several seconds later, the point is Unacknowledged. If transitions in and out of the alarm state are quick enough (within a few seconds), the issue reported in the SDR still occurs. (Brown, Sean Sep 25, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This problem was resolved by Mike Durbin. (Plymire, Alvan W. Sep 25, 2013) <br> |  | 35 | FINDING | 10144 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76524
31328 | FINDING | OVA350036/SDR19895: OCR400 having a large number of points often gets stuck in Startup Mode | Zaremsky, Mark External MZCI | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | OCR400 Advanced Controller 14/64 (WALT) had multiple control sheets added to bring the point count to 31,026.<br><br>Cycles of Clear/Load/Reboot were performed with 14/64. After the fourth cycle 64 got stuck (as described in SDR 19895). (Brown, Sean Oct 14, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Brown, Sean</p> <p><strong>Responsible:</strong> Zaremsky, Mark</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Brown, Sean</p> <p><strong>Entry Date:</strong> 2013-10-14T09:01:59-04:00</p> <p><strong>Modified Date:</strong> 2013-10-22T09:10:43-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10208 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76652
31331 | FINDING | In Point review, Select the "Select Coloums" option, Error message is popping up. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 |  |  |  | 2015-06-12 04:07 |  |  |  | USPITTFSService | 2015-06-12 04:07 |  | Drop:- Drop176<br>Ov:- Ov 3.5.0<br>Step followed:-<br>1:- Open the Point review.<br>2:- Go to filter tab &amp; select the &quot;Select Coloums&quot; option.<br> Error message is popping up.<br> For more information please find the attached screen shot&quot;Unhandled exception error.jpg&quot; &amp; Error detail.txt. (Agarwal, Gaurav Oct 15, 2013) | none |  |  | Select columns functionality no longer causes application crash. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected in Ovation OVA350033 (Burgoon, Frank J. Oct 15, 2013)<br><br>GA:- <br><br>Issue has been resolved in OVA350033. Hence finding is closed. (Agarwal, Gaurav Nov 11, 2013) <br> |  | 35 | FINDING | 10211 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA350033 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | This was due to a change in OvPointDirObjects | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76658
31383 | FINDING | OVA350036/SDR19913: GNI3_sync utilize large amounts of a controllers CPU | Christy, Benjamin A PROCESS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | OVA350-036-10152013163323 was installed on Drop245 (WALT).<br>OCR400 Advanced Controller 14/64 is currently configured with 22,396 points; gni3_sync uses 80% of the CPU in the Backup controller. (Brown, Sean Oct 21, 2013) |  |  |  | Test as before | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Improved gni3_sync perfromance. (Christy, Benjamin Jan 15, 2014) <br> |  | 35 | FINDING | 10263 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | OVA350036, 3.5.1 U4 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | Changed hash function for better hash table lookup under certain conditions. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76763
31488 | FINDING | Help button is not functioning in Historical Trend. | Contento, James AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | Help button on upper right corner of Historical Trend window is not working. Whereas we are able to launch the online help in live trend window (Jain, Yukta Nov 8, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Is this a duplicate of finding #10185? Or is this a new problem? (Contento, James L. Mar 10, 2014)<br><br>During testing OVA350 patch of November Month, I found that help button of Historical trend was not working. So I reported issue for 3.5.0_OVA350_Patches.<br>F#10185 was against Ov3.5.1 release. (Jain, Yukta Mar 10, 2014) <br> |  | 35 | FINDING | 10368 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | More Information Supplied | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 76973
31611 | FINDING | Operator"s event are not coming if Test mode quality is changing from PI GUI. | Augustine, Lisa EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | If Quality of Any Point- LA,DA,LD,DD is changed from PI application then no operator event is coming for the point in Historical review.<br>However if quality is changed from Alarm or Point review application then same message can be seen in operator events. (Jain, Yukta Nov 21, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Operator Station (OW-OP)</p> <p><strong>Subproduct:</strong> Point Information (PI)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Jain, Yukta</p> <p><strong>Responsible:</strong> Augustine, Lisa</p> <p><strong>Notify List:</strong> Burgoon, Frank J. Jain, Yukta</p> <p><strong>Entry Date:</strong> 2013-11-21T23:04:23-05:00</p> <p><strong>Modified Date:</strong> 2013-11-21T23:04:23-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10491 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77209
31619 | FINDING | OVA350036/SDR19913: CPU usage of gni3_sync is reduced, but still high. | Christy, Benjamin A PROCESS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 |  |  |  | 2015-06-12 04:07 |  |  |  | USPITTFSService | 2015-06-12 04:07 |  | OVA350036/SDR19913: OVA350-036-11212013155036 was installed on the WALT system and downloaded to 14/64 (which were cleared and then loaded).<br><br>CPU usage of gni3_sync in the backup controller is less than it was previously, but is still higher than the expected 10%.<br><br>With an initial point count of 16,190 points the usage was 11% - 12%. It increased as the point count was raised and was 33% - 36% with a point count of 31,790. (Brown, Sean Nov 24, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10499 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | OVA350036 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77225
31648 | FINDING | SDR 19642 Failed:-Primary controller goes into failed mode when backup controller comes into backup mode. | Zaremsky, Mark External MZCI | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | Controller: - OCR1100 G02<br>Drop: - Drop21/drop71<br>Ov: - OV 3.5.0 (Net#8)<br>Patch used: - OVA350036<br>SFP Part no.: - FTLF1323P1BTR<br>Media Convertor: - EL100T-20<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1OFF<br>2ON<br>3OFF<br>4OFF<br>5OFF<br>6OFF<br><br>Steps followed:-<br>1:- Initially both the controller are Power OFF.<br>2:- In Primary controller, unplugged the SFP from N2 Port . <br>3:- Power ON the controller &amp; Communication is established with the N3 port &amp; <br> Controller is in control mode. <br> In Status tab of Drop point (Drop21.unit0@FE350), K0 is unavailable &amp; K1 is Unknown.<br>4:- In Backup controller, LC connector (Fiber cable) is not connected from the N3 port. <br>5:- Power ON the Controller.<br>6:- When Backup controller comes into backup mode, Primary controller goes into failed mode &amp; Backup controller comes into control mode.<br> Status tab of Drop point (Drop71.unit0@FE350), K0 is Active &amp; K1 is<br>unavailable. (Agarwal, Gaurav Dec 3, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> Controller Failover (FO)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Zaremsky, Mark</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2013-12-03T05:33:00-05:00</p> <p><strong>Modified Date:</strong> 2013-12-03T15:01:44-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10528 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77279
31649 | FINDING | SDR 19643 Failed:-Link of the N3 port is not available in SSD Graphic 1800 if unplugged the SFP from N2 Port. | Zaremsky, Mark External MZCI | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | Controller: - OCR1100 G02<br>Drop: - Drop21/drop71<br>Ov: - OV 3.5.0 (Net#8)<br>Patch used: - OVA350036<br>SFP Part no.: - FTLF1323P1BTR<br>Media Convertor: - EL100T-20<br><br>Media converter switch setting is as follows:<br><br>Dip Switch Status<br>1 OFF<br>2 ON<br>3 OFF<br>4 OFF<br>5 OFF<br>6 OFF<br><br>Steps followed:-<br>1:- Initially both the controller are Power OFF.<br>2:- In Primary controller, unplugged the SFP from N2 Port . <br>3:- Power ON the controller &amp; Communication is established with the N3 port &amp;<br>Controller is in control mode. <br> In Status tab of Drop point (Drop21.unit0@FE350), K0 is unavailable &amp; K1 is<br>Unknown.<br><br>In SSD Graphic 1800, Link of N2 port is red, but Link of N3 port is not available (Agarwal, Gaurav Dec 3, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Agarwal, Gaurav</p> <p><strong>Responsible:</strong> Zaremsky, Mark</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Agarwal, Gaurav</p> <p><strong>Entry Date:</strong> 2013-12-03T05:37:22-05:00</p> <p><strong>Modified Date:</strong> 2013-12-03T13:43:37-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10529 |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Boehmer, Robert W AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77280
31653 | FINDING | Fast/Slow time for virtual controllers not operating correctly for Operating System (kernel) mode. Patch OVA350036 | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 | [7 empty] | USPITTFSService | 2015-06-12 04:07 |  | The &quot;Task&quot; mode seems to work correctly for both the controller and virtual controller for both control and opp alarming. For Kernel mode, which is only applicable for Virtual controllers, fast or slow has no affect on OPP alarming. Slow speed commands appears to only affect the broadcasting rate, the control execution seems to be the same. i.e. running 10 times slow will update an incrementing (+1 every second) value every 10 seconds, but will still update by 10 when it should update by 1. Sending a &quot;fast&quot; command while in kernel mode produces the following error and has not affect on the control execution. <br>Controller Error : Coordinator Subsystem Error : Coordinator Monitor: Warning : 0x30 : 0x0 : 0x0 : 0x0 (Perdeus, Matthew Dec 3, 2013) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Virtual Controller (OVC)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Perdeus, Matthew</p> <p><strong>Responsible:</strong> Shiferaw,Tedla</p> <p><strong>Notify List:</strong> Shiferaw,Tedla Perdeus, Matthew</p> <p><strong>Entry Date:</strong> 2013-12-03T15:13:14-05:00</p> <p><strong>Modified Date:</strong> 2013-12-03T15:18:59-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10533 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77287
31665 | FINDING | Macro is not working fine when Records field are assigned as Analog point in GBNT. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:07 | [11 empty] | USPITTFSService | 2015-06-12 04:07 |  |  |  | 2015-06-12 04:07 |  |  |  | USPITTFSService | 2015-06-12 04:07 |  | Issue is observed in OVA350039 Patch and found during validating the SDR #19965.<br><br>It has been observed that Macro is not allowing to assign &quot;A1&quot;, &quot;A2&quot;, and &quot;A3&quot; as a process value in GBNT: Macro window, and If we are assigning the Other Records field like U4, U5, U6, 1W, 2W, and 3W in GBNT: Macro window, It is not able to display its real time values.<br> <br>Steps to reproduce:<br>1. Create various analog point as &quot;A1&quot;, &quot;A2&quot;,&quot;A3&quot;, &quot;1W&quot;, &quot;2W&quot;, &quot;3W&quot;, &quot;U4&quot;, &quot;U5&quot;AND &quot;U6&quot;.<br>2. Create a Macro of 6 Process point.<br>3. Now try to assign 1W,2W,3W,U4,U5,U6 in Macro window at the time of calling that Macro in GBNT, got assigned successfully. (But if the same time if you try to assign A1, A2 and A3, error popup is generated refer &quot;sdr-19965_2&quot; screenshot attached)<br>4. Save it ,compile it and close GBNT.<br>5. Now try to reopen that GBNT.<br>6. It is opening fine. (Here SDR#19965- Got Passed)<br><br>But now if we check the same GBNT in Real time situation, real time value of all the above assigned record field value are not displaying.<br><br>Refer attached screenshot. (Khandelwal, Rachit Dec 5, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Please check what you are doing in your test. I did what you described and my test graphic worked fine at runtime (i.e the values displayed from the macro were identical to the values displayed on the same graphic). Per your comment that \a1\ a1, \a2\ a2, and \a3\ a3 yield errors in GB when passed to a macro, that is correct. A1,a2,and a3 are NOT record fields in analog type points so GB should tell you that! For instance, A2 is a record field in packed points. I am wondering if you are displaying the AV field of your points in the PROCESS_POINT commands on the main graphic and the 1w,2w,3w,u4,u5,u6 fields of the same points in the PROCESS_POINT commands in the macro and comparing them and expecting them to be the same ?! If you still think there is a problem here submit the graphic .src for both the main graphic and the macro so I can see what you are doing in your test graphic. I believe the graphic runtime code and GB are functioning correctly. (Johnson, Kathy Dec 5, 2013)<br><br>RK:- Tested as per developer comments.. Found OK. Hence Closed (Khandelwal, Rachit Dec 6, 2013) <br> |  | 35 | FINDING | 10545 |  | FINDING | Khandelwal, Rachit PROCESS PWS NOIDA | [9 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Khandelwal, Rachit PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77311
31705 | FINDING | SDR#19922 - failed validation (is not working as mentioned in the resolution field) | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:08 | [11 empty] | USPITTFSService | 2015-06-12 04:08 |  |  |  | 2015-06-12 04:08 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | In the resolution field and affected areas of SDR19922, it is mentioned that If main screen with a trigger calls [RUN_PROGRAMS] command to write to an entry field in a window (Program 119) then there may be possibilities that the remaining commands in the trigger will be ignored. <br>I have used the code mentioned by DEV in Test recommendation area to test the SDR in OV350039 Patched System and found the issue unresolved. (Jain, Yukta Dec 14, 2013) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This finding should be tracked via SDR 19922. (Spillane, Donal A. Jan 24, 2014) <br> |  | 35 | FINDING | 10585 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 77386
31860 | FINDING | LP Points(the word) should be removed In the Online help document of System viewer Plant Mode Ribbon tab. | Jain, Swati EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2015-08-25 04:03 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | In the Online help document of System viewer Plant Mode Ribbon tab, the 2nd para which contains DA, DD, DP POINTS Long packed (LP) is also there for the appearance of the tab. The same should be removed here. The tab does not appear for LP Points.<br>Kindly find attached the snapshot for reference. (N, Thamaraiselvi Jan 28, 2014) | SJ Jan30,2014: Updated the System viewer Plant Mode Ribbon tab section. |  |  | SJ Jan30,2014: Updated the System viewer Plant Mode Ribbon tab section. The updated document is placed @ Q:\communication\TechComm\Share\Validation\OW351_20.pdf Also, check OvationApplications online help in 3.5.1 U5 build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | SJ Jan30,2014: Updated the System viewer Plant Mode Ribbon tab section. Check 3.5.1 U5 build. (Jain, Swati Jan 30, 2014) <br> |  | 35 | FINDING | 10740 |  | FINDING | [10 empty] | Implementation | 3.5.1_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Not Critical for This Release | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | SJ Jan30,2014: Updated the System viewer Plant Mode Ribbon tab section. The updated document is placed @ Q:\communication\TechComm\Share\Validation\OW351_20.pdf Also, check OvationApplications online help in 3.5.1 U5 build. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | u1 |  |  | FINDING | [6 empty] | 112961
32053 | FINDING | Simulation fast time not alarming points properly at 10x speed in "Task" mode. OVA350060 | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:08 | [11 empty] | USPITTFSService | 2015-06-12 04:08 | [7 empty] | USPITTFSService | 2015-06-12 04:08 |  | After issuing a fast x10 simulation speed command, the control is executing at 10x, but the points are only alarming at 6x. For example a digital toggling in/out of alarm every second is only being alarmed/returned 6x/sec in 10x mode. The remaining fast speeds work as expected, as 8x speed alarms/returns the point 8x/sec, etc. No task timeouts are being reported and SPY was showing 98% idle. This issue was repeatable in multiple VCs and also in a simcontroller. (Perdeus, Matthew Mar 5, 2014) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Simulator (SIM)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Perdeus, Matthew</p> <p><strong>Responsible:</strong> Shiferaw,Tedla</p> <p><strong>Notify List:</strong> Long, Edward M. Perdeus, Matthew Durbin, Michael J.</p> <p><strong>Entry Date:</strong> 2014-03-05T15:38:12-05:00</p> <p><strong>Modified Date:</strong> 2014-03-05T15:51:37-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10933 |  | FINDING | Durbin, Michael EMR SYSS PWS PITT | Long, Edward M EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78060
32117 | FINDING | In the Point Information, by clicking system id "ID", online help does not opens up. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:08 | [11 empty] | USPITTFSService | 2015-06-12 04:08 |  |  |  | 2015-06-12 04:08 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | In the Point Information, by clicking system id &quot;ID&quot;, online help does not opens up.<br>It has been observed in both DBS as well EWS stations.<br>Same case in Ovation 3.5.1 drops also. (N, Thamaraiselvi Mar 26, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | WIW - The ID field does not have any help - Way It Works No plans to fix. This issue was documented in Finding 10183 and 10970 and has been closed. (Augustine, Lisa Mar 26, 2014).<br><br>Agreeing with the developer&quot;s reply, closing the finding. (N, Thamaraiselvi Apr 4, 2014) <br> |  | 35 | FINDING | 10997 |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Cannot Duplicate | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78174
32159 | FINDING | Invalid configuration combinations do not generate errors for the 16 channel RTD module. | Swartz, Mark EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 | [7 empty] | USPITTFSService | 2015-06-12 04:09 |  | Various combinations of Ohmic Ranges and RTD Types were configured for the 16 channel RTD module which should generate errors and not allow the controller to be loaded. However the controller loads to completion and does not show any errors. Doing a consistency check at the controller level does not create any errors either, but if the consistency check is done from the unit level the error message &quot;RTD Channel Configuration must be greater than selected RTD R(Cold)&quot; is generated for each invalid combination. (Wood, Tom Apr 14, 2014) |  |  |  | The affected area is in the RTD consistency checks. Each internal RTD check will now set the status indicating that one-or-more errors exist. Tests must include the situation where the consistency checks report NO results other than the RTD-related consistency checks. The applicable binary is OvPtApi.dll (on the database server). | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | The RTD consistency checks will be updated to ensure that the results are propagated to the calling software such that loads are prevented (where applicable) and results are shown (where applicable).<br>This issue may also exist in Ovation 3.5.1. (Swartz, Mark E. Apr 14, 2014) <br> |  | 35 | FINDING | 11039 |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  | The RTD consistency checks are not returning a status indicating that &quot;one-or-more errors have been detected&quot;. If other consistency errors exist, then the load will be prevented. If other consistency error/warning/info situations exist, then results will be reported. This will be corrected. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78251
32174 | FINDING | SDR#20192 failed: Ovation developer Studio is crashing on configuring OPC on EWS. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | Ovation developer Studio is crashing on configuring OPC on EWS even after installing patch OVA350064. <br>Procedure: Developer studio --&gt; Configuration --&gt; Insert New OPC Server --&gt; Enter [Node] --&gt; Click on Browse button located at the end of the [ProgID field] --&gt; Select OPC Server from list --&gt; After selecting Server, Developer studio gets crash. (Jain, Yukta Apr 17, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Cannot duplicate in Pittsburgh Validation lab on 3.5.0 with OVA350064 on Database Server or on Operator Station. (Swartz, Mark E. Apr 17, 2014)<br><br>YJ: Instruction file of patch OVA350064 is updated with patch installation instructions. After installing the patch on EWS, problem is found to be fixed. Hence finding closed. (Jain, Yukta Apr 24, 2014) <br> |  | 35 | FINDING | 11054 |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | CND |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78281
32189 | FINDING | SDR#19959:Sensor alarm was not generated properly on all HW AI points when installing Ovation SP1 on SIS fails. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | While testing SDR#19959 its found that SENSOR alarm is not generated if HAI exceeds limit of over range/Under range.<br>On OCR400 controller SIS I/O channel-1 is defined as HAI, overrange pct of 23 and underange pct of 0.<br>Top scale is 100 and bottom scale is 0.BAD if limited is checked.<br>Channel 1 is wired to Temp transmitter and value coming is 25(Good quality).<br>ALRM sheet is also added in same SLS /control module. Another sheet is made with LSAI linking this channel 1.<br>Although value is greater than 23 expectation is SENSOR alarm BAD quality but, this is not the case. (Kumar, Shailendra Apr 22, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | This is expected behavior of in the patch if patch 59 was not installed previously. <br>This will be fixed after patch 71.<br><br>This issue is tracked by SDR. (Raciborski, Mikolaj Apr 23, 2014) <br> |  | 35 | FINDING | 11069 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78311
32191 | FINDING | Upgrading redundant SLS firmware gives error:Response should have at least one byte for partner SLS. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:09 |  | While testing SDR#19959 its observed that while upgrading firmware of Redundant SLS, Primary SLS firmware upgrades successfully but it gives error for partner SLS :&quot;Error while upgrading Logic Solver: Response should have at least one byte &quot;<br>attached is firmware up gradation session, we tried inter changing slot but with same result. (Kumar, Shailendra Apr 22, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <br> |  | 35 | FINDING | 11071 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
32266 | FINDING | "Reboot later" option is not working in Ovation (3.5.0 Patch update) install shield wizard | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | Run &quot;Ovation 3.5.0 April 2014 Update.exe&quot; on DBS(we used drop176)<br>Select setup type &quot;install all patches&quot; <br>Observe in the mid of installation,if reboot required option display <br>Select &quot;No, I will restart my computer later&quot; <br>Observed that if we select &quot;No reboot&quot; option even though it&quot;s reboot the drop<br><br>Install shield wizard should not reboot the system, If user is selected the &quot;NO&quot; option. (K, SendhilKumar May 5, 2014) (Matreja Shyam May 5, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | smatreja: This is the default dialog box from installshield. We always suggest to reboot after installation or during force reboot. (Matreja Shyam May 5, 2014) <br> |  | 35 | FINDING | 11146 |  | FINDING | K, SendhilKumar PROCESS PWS NOIDA | [9 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | K, SendhilKumar PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78463
32320 | FINDING | OVA350072 enables simcommand.exe on every VCH and base station regardless of if it is a simulator system. | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | This patch enables simcommand.exe on all VCH machines and all base stations. It may not be desireable to load this patch on these machines that exist in a DCS. A method for installing this as needed (as in 3.5.1) may be a better solution. (Perdeus, Matthew May 15, 2014) |  |  |  | run simcommand.exe -i to install restart the machine. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | simcommand.exe only will be installed if it run as simmcommand.exe -i<br>to uninstall simcommand.exe -u (Shiferaw,Tedla May 29, 2014) <br> |  | 35 | FINDING | 11200 |  | FINDING | Long, Edward M EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | OVA350072 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | Verified that simcommand is not starting automatically, but can be configured to start automatically by above command. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78568
32445 | FINDING | OVA350075 - DU ddb age in ddb.cnf for a virtual controller is ignored. | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | The age for a DU record always shows as 11. It is not configurable via this parameter. Changing this parameter in the local file and reboot, still shows age of 11. DDBTool was used to verify this. (Perdeus, Matthew Jun 12, 2014) | Embedded\Controller\vxsim\Contoller |  |  | change ddb-ageoriginatedDU value in ddb.cnf require download and reboot Observe if the value change in ddb age | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 11325 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | Zaremsky, Mark External MZCI | [8 empty] | Implementation | OVA350075 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78815
32464 | FINDING | The Controller"s "SCADA" process included with Prelim Patch 75 is crashing. | Plymire, Alvan AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 | [7 empty] | USPITTFSService | 2015-06-12 04:09 |  | Prelim OVA350-075-06102014094640 includes &quot;SCADA&quot; for the controller.<br><br>Issuing any Application program 226 command causes this process to crash. (Adkins, Craig T. Jun 18, 2014) | None |  |  | Please retest processing of GCODE226 requests. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Corrected by changing the ELC driver in the controller. (Plymire, Alvan W. Jun 18, 2014) <br> |  | 35 | FINDING | 11344 |  | FINDING | Adkins, Craig T EMR SYSS PWS PITT | [9 empty] | Implementation | OVA350075 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Adkins, Craig T EMR SYSS PWS PITT | Validation |  | None | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78851
32472 | FINDING | Cannot see SIS events in Historical Review. | Contento, James AUTOSOL PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 | [7 empty] | USPITTFSService | 2015-06-12 04:09 |  | While testing SDR#19962 which mention about SIS event, generated SIS event manually then checked in OPH tool (OVHconsole), events were coming in Ovhconsole but Historical review was not showing SIS events. It only displayed Time(attached is snapshot).OVA350075 patch is installed on DBS.<br>OPH release is OPH3.5.0 and machine on which its is checked is drop245(Win7 32 bit machine). (Kumar, Shailendra Jun 19, 2014) |  |  |  | See finding | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | A Ov3.5.1 change to SIS decoding was inadvertently introduced in a previous Ov350 patch causing the Hist Review application to no longer extract that information from TXT message history. The Hist Review application has been updated to call the new DecodeSIS function. (Contento, James L. Jun 26, 2014) <br> |  | 35 | FINDING | 11352 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350079 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78867
32476 | FINDING | Switchover of SLS in redundant SLS does not display process value for about 2-4 secs. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:09 | [11 empty] | USPITTFSService | 2015-06-12 04:09 |  |  |  | 2015-06-12 04:09 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | While testing SDR 18088 with Patch 75 loaded: 5 HART devices were connected to redundant SLS.<br>All 5 HART devices(2 HAI and 3 HAO)were seen in AMS 12.0 and Values were seen in AMS. When switchover of SLS was done from L--&gt;&quot;³R or through [Force Restart Active]we could not see the values of HAI in AMS for about 2-4 secs and got error message of disconnection(attached is snapshot of error). At this time Ovation trend either showed BAD/SENSOR alarm or remain constant to last value. After about 2 secs values of Hart I/P are seen correctly. HART Devices used for HAI are 3051 and 3144P.<br>Also attached is error log from SIS controller drop23.Controller has G03 IOIC mdule (Kumar, Shailendra Jun 19, 2014) (Raciborski, Mikolaj Jul 15, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | We tried to reproduce the issue without success, the only way the issue can happen is due to user activity. When user performing switchover without any delay, it may happen that the bad quality will be observed. (Raciborski, Mikolaj Jul 15, 2014) <br> |  | 35 | FINDING | 11356 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | NAR |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 78875
32518 | FINDING | Help not available for ELCCONTROL Algorithm in Control Builder. | Antony, Leena PROCESS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Nalwa, Varun AUTOSOL PWS NOIDA | 2015-07-06 05:08 | [11 empty] | Nalwa, Varun AUTOSOL PWS NOIDA | 2015-07-06 05:08 |  |  |  | 2015-07-06 05:08 |  |  |  | USPITTFSService | 2015-06-12 04:09 |  | The details of ELCCONTROL Algorithm is not available in the Help document of Control Builder for Ovation 3.5.0.<br>The Algorithm was added in Ovation Patch: OVA350075. (Nalwa, Varun Jul 3, 2014) | <p>LA 07/06/2015:The standard algorithms reference manual has been updated with the ELCCONTROL help. </p> |  |  | <p>LA 07/06/2015:The standard algorithms reference manual has been updated with the ELCCONTROL help. These changes will reflect in U10 build. The pdf version of the updated manual (U10_OW352_R1100) is placed at:<br>\\USPIT-FP05\Ohara\Communication\TechComm\Share\Validation\LEENA\Ovation 3.5.2 release\OW352_R1100 - Standard Algorithms\U10. </p><p>&nbsp;</p><p>Please navigate to section 5.40 ELCCTONTROL.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>LC 07/03/2014: Will be investigated for the Ovation 3.5.2 release. (Casteel, Linda Jul 3, 2014) <br></p><p>LA 07/06/2015:The standard algorithms reference manual has been updated with the ELCCONTROL help. These changes will reflect in U10 build. The pdf version of the updated manual (U10_OW352_R1100) is placed at:<br>\\USPIT-FP05\Ohara\Communication\TechComm\Share\Validation\LEENA\Ovation 3.5.2 release\OW352_R1100 - Standard Algorithms\U10. </p> |  | 35 | FINDING | 11398 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | MNR |  | <p><br></p> |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 1 |  |  | Nalwa, Varun AUTOSOL PWS NOIDA | Validation |  | Finding fixed, as seen in OV3.5.2_U10 Release. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | 3.5.2_U10 |  |  | FINDING | [6 empty] | 82202
32561 | FINDING | SIS events messages contains special characters, not understandable. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:05 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:05 |  |  |  | 2017-02-24 07:05 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | SIS events messages contains special characters, not understandable.<br>Performed some SIS events e.g. LS load, LS switchover.<br>Screenshots of results are attached for reference. (Pandey, Vijay Jul 16, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | Closing as this was resolved long ago<br> |  | 35 | FINDING | 11441 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | UNKNOWN |  |  | FINDING | [6 empty] | 109263
32602 | FINDING | SIS diagnostics gives protocol error as OVA350075 does not install on EWS as per instruction file. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Active | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2015-06-23 04:20 | [7 empty] | USPITTFSService | 2015-06-12 04:10 |  | In Instruction file of OVA350075 :<br>Under SIS support ONLY its mentioned<br><br>4. Install the patch on operator stations (it will only affect SIS Diagnostic supported firmware detection, then it may be omitted on stations where sis diagnostic is not and will be not used)<br><br>But OVA350075 is not allowed to be installed on operator station as it has dependency with Patches(14,60 and 62) which are installed on DBS only.<br>Due to this opening SIS diagnostics we get protocol error on operator station(refer attached snapshot).<br>SDS has the latest firmware update(3.5.0.152h)<br>Also tried to open SIS diagnostics on DBS but got same error. (Kumar, Shailendra Jul 27, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This issue is resolved in patch OVA350090 (Raciborski, Mikolaj Feb 23, 2015) <br> |  | 35 | FINDING | 11482 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350090 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 81657
32609 | FINDING | PWTTS - Fieldbus port download failed | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:42 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-07-02 10:42 |  |  |  | 2019-07-02 10:42 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | During configuration of function block on control builder, port download performed. <br>Download progress required user to click on Retry or else it won&quot;t advance.<br>At the completion of download process an error message window popup stating that: <br>[Error clearing port script attributes for P01]<br>[Error Sending Script (PortKey=&quot;3601&quot;, Script=&quot;LASSCH&quot;)]<br>[Download script LASSCH failed]<br><br>Module is left in it current stage for Al, Gil, and Bob to investigate.<br>Attached is the email discussion with details. (Phan, Quang Jul 28, 2014)<br><br>System Info:<br>Ovation 3.5.0 with latest patch OVA350075 installed: OVA350075-06302014113934 (Phan, Quang Jul 28, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 11489 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | Pratley, Bob EMR SYSS PWS PITT | [6 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | No Action Required | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation | patch 75 |  |  | FINDING | [6 empty] | 143791
32610 | FINDING | PWTTS - DVC6000 Rev 1, adding MAI block to controller build will affect functionality of AO block | Hutchison, Steven EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 | [7 empty] | USPITTFSService | 2015-06-12 04:10 |  | An AO block was configured to control the valve using the following logic:<br>AI=&gt;PID=&gt;AO<br>Configuration is working as expected. AO block from valve can be put in different modes (Man, Cas, Auto, OOS)<br><br>When MAI block from the same valve is configured, controller is loaded, port is clear and download, AO block from the valve went into OOS mode and can&quot;t no longer in control.<br><br>See attached email for details discussion.<br><br>System Info:<br>Ovation 3.5.0 with latest patch OVA350075 installed: OVA350075-06302014113934 (Phan, Quang Jul 28, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Fixed. Reference Data for FFMAI link offsets was mis-assigned.<br><br>Patch Updated on Friday July 25, 2014<br>- (Hutchison, Steven B. Aug 1, 2014) <br> |  | 35 | FINDING | 11490 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [8 empty] | Implementation | OVA350075 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79135
32694 | FINDING | Alarm Frequency List feature (SDR20519) is not included in Help. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 |  |  |  | 2015-06-12 04:10 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | No help is provided for Alarm Frequency List feature (SDR20519). This is not included in <br>Alarm application Help, <br>Online help or <br>Ovation Studio configuration Help. (Saxena, Pratishtha Aug 22, 2014)<br><br>This feature is added in Ovation 3.5.1, 3.5.0, 3.3.1 releases as SDR 20519, by installing different OVA patches. But help is not provided in any of the mentioned release. (Saxena, Pratishtha Sep 25, 2014) | SJ Jan 15, 2015: Alarm Frequency List feature has been added in Operator Station User Guide and Configuration Guide. SJ March 25, 2015: Alarm Frequency List feature has been added in Operator Station User Guide and Configuration Guide. SJ April 24, 2015: Alarm Frequency tab description added in Studio configuration help |  |  | SJ Jan 15, 2015: Alarm Frequency tab in the Operator Station Alarm window and Using the Alarm frequency tab sections have been added in Operator Station User Guide manual. Check OvationApplications.chm file in Ovation 3.5.2 U0 release. Also, check OW352_20.pdf placed @ Q:\communication\TechComm\Share\Validation Also, for configuration changes, Operator Station Configuration Guide has been updated. Check &quot;To configure the Alarm Display tab&quot; for the changes. Check OvptStudio.chm file in Ovation 3.5.2_U0 build and OW352_21.pdf placed @ Q:\communication\TechComm\Share\Validation SJ March 25, 2015: Alarm Frequency tab in the Operator Station Alarm window and Using the Alarm frequency tab sections have been added in Operator Station User Guide manual. Check OvationApplications online help in Ovation 3.5.2 U1 release. Also, check OW352_20.pdf placed @ Q:\communication\TechComm\Share\Validation Also, for configuration changes, Operator Station Configuration Guide has been updated. Check &quot;To configure the Alarm Display tab&quot; for the changes. Check OvptStudio online help in Ovation 3.5.2_U1 build and OW352_21.pdf placed @ Q:\communication\TechComm\Share\Validation SJ April 24, 2015: Alarm Frequency tab description added in Studio configuration help&gt; Configure Ovation Alarms&gt; What is Ovation Alarm System topic as well as in OW352_21.pdf. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | LC 08/22/2014: Reassigning to Swati Jain for 3.5.2 release of Operator Station User Guide and/or Config manual. (Casteel, Linda Aug 22, 2014)<br>SJ Jan 15, 2015: Alarm Frequency List feature has been added. Check Ovation 3.5.2 U0 release. (Jain, Swati Jan 15, 2015)<br><br>PRS 24 Feb 2015: No help is provided for Alarm Frequency List feature SRF1787 in Ov3.5.2_U0. This is not included in Alarm application Help, Online help or Ovation Studio configuration Help. Finding Failed. (Saxena, Pratishtha Feb 24, 2015)<br><br>SJ March 25, 2015: Alarm Frequency List feature has been added. Check Ovation 3.5.2 U1 release. (Jain, Swati Mar 25, 2015)<br><br>PRS 2 Apr 2015: Alarm Frequency list feature has been added in Alarm application Help, Online help or Ovation Studio configuration Help. <br> However Alarm Frequency tab description should also be added in Studio configuration help&gt; Configure Ovation Alarms&gt; What is Ovation Alarm System topic as well as in OW352_21.pdf. (Saxena, Pratishtha Apr 2, 2015)<br><br>SJ April 24, 2015: Alarm Frequency tab description added in Studio configuration help&gt; Configure Ovation Alarms&gt; What is Ovation Alarm System topic as well as in OW352_21.pdf. (Jain, Swati Apr 24, 2015)<br><br>PRS 24 Apr 2015: Ov3.5.2_U5, Alarm Frequency tab description has been added in Studio configuration help as well as in OW352_21.pdf. Hence closing this finding. (Saxena, Pratishtha Apr 24, 2015) <br> |  | 35 | FINDING | 11574 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Saxena, Pratishtha EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.5.2_U5 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | SJ Jan 15, 2015: Alarm Frequency tab in the Operator Station Alarm window and Using the Alarm frequency tab sections have been added in Operator Station User Guide manual. Check OvationApplications.chm file in Ovation 3.5.2 U0 release. Also, check OW352_20.pdf placed @ Q:\communication\TechComm\Share\Validation Also, for configuration changes, Operator Station Configuration Guide has been updated. Check &quot;To configure the Alarm Display tab&quot; for the changes. Check OvptStudio.chm file in Ovation 3.5.2_U0 build and OW352_21.pdf placed @ Q:\communication\TechComm\Share\Validation SJ March 25, 2015: Alarm Frequency tab in the Operator Station Alarm window and Using the Alarm frequency tab sections have been added in Operator Station User Guide manual. Check OvationApplications online help in Ovation 3.5.2 U1 release. Also, check OW352_20.pdf placed @ Q:\communication\TechComm\Share\Validation Also, for configuration changes, Operator Station Configuration Guide has been updated. Check &quot;To configure the Alarm Display tab&quot; for the changes. Check OvptStudio online help in Ovation 3.5.2_U1 build and OW352_21.pdf placed @ Q:\communication\TechComm\Share\Validation | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79300
32695 | FINDING | Points are not changing their position dynamically according to their Alarm frequency count. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 |  |  |  | 2015-06-12 04:10 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | In Alarm Frequency list there was a scenario when the alarm count of point A (which was relatively down in the list) gets higher then the alarm count of point B (which was up in the list). In this case point A which has higher Alarm count should move up in the list and point B should come at lower position then point A dynamically. <br> But actually they are retaining their position in the list and not changing according to their Alarm frequency count. (Saxena, Pratishtha Aug 22, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Works Per Design - The data for the points on the alarm frequency list is dynamic and will update. However, the points will not constantly move based on the alarm frequency count. When there is no sorting applied they remain in their current location and simply updated. The only time a point would shift positions is when a new point that is not currently displayed is added to the list. When this happens, then points might be moved on the display since a new point is added and an old point must be removed. That is providing the maximum number is already displayed. If you want the view to be sorted by the alarm frequency count, the column header can be selected to provide this functionality. (Augustine, Lisa Aug 22, 2014)<br><br>prs Aug 25, 2014: Closing this finding as per the developer&quot;s comments. (Saxena, Pratishtha Aug 25, 2014) <br> |  | 35 | FINDING | 11575 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Saxena, Pratishtha EMR SYSS PWS NOIDA | [8 empty] | Implementation | WAD |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79302
32717 | FINDING | Existing Alarm configuration can not be resaved with additional tabs. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 |  |  |  | 2015-06-12 04:10 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | Existing Alarm configuration can not be resaved with adding tabs. Steps followed are:-<br><br>1&gt; In Alarm application open an existing alarm configuration &quot;prs_aflist2&quot; having 7 tabs. <br>2&gt; Added Alarm Frequency tab in this window.<br>3&gt; Save this configuration with the same name &quot;prs_aflist2&quot;.<br>4&gt; Message is displayed if we want to rewrite this file, select yes.<br>5&gt; Close and reopen the Alarm application.<br>6&gt; Load configuration &quot;prs_aflist2&quot;. Error message is displayed saying &quot;Index was outside the bounds of the array&quot;. Select OK.<br>7&gt; Now we can see that total 7 tabs are displaying in alarm window. However the Alarm Frequency tab has been added in the window but Remote network Status tab is missing. (Saxena, Pratishtha Sep 5, 2014)<br><br>Please find the attached jpeg for message while saving configuration &quot;AFList_saving_error&quot; and for loading error &quot;AFList_loading_error&quot; (Saxena, Pratishtha Sep 5, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | I was not able to reproduce this in order to debug the alarm application. Please send me the prs_aflist2.alm and prs_aflist2.alm.lay files that are causing this issue. (Augustine, Lisa Sep 5, 2014)<br><br>I was testing the Ovation 3.5.1 not Ovation 3.5.0. I was able to get this to happen on Ovation 3.5.0 so I do not need the files. (Augustine, Lisa Sep 5, 2014)<br><br>This issue is also in the Ovation 3.5.1 patch as well. Finding 11606 was written against both releases, but it is a duplicate of this finding. We will track the issue with this Finding. (Augustine, Lisa Sep 8, 2014)<br><br>prs: After installing the patch, Checked saving n loading of new and existing alarm configurations. We are getting the desired configuration and no error message is displayed. Finding has been resolved. This issue has been resolved in 3.5.1 also after installing patch OVA351008. (Saxena, Pratishtha Sep 11, 2014) <br> |  | 35 | FINDING | 11597 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Saxena, Pratishtha EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA350082 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79344
32751 | FINDING | PWTTS - Controller failover cause FF devices failure | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pratley, Bob EMR SYSS PWS PITT | 2019-06-25 14:01 | [11 empty] | Pratley, Bob EMR SYSS PWS PITT | 2019-06-25 14:01 |  |  |  | 2019-06-25 14:01 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | System has both Simplex and Redundant Fieldbus modules available with patch OVA350-075-09082014145514 installed. Fieldbus devices are commissioned and configured in control sheet. All function blocks reported good status in Signal Diagram. Reboot active controller to cause a failover to standby controller. After period of time, note that FF devices started to fail on both Simplex and Redundant Fieldbus module. Port clear and download is required to recover failed devices.<br><br>Attached is reproduce of issue included serial log file from controllers and Fieldbus module. Also included email discussion with developer team. (Phan, Quang Sep 18, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 11631 |  | FINDING | Phan, Quang EMR ENT TECH AUS | Pratley, Bob EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Investigate After Release | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation | ? |  |  | FINDING | [6 empty] | 143459
32752 | FINDING | PWTTS - Controller constantly report unable to find point which is no longer on system | Christy, Benjamin A PROCESS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 | [7 empty] | USPITTFSService | 2015-06-12 04:10 |  | During the course of troubleshooting for issue filed in Finding 11631, monitor communication on controller via serial port, note that it kept reporting &quot;Unable to find PDT1REV08 on card 3&quot;. This point belong to a device that was commission on system before and no longer exist on system.<br><br>See attached for log files capture on both controllers and email discussion invloved this issue. (Phan, Quang Sep 18, 2014) (Boehmer, Robert W. Feb 9, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Controller (CTLR)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Phan, Quang</p> <p><strong>Responsible:</strong> Christy, Benjamin</p> <p><strong>Notify List:</strong> Boehmer, Robert W. Phan, Quang</p> <p><strong>Entry Date:</strong> 2014-09-18T11:57:05-04:00</p> <p><strong>Modified Date:</strong> 2015-02-09T15:28:43-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 11632 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79408
32753 | FINDING | PWTTS - Clear and download FF port occasionally hang with "Server Busy" window popup | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 |  |  |  | 2015-06-12 04:10 |  |  |  | USPITTFSService | 2015-06-12 04:10 |  | Occasionally, perform a clear and download of FF port will cause &quot;Server Busy&quot; window to popup constantly. User is required to keep clicking on &quot;Retry&quot; in order to proceed with download process. If this is not done then it will just hang and won&quot;t complete download process.<br><br>Don&quot;t know what cause this problem and don&quot;t know how to setup system to reproduce this issue. However, once happen, issue is reproducible easily after that.<br><br>Normally, when the &quot;Server Busy&quot; window popup, if leave alone, whatever process was running, it will continue on the background. This window will go away once process completed.<br>Discussed with Nooch and agreed to file this as WIW to document this observation. (Phan, Quang Sep 18, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 9/18/14 &gt; Quang saw this issue during patch OVA350075 testing. The Server Busy popup seemed to occur when loading a heavily loaded Fieldbus module segment. This was discussed during Ov patch meetings and was noted that this was a Microsoft popup that could not be &quot;fixed&quot;. This finding serves as documentation of this scenario. Closing finding as WIW. (Capani, Nooch Sep 18, 2014) <br> |  | 35 | FINDING | 11633 |  | FINDING | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | WIW |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79410
32830 | FINDING | OVA350086: Channel faults are usually reported when OCR pair is powered up (when task period &lt= 25 ms) | Souders, Sarah EMR SYSS PWS PITT | Active | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 | [7 empty] | USPITTFSService | 2015-06-12 04:10 |  | OVA350-086-09252014121000:<br>Several HSDO modules are configured with points and control in OCR400 Controller 12/62 (WALT). Some of the points and control were assigned to a task running at 15ms. 3 HSDOs are Simplex; 3 pairs are redundant. When a hard reboot of both partners is performed the fast-running module points will usually report one or more channels as having a fault (Bit 14 of the A2 field and multiple bits of the RK field). It was determined that the module test rate of 25ms may be the cause. The phenomenon does not occur when the task period is 50ms or greater. This was not observed in Revision 4.<br><br>Additional observations:<br>-Both simplex and redundant modules report this.<br>-The redundant modules do not always report the same channels. In one instance the left module reported 16 channel faults and the right module reported none.<br>-This does not occur if the timeout action is set to Latch, unless the module is reseated while the OCRs are powered off.<br>-By default the control for the HSDO output points cycle on and off. If the control sets or resets all of the points simultaneously the channel fault bits will clear and stay cleared. (Brown, Sean Oct 10, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | In the last case mentioned, where control sets all bits to 1 or 0 simultaneously, do the bits toggle at the same rate as in the normal test case involving cascading 1&quot;s? (Souders, Sarah Oct 10, 2014)<br><br>No, they point states do not toggle. They all stay at 1 or 0 (depending on which has been selected). (Brown, Sean Oct 10, 2014)<br><br>The DO_FAULT alarm following controller reboot issue is now fixed for task periods &gt; 50ms. The HSDO module does not support task periods &lt;= 50ms. Users are advised against running this module in such a fast task. (Souders, Sarah Oct 14, 2014) <br> |  | 35 | FINDING | 11710 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation | OVA350086 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Will Fix in the Future Update | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | Added some code to detect the state of the output control registers. If the value of these registers does not match the value the ATmega8515 is sending to them, then we know the I/O controller is overriding them due to I/O timeout. In this case, we don&quot;t trigger a DO_FAULT alarm. | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79563
32861 | FINDING | PWTTS - Alarm system doesn"t Rosemount 848T Rev 8 device alert | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2015-06-12 04:10 | [11 empty] | USPITTFSService | 2015-06-12 04:10 | [7 empty] | USPITTFSService | 2015-06-12 04:10 |  | System has 3 different revisions of 848 device. 5, 7 and 8. Alert for Revision 8 device is working fine on DeltaV system.<br>When simulate alarm by removing sensor 1&amp;2 on all 3 devices. Alarm for 5 and 7 come up but not on 8<br>AMS does show sensor alarm for all 3 devices.<br>Alarm does show when revision 8 device is disconnect from the segment (as note in the screenshot attached that it return to green when we reconnect back to segment)<br><br>This system has all the latest patches up to September 2014 included OVA350-0075 (Phan, Quang Oct 17, 2014) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Fieldbus Engineering Server (FES)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Phan, Quang</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Swartz, Mark E. Phan, Quang Capani, Nooch</p> <p><strong>Entry Date:</strong> 2014-10-17T16:04:49-04:00</p> <p><strong>Modified Date:</strong> 2014-10-17T16:04:49-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 11741 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | Swartz, Mark EMR SYSS PWS PITT | [12 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 79624
33215 | FINDING | SDR-20826 fails: GBNT Crashes on installing Patch-OVA350094. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 |  |  |  | 2015-06-12 04:11 |  |  |  | USPITTFSService | 2015-06-12 04:11 |  | GBNT crashes while opening any graphic after installing Patch-OVA350094. <br>Crashing issue is observed on NET#8 Drop-176 DBS, Drop-182 EWS. <br>Screenshot attached for reference. (Khandelwal, Rachit Jan 19, 2015)<br><br>RK (01/27/15):-<br>Issue is resolved by installing updated patch OVA350-094-01202015133450 provided by developer.<br>Hence closing this finding. (Khandelwal, Rachit Jan 27, 2015) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12095 |  | FINDING | Johnson, Kathy EMR SYSS PWS PITT | Khandelwal, Rachit PROCESS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Khandelwal, Rachit PROCESS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 80316
33273 | FINDING | Use of unique drop names in drop.cfg is not working in OVA350093. | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 | [7 empty] | USPITTFSService | 2015-06-12 04:11 |  | The use of unique drop names in the drops.cfg file will not work. The response from the controllers is not seen. Also if the same drop name is in the drops.cfg twice, even with different IP addresses, it will fail. (Perdeus, Matthew Jan 30, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Simulator (SIM)</p> <p><strong>Subproduct:</strong> General (GEN)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Perdeus, Matthew</p> <p><strong>Responsible:</strong> Shiferaw,Tedla</p> <p><strong>Notify List:</strong> Long, Edward M. Perdeus, Matthew Shiferaw,Tedla</p> <p><strong>Entry Date:</strong> 2015-01-30T17:11:29-05:00</p> <p><strong>Modified Date:</strong> 2015-02-06T15:56:03-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12153 |  | FINDING | Long, Edward M EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Create drops.cfg file with unique drop names and run simulator command test program to send commands. | EPM Validation |  |  |  | FINDING | [6 empty] | 80428
33335 | FINDING | SDR 20758 Fails : SBSequence algorithm do not skip over a sequence that has an invalid ID . | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 | [7 empty] | USPITTFSService | 2015-06-12 04:11 |  | SDR 20758 Fails : SBSequence algorithm do not skip over a sequence that has an invalid ID in ovation 3.5.0.<br><br>If the first blower of a particular step is left blank /invalid ID and the second blower is configured for any blower, the sequence freezes when it comes to that step.<br><br>Recreated steps are below:<br>Step1- Configure steps in SBSequence algorithm.<br>Step2- Enter parameters. (Algo runs fine as expected)<br>Step3- Enter Invalid Blower ID in one of the steps.(Example as in attached snapshot)<br>Step4- Save -&gt; Load -&gt;Run the sheet.<br>It is observed that reaching the invalid blower ID step the algorithm freezes (Kumar, Sudheer Feb 20, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Advanced Controller (ADVC)</p> <p><strong>Subproduct:</strong> Advanced Algorithms (AALG)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Kumar, Sudheer</p> <p><strong>Responsible:</strong> Bush, Kirt T</p> <p><strong>Notify List:</strong> Long, Edward M. Kumar, Sudheer</p> <p><strong>Entry Date:</strong> 2015-02-20T03:19:56-05:00</p> <p><strong>Modified Date:</strong> 2015-02-20T03:19:56-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12215 |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | Long, Edward M EMR SYSS PWS PITT | [11 empty] | Drop176(DBS+PDC) Net#8; Ovation 3.5.0 with OVA350092 + APC 3.5.1 + OCR400 . |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation |  |  |  | FINDING | [6 empty] | 80549
33337 | FINDING | No default values are provided for writable parameters in FF Analog Input & Analog Output Function Blocks | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 | [7 empty] | USPITTFSService | 2015-06-12 04:11 |  | ISSUE DESCRIPTION:<br> In the FFAI FB &amp; FFAO FB, parameters as XD_SCALE_EU_0, XD_SCALE_DECIMAL, OUT_SCALE_EU_0, OUT_SCALE_DECIMAL, LOW_CUTOFF, PV_FTIME, PV_SCALE_EU_0, SP_RATE_DN, SP_RATE_UP, SP_HI_LIM, FSTATE_TIME,RCAS_IN_VALUE do not have a predefined value to be downloaded from ovation database to the device. <br><br>See Steven Hutchison comment:<br><br>Currently, none of the values have defaults. We display the values that are read from the device. The read may be failing, which we are not reporting. In this case we should present a default value.<br><br>The above parameters mentioned are filled in with HUGE values that makes difficult to commission the FFAI &amp; FFAO FBs. See attached picture for further reference. (de la Cruz, Irving Feb 20, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Fieldbus Engineering Server (FES)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> de la Cruz, Irving</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Swartz, Mark E. de la Cruz, Irving Capani, Nooch</p> <p><strong>Entry Date:</strong> 2015-02-20T17:06:15-05:00</p> <p><strong>Modified Date:</strong> 2015-02-20T17:06:15-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12217 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Commission a FF device and create a Control Sheet in order to assign a AI to that device. Download the AI or AO to the device and read the values. Observe that some extremely large values make no sense, specially in important parameters as XD_SCALE_EU_0 | EPM Validation |  |  |  | FINDING | [6 empty] | 80551
33338 | FINDING | The parameter PV_FTIME is not defined as writable. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 | [7 empty] | USPITTFSService | 2015-06-12 04:11 |  | ISSUE DESCRIPTION:<br>The parameter PV_FTIME (Process Value Filter Time) is defined as read only. It must be user enterable. (de la Cruz, Irving Feb 20, 2015)<br><br>This parameter must be defined as writable in all the foundation function blocks where it is defined, for instance it can be found in FFAIs, FFPIDs and FFDIs but might be also found in other FBs. (de la Cruz, Irving Feb 25, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Control Builder (OW-CB)</p> <p><strong>Subproduct:</strong> Fieldbus Engineering Server (FES)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> de la Cruz, Irving</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Hutchison, Steven B. de la Cruz, Irving Capani, Nooch</p> <p><strong>Entry Date:</strong> 2015-02-20T17:28:08-05:00</p> <p><strong>Modified Date:</strong> 2015-02-25T17:01:09-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12218 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [14 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Launch the application Tuning from an active FFAI, FFPID, FFDI and try to modify this value. Observe that it is greyed out with a value similar to 4.874444 e+014. | EPM Validation |  |  |  | FINDING | [6 empty] | 80552
33344 | FINDING | PWTTS: The FFPID FB can be changed to CAS mode even tough the parameter CAS_IN is NOT being wired. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2015-06-12 04:11 | [11 empty] | USPITTFSService | 2015-06-12 04:11 | [7 empty] | USPITTFSService | 2015-06-12 04:11 |  | ISSUE DESCRIPTION:<br>The FFPID function block can be sent to CAS mode even tough the parameter CAS is not being wired in a Control Sheet logic.<br>EXPECTED RESULTS<br>The CAS_IN_STATUS should know that the CAS mode is not being invited and should reject the attempt to change to CAS mode. (de la Cruz, Irving Feb 24, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> WIN Developer Studio (OW-DS)</p> <p><strong>Subproduct:</strong> Fieldbus Engineering Server (FES)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> de la Cruz, Irving</p> <p><strong>Responsible:</strong> Hutchison, Steven B.</p> <p><strong>Notify List:</strong> Swartz, Mark E. de la Cruz, Irving Capani, Nooch</p> <p><strong>Entry Date:</strong> 2015-02-24T16:15:10-05:00</p> <p><strong>Modified Date:</strong> 2015-02-24T16:15:10-05:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12224 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [13 empty] | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  |  | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | See attached Picture:Cas_In_Value | EPM Validation |  |  |  | FINDING | [6 empty] | 80563
33625 | FINDING | OVA350099 causes I/O immediate simulation with remote points to not work. | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:12 | [11 empty] | USPITTFSService | 2015-06-12 04:12 | [7 empty] | USPITTFSService | 2015-06-12 04:12 |  | Simulation using remote network points with standard I/O and I/O immediate points was corrected with patch OVA350076. Installing patch OVA350099 causes the I/O immediate simulation to not work with remote points. This invalidates the previous patch 076. (Perdeus, Matthew May 13, 2015) |  |  |  |  | 0 |  |  |  | <p><strong>Product:</strong> Ovation Virtual Controller (OVC)</p> <p><strong>Subproduct:</strong> Controller Input/Output (IO)</p> <p><strong>Release Level:</strong> 3.5.0_OVA350_Patches</p> <p><strong>Originator:</strong> Perdeus, Matthew</p> <p><strong>Responsible:</strong> Shiferaw,Tedla</p> <p><strong>Notify List:</strong> Shiferaw,Tedla Perdeus, Matthew</p> <p><strong>Entry Date:</strong> 2015-05-13T10:59:16-04:00</p> <p><strong>Modified Date:</strong> 2015-05-13T10:59:16-04:00</p> | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 12505 |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | [12 empty] | Windows 3.5.0. + patch OVA350099. |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 1 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Create a simulated RLC and a sheet with SLC in algoritm. Attempt to simulate output of a SLC IN algorithm with a remote point. | EPM Validation |  |  |  | FINDING | [6 empty] | 81072
33650 | FINDING | SDR#20722 in OVA350095 partially failed. | Shaw, Scott External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2015-06-12 04:12 | [11 empty] | USPITTFSService | 2015-06-12 04:12 |  |  |  | 2015-06-12 04:12 |  |  |  | USPITTFSService | 2015-06-12 04:12 |  | As per this SDR,while the Burst mode os ON with message-&gt;1current-&gt; verified all multivariables are good.-SDR passed for this point. But for the message2-&gt;percent of scale, instead of PV through FV bad quality, observed the PV &amp; TDV remained good quality.<br>This observation was verified with both the Tempearture &amp; Pressure Transmitters connected to the device and observed repeatedly.<br>Thus partially failing this SDR. (N, Thamaraiselvi May 21, 2015) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 5/26/15&gt; Selvi, I believe this observation is tracked already as SDR 20775. Please discuss with Sendhil to confirm. If it is the same issue : <br>-you may pass the OVA350095 test as SDR Passed, Finding Writen.<br>-Close this Finding and note that it is the same issue as 20775. <br>Thx! (Capani, Nooch May 26, 2015).<br>As per Nooch&quot;s advice and also observed tis same as SDR20775, closing the finding. (N, Thamaraiselvi May 27, 2015) <br> |  | 35 | FINDING | 12530 |  | FINDING | Brown, Rick P EMR SYSS PWS PITT | N, Thamaraiselvi AUTOSOL PWS NOIDA | [8 empty] | Implementation |  |  | Ovation 3.5.0, with OVA350095. |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.5.0 |  |  | User Error | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | As per this SDR,while the Burst mode os ON with message-&gt;1current-&gt; verified all multivariables are good.-SDR passed for this point. But for the message2-&gt;percent of scale, instead of PV through FV bad quality, observed the PV &amp; TDV remained good quality. This observation was verified with both the Tempearture &amp; Pressure Transmitters connected to the device and observed repeatedly. Thus partially failing this SDR. | EPM Validation |  |  |  | FINDING | [6 empty] | 81116
33946 | FINDING | OSR fails to read from Controller when OVA350107 is loaded | Lim, Leo EMR SYSS PWS MAND | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 |  |  |  | 2015-08-28 11:22 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2015-07-08 07:31 |  | <p>When Ov-3.5.0 DBS is loaded with OSR Patch OVA350-107-06022015092513,</p><p>The OSR fails to read data from any live Controller.</p><p>Error in the SysReg.log file</p><p>&nbsp;&nbsp;&nbsp; Requesting controller information from DROP1/51<br>&nbsp;&nbsp;&nbsp; Error&nbsp;Exception caught while getting drop info: </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Unable to find an entry point named 'GetDropInfoEx' in DLL 'ctrlxfacewrapper.dll'.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jimenez, William PROCESS PWS MNL | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Perdeus, Matthew AUTOSOL PWS PITT | [7 empty] | Implementation |  |  | <p>Ov-350 DBS </p><p>Ov-350 + OVA350-107</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | OVA350-107-07292015053728 was released on the Ov.3.5.0 Jul CD. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OVA350107 |  |  | FINDING | [6 empty] | 87500
34020 | FINDING | Description for ONDELAY Algorithm ENBL input should be changed to optional IN Ov3.5.0 | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 |  |  |  | 2015-07-20 07:45 |  |  |  | Nalwa, Varun AUTOSOL PWS NOIDA | 2015-07-20 05:07 |  | <p>ENBL(Enable) Input of ONDELAY Algorithm has been changed to optional input as mentioned in SDR#21006.</p><p>If ENBL is not connected to the algorithm, it works as if IN1 and ENBL inputs are tied together.<br>The Help documentation for ONDELAY algorithm must be updated for OV3.5.0 as already done for Ov3.5.1 &amp; 3.5.2.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.5.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Nalwa, Varun AUTOSOL PWS NOIDA | Validation |  | LC 07/20/2015:&nbsp; We cannot go back to the Ovation 3.5.0 release to update the online help. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.5.0 |  |  | FINDING | [6 empty] | 87500
34612 | FINDING | OVA350112 - SDR34295 Failed : ELC xxxxx command line generates SOE events for LA points | Kakroo, Tanisha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2023-07-12 03:44 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2023-07-12 03:44 |  |  |  | 2023-07-12 03:44 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2015-09-23 22:44 |  | <font face="Times New Roman" size=3> </font><p class=MsoPlainText style="margin:0cm 0cm 0pt;"><span style="color:windowtext;"><font size=2><font face=Arial>When running the command line “ELC_Generate_SOE_Test_Report 0 &quot; or “ELC_Generate_SOE_Test_Report 1&quot; , controller generates </font></font></span><span style="color:windowtext;"><font size=2><font face=Arial>SOE messages for LA point configured in ELC. </font></font></span></p><p class=MsoPlainText style="margin:0cm 0cm 0pt;"><span style="color:windowtext;"></span>&nbsp;</p><span style="color:windowtext;"><font size=2><font face=Arial><p class=MsoPlainText style="margin:0cm 0cm 0pt;"><span style="color:windowtext;">Historical Review application displays LA points in SOE tab with point name as SID of that point and description as “</span><span lang=EN-US style=""><font color="#0000cc">SID not configured for drop</font></span><span style="color:windowtext;">”.</span></p></font><p class=MsoPlainText style="margin:0cm 0cm 0pt;"></p><p class=MsoPlainText style="margin:0cm 0cm 0pt;">&nbsp;</p></font><p class=MsoPlainText style="margin:0cm 0cm 0pt;">&nbsp;</p><p class=MsoPlainText style="margin:0cm 0cm 0pt;">&nbsp;</p></span><p class=MsoPlainText style="margin:0cm 0cm 0pt;">&nbsp;</p><p class=MsoPlainText style="margin:0cm 0cm 0pt;">&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.5.0 </p><p>Controller : OCR-400 &amp; OCR-1100</p><p>Patch : OVA350-112</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | <p>Patch OVA&nbsp;350-112&nbsp; has been updated, Please Retest.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">1) Install OVA&nbsp;350-112 patch on OV350 DBS drop.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">2) Restart DBS.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">3) Download &amp; Reboot controllers .</span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">4) Login to the drop (with ELC configured)&nbsp;through Putty.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">5) Run the command &quot;ELC_Generate_SOE_Test_Report 0&quot; or&nbsp; “ELC_Generate_SOE_Test_Report 1&quot; .</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">6) Open Historical Review , navigate to SOE tab</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">7) Start review from concerned drop.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"></span>&nbsp;</p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Observation : </span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">1) SOE messages are generated with correct information for LD points.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">2) SOE messages are generated for LA points with following information :-</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Point Name :&nbsp; 0x8004a45a (SID of point)</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Description : SID not configured for drop</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"></span>&nbsp;This SID after checking from Point Review shows the point is LA.</p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Please find the screenshot attached.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"></span>&nbsp;</p><p><font face="Times New Roman" size=3> </font></p> |  | OVA350-112 |  |  | FINDING | [6 empty] | 204492
35071 | FINDING | SDR 34585 failed for OVA 350-116. | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 06:07 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 06:07 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 06:02 |  | SDR 34585 <font face=Calibri><font size=3>(In a simulator environment, the OPP is not properly restoring the packed points on an IC load) failed for OVA 350-116..</font></font><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.5.0 with patch OVA 350-116&nbsp; |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.5.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following steps are performed in drop1 (virtual controller ) in simulator environment.</p><p>1. Loaded the patch in DBS (drop176) &amp; in VCH (drop206) as per instruction file.</p><p>2.&nbsp;Saved the IC( using simcontrol GUI- running on VCH)&nbsp;&nbsp;with packed points in non-alarm state and made sure it they have been acknowledged and reset.</p><p><font color="#1f497d">3.&nbsp;<font color="#000000">Placed the simulator in run&nbsp;</font></font></p><p><font color="#1f497d"><font color="#000000">4.&nbsp;Forced the appropriate bits on the points to cause them&nbsp;to alarm.</font></font></p><p><font color="#1f497d"><font color="#000000">5. Freeze the simulator.</font></font></p><p>6. Load the IC saved in step2</p><p>&nbsp;&nbsp; It is observed that point was in &quot;RETURN&quot; state instead of non-alarm state , it was acknowledged but not RESET</p><p>&nbsp;&nbsp; also bit 19 1W was SET.</p><p><br></p><p>&nbsp;&nbsp; I also tried by&nbsp;<span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">saving IC when packed point bit 19 is set to 0 and &nbsp;using shc_demo force alarm bit.</span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p>&nbsp;&nbsp;&nbsp;and&nbsp;load saved IC&nbsp; but the point was in &quot;RETURN&quot; state instead of non-alarm state , it was acknowledged but not RESET</p><p>&nbsp;&nbsp; also bit 19 1W was SET.</p><p>&nbsp;</p></span><p>&nbsp;Hence this SDR is failed.</p><p><br></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><br></p><p><br></p><p><br></p><p>&nbsp;&nbsp; </p></span><p><br></p><p><br></p><p><br></p> |  | Patches |  |  | FINDING | [6 empty] | 88893
35265 | FINDING | OVA350118 contains no instruction to download/reboot controllers | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-16 14:24 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-16 14:24 |  |  |  | 2015-12-16 14:24 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-16 11:14 |  | Patch OVA350118 contains a new vxworks for the controller/virtual controller.&nbsp; There are no instructions included stating that it is necessary to download/reboot the controllers. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.5.0 + OVA350118 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>Added instructions to patch:</p><p><br>Install the patch the Database Server.</p><p>Perform the following steps in Developer's Studio for each Ovation Controller:<br>&nbsp;<br>1)&nbsp; Right click on the controller drop and select Download</p><p>2)&nbsp; From the menu, select the file &quot;vxWorks&quot;, deselect all other files.</p><p>3)&nbsp; After file has been downloaded, right click again and select Reboot.</p><p>4)&nbsp; Verify the drop rebooted and is in Backup Mode before repeating the steps for the partner drop.</p><p><br></p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | View contents of OVA350118 |  | OVA350118 |  |  | FINDING | [6 empty] | 89878
35535 | FINDING | SDR34357, RR35278 failed in patch OVA350115 | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-01-27 04:23 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-01-27 04:23 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-01-27 03:02 |  | <font size=3><font face=Calibri><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font face=Calibri>Higher No of Vxsim Drops are rebooting by themselves if lower no of Vxsim Drops are stopped by stopping VCoordinater Service or VCoordManager application<span style="color:rgb(31, 73, 125);">.</span></font></p><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font face=Calibri><span style="color:rgb(31, 73, 125);">OR</span></font></p><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font face=Calibri><span style="color:rgb(31, 73, 125);"></span>Secondary Virtual Controllers are rebooting by themselves, if primary Virtual Controllers are stopped by stopping VCoordinater Service or VCoordManager application<span style="color:rgb(31, 73, 125);">.</span></font></p></font></font><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></font></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.5.0 Setup with&nbsp;DB Server Drop176 (win 2008R2)&nbsp;+ VCH Drop210 (win 7 32 bit) + VCH Drop206 (win 7 32 bit) |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.5.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="margin:0in 0in 0pt;"><b><font face=Calibri>Steps to Reproduce:</font></b></p><p class=MsoListParagraph style="margin:0in 0in 0pt 0.25in;text-indent:-0.25in;"><span><span><font face=Calibri>1.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Verify the Primary Virtual Controllers are in one VCH and Secondary Virtual Controllers are in Second VCH. (E.g. All primary Virtual Controllers are configured in one VCH Drop and Secondary Virtual Controllers are in another VCH Drop.)</font></p><p class=MsoListParagraph style="margin:0in 0in 0pt 0.25in;text-indent:-0.25in;"><span><span><font face=Calibri>2.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Verify the Primary Virtual Controllers are “In Control” and Secondary Virtual Controllers are in “Back Up”.</font></p><p class=MsoListParagraph style="margin:0in 0in 0pt 0.25in;text-indent:-0.25in;"><span><span><font face=Calibri>3.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Stop Primary Virtual Controllers by stopping Vcoordinator Service or VCoordManager Application. </font></p><p class=MsoListParagraph style="margin:0in 0in 0pt 0.25in;text-indent:-0.25in;"><span><span><font face=Calibri>4.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Check the Status of Secondary Virtual Controllers in System Viewer or Graphics Application and verify that these are “in Control”.</font></p><p class=MsoListParagraph style="margin:0in 0in 0pt 0.25in;text-indent:-0.25in;"><span><span><font face=Calibri>5.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span></span></span><font face=Calibri>Check the Ovation Error Log and mainly following error messages can be observed for Secondary VxSim Controller drop:</font></p><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);"><b><u><font color="#000000"><font face=Calibri>Note:</font></font></u></b></span></font></font></p><font size=3><font face=Calibri><p class=MsoListParagraph style="margin:0in 0in 0pt;"><font color="#000000"><font face=Calibri>1. Setup&nbsp;is updated till Ovation 3.5.0 Patch OVA350114.</font></font></p></font></font> |  | OVA350115 |  |  | FINDING | [6 empty] | 91615
37409 | FINDING | G04 OCR1100 controller goes to offline state consistently on Ovation 3.5.0 during Reboot/Failover operation. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-10-19 22:54 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-10-19 22:54 |  |  |  | 2016-09-13 08:44 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-09-01 06:13 |  | <p>After downloading the OVA350-131-07292016131405 patch on Ov3.5.0, Reboot/Failover operation of G04 OCR1100 controller goes to offline state consistently on Ovation 3.5.0.</p><p>The issue was same on old controller pair 25/75&nbsp;as well as on&nbsp;11/61&nbsp;which is hooked up&nbsp; as fresh&nbsp;controller pair.</p><p>This behaviour is consistent when G04 is in control (Partner presnt in backup or switched Off). </p><p>However,&nbsp;when the G04 is in back up&nbsp; (Partner) this behaviour is less frequent ~ Once in four times.</p><p>Attached are USB details. Flash details are provided to&nbsp;developer in seperate mail.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [7 empty] | Implementation |  |  | <p>Ovation 3.5.0;</p><p>OVA350-131-0729;</p><p>OCR1100 -G04;</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | No Action Required | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri>I had configured only N2 port in the beginning.</font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face=Calibri>&nbsp;</font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri><span>&nbsp;</span>It was noticed that N2 port cable was not reliable which resulted into<span>&nbsp; </span>intermittent failure of the pinging.<span> </span></font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri><span>&nbsp;</span><span>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font face=Calibri><font size=3>Later on I configured <span>&nbsp;</span>N3 port also which inadvertently was connected to NID port (which is not recommended.)</font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri><span>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri>So when the above 2 cases occurred simultaneously, controller went to failure state due to network connectivity.</font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face=Calibri>&nbsp;</font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri>Remedy: </font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri>1. Changed the N2 patch card permanently.</font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font face=Calibri><font size=3>2. Replaced <span>&nbsp;</span>the N3 port connectivity to other port of backup switch .</font></font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face=Calibri>&nbsp;</font></p><font size=3 face="Times New Roman"> </font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3><font face=Calibri>After changing this, I <span>&nbsp;</span>rebooted/failover the controller (both Offline &amp; Hard reboot) with the following combinations.</font></font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font face=Calibri><font size=3 face="Times New Roman"> </font></font></p><font face=Calibri><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3>Configured the OHI mode of the controller as single with N2 only.</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3>Configured the OHI mode of the controller as single with N3 only.</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3>Configured the OHI mode of the controller as dual with N2 connected, N3 removed and</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3>Configured the OHI mode of the controller as dual with N3 connected, N2 removed.</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face="Times New Roman"> </font><font size=3>After doing many attempts, now it is confirmed the reboot/failover of the G04 controller is working fine.</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3>So closing the finding.</font></p><p style="margin:0in 0in 0pt;" class=MsoPlainText><font size=3 face="Times New Roman"> </font></p></font><p style="margin:0in 0in 0pt;" class=MsoPlainText><font face="Times New Roman"><font size=3> </font></font></p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Step1&gt; Format flash, Enter MAC Address of controller, wait for download.</p><p>Step2&gt; Download-&gt;Hard boot controller (Power Cycle)-&gt;here Pinging is seen to be lost-&gt;</p><p>Step3&gt; Hard boot controller for 2nd time-&gt; this time Pinging is on and continous. </p><p>Now, controller is seen In Control state.</p><p>&nbsp;</p> |  | OVA350131-07292016131405 |  |  | FINDING | [6 empty] | 104192
37637 | FINDING | G04 OCR1100 controllers details are not being reported in OSR report for the proto type as well as Pilot production units. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-09 00:08 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-09 00:08 |  |  |  | 2016-11-09 00:08 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-09-27 03:35 |  | <p>Configured prototype OCR110 controller pairs 25/75 and Pilot&nbsp; production units 32/822&nbsp;on Ov.3.5.0 for G04 testing with OCR1100 G04 as primary and G01 as partner.</p><p>&nbsp;</p><p>While running SureService Ovation System Registration tool it is observed that the tool doesn't report correct details for both the units.<br>The&nbsp;Reports are as below:</p><table class=SectionTable> <tbody><tr> <td class=ParamColumn>Serial Number:&nbsp;&nbsp;&nbsp;</td> <td class=ValueColumn></td> <tr> <td class=ParamColumn><p>Electronic Index:</p><p>&nbsp;</p><p>This above&nbsp; details are blank&nbsp; for both proto and Pilot&nbsp; production units.&nbsp;</p><p>Partner Serial Number is displayed as s.</p><p>Please find attached the report.</p></td></tr></tbody> </table> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Ovation 3.5.0 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.5.0 |  |  | System Deviation Report created | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>GWS 11/1/2016&gt; Do the OCR1100 G01 details appear in the Ovation 3.5.0 version of the System Registration Utility?</p><p><br></p><p>cg (11/9) - SDR#37968 created to track this issue. Hence finding closed.</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Configured OCR110 controller pairs 25/75 and 32/72 on Ov.3.5.0 for G04 testing with OCR1100 G04 as primary and G01 as partner.</p><p>Ran OSR report on DBS drop176. The report missed the required details as above.</p> |  | OVA350131-07152016103842 |  |  | FINDING | [6 empty] | 105158
37638 | FINDING | After patch installation OVA 350132, few record fields (e.g.: - KM, VE, K0 and K1) of virtual controller Drop(DU) point goes into Unknown state. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-09-29 08:19 | [11 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-09-29 08:19 |  |  |  | 2016-09-29 08:19 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-09-27 05:46 |  | After patch installation OVA 350132, few record fields (e.g.: - KM, VE, K0 and K1) of virtual controller Drop(DU) point goes into Unknown state.<div><br></div><div><br></div> |  |  |  | Please provide values for these fields for the VCH drop (DU) point, i.e.&nbsp;<span style="font-family:Calibri;font-size:medium;">drop210. &nbsp;</span> | 0 |  |  |  | <p>GA:- </p><p>Date:- 9/29/2016</p><p><br></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test with OVA350-132-09282016142732 patch and observed that issue has been resolved. Hence finding is closed.</span></p> | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Shiferaw, Tedla AUTOSOL PWS PITT | Zaremsky, Mark External MZCI | Sachan, Pallavi EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [6 empty] | Implementation | OVA350132 Sept 28 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>VCH drop: - drop210</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>DBS Drop:- Drop176</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation Release: - Ov 3.5.0</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>VC drop: - drop100</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | Added &quot;ddb_simpc.drv&quot; to the patch. | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Before patch installation(OVA350132): - </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1: - All the Virtual controller are running and all the record fields of virtual controller Drop(DU) points are in healthy state. Please refer the screen shots” Before patch installation.jpg”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>&nbsp;</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>After patch installation(OVA350132): - </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>1: - Install the patch into DBS and reboot the system.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>2: - In the developer studio, Select the Virtual controller drop(Drop100), download and reboot the drop.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>3: - It is observed that drop(drop100) come into healthy state but few record fields (e.g.: - KM, VE, K0 </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>and K1) of virtual controller Drop(DU) point goes into Unknown state.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Please refer the screen shots” After patch installation.jpg”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>For further investigation please find the remote login details.</font></p><font face="Times New Roman" size=3> </font> |  | OVA350132 |  |  | FINDING | [6 empty] | 103376
37640 | FINDING | G04 OCR1100 controller type is not being displayed as type G04 in Controller Diagonostic tool. It shows as type G01 for pilot production unit. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-15 05:26 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-15 05:26 |  |  |  | 2016-11-15 05:26 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-09-27 07:36 |  | <p>Pilot production unit Sr. no. 2361655771 with Mac address 00:40:03:06:D6:41 is configured on Ovation 3.5.0. </p><p>However CD tool displays the type as G01.</p><p>Mac id is showing correct.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software | As long as the Manufacturing Index on the OCR1100 starts with the number 245 (represented internally in hex&nbsp;as &quot;FC&quot; in the&nbsp;Index string), the group number will now be pulled from this Index. Otherwise, the old method that differentiates only&nbsp;between copper (G01) and fiber (G02) will be used. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Zaremsky, Mark External MZCI | [6 empty] | Implementation | OVA350131_21October |  |  |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>Controller Diagnostics now correctly displays the&nbsp;OCR1100 group number.</p><p><font size=3 face="Times New Roman"> </font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/9/2016</span></p><p><font size=3 face="Times New Roman"> </font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch OVA350-131_1108 (Baytrail)on DBS drop#176. Downloaded, Clered, Loaded the Pilot G04 Controller/Go2 Controllers of drop32/82.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the Controller Diagnostic tool. Click on controller 32/82 . Here drop32 is pilot type. </span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Even after installing the latest patch OVA350-131_1108 (Baytrail), it still displays as G01 type instead of G04.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus Changing the state of this finding as open with state reason failed retest.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Also please find attached the snapshot.</span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;"><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/15/2016</span></p><p><font size=3 face="Times New Roman"></font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch OVA350-137-10252016133133 (Baytrail)on DBS drop#176 and EWS drop#231.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the Controller Diagnostic tool. Click on controller 32/82 . Here drop32 is pilot type. </span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Verified that&nbsp;after installing the latest patch OVA350-137-10252016133133 (Baytrail),&nbsp; now the controller type displayed as&nbsp;G04.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">This has been verified both on DBS &amp; EWS.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus closing the finding.</span></p></span><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;"></span>&nbsp;</p><p><font size=3 face="Times New Roman"> </font></p> | 12 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA350131-07152016103842 |  |  | FINDING | [6 empty] | 105324
37644 | FINDING | SDR 37372: Fuses is misspelled in the Module Type (OVA350) | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2016-10-06 10:37 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-10-06 10:37 |  |  |  | 2016-10-06 10:37 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-09-27 09:47 |  | SDR 37372<br><br>The Module Type description is misspelled:&nbsp; <span style="font-style:italic;">Digital Output 5-60 VDC w/ Ch STO, relay pnl comm and ext <span style="font-weight:bold;">fusses</span></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA350134-09072016084611 |  |  | FINDING | [6 empty] | 103685
37669 | FINDING | G04_SD_SVTP_rev1.1.docx Test 5.1.1.10 has error in calculation | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-09-29 09:32 | [11 empty] | USPITTFSService | 2016-09-29 09:32 | [7 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-09-29 09:32 |  | Test 5.1.1.10:&nbsp; Calculated Developer Studio entry<br><br><span style="font-weight:bold;">[Update Period at Nominal Speed (msec)] = (1/[Nominal Speed (RPM)]) x (60 sec/min) x (1/[Number of Teeth]) x [Number of Teeth per Sample]</span><br>should include <span style="font-weight:bold;">x (1000 msec/sec)<br></span><br>This error is present in the G03 SVTP as well.<span style="font-weight:bold;"><br></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Firmware/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Firmware | SVTP/STP | Standard Release | 3.5.0 |  |  | New Issue | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | Any |  |  | FINDING | [6 empty] | 103381
37693 | FINDING | G04 OCR1100: Controller switched to “Failed mode” after configuration of 3rd party Device followed by download, Clear and Load operation. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-11 06:05 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-11 06:05 |  |  |  | 2016-11-11 06:05 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-10-04 03:35 |  | <p>Configured 3rd party devices GE mark vi and RTO IO and corredponding IOIC drivers.</p><p>On performing a Download , Clear and Load operation OCR1100 G04 Controller switched to “Failed mode” during load operation .</p><p>Controller error log as well as the putty error showed&nbsp;as&nbsp; Coordinator Subsystem Error” followed by “Could not sync with ssv_task”.</p><p>Controller id not boot up with multiple hard boots. It came up only after deleting the flash files.</p><p>Since the error was Coordinator Subsystem Error, did not report previously &amp; did not take the the putty details.</p><p>It is similar as f#37654 &amp; 37655.</p><p>I do't have the putty logs now.</p><p>If the developer needs the putty details, then will recreate the scenario &amp; attach the details.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ov3.5.0 with OVA350-131-07152016103842 patch |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 8pt;" class=MsoNormal><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/9/2016</span></p><p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 8pt;" class=MsoNormal><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch OVA350-131_1108 (Baytrail)on DBS drop#176. Downloaded, Cleared, <span style="">&nbsp;</span>&amp; Loaded the Pilot G04 Controller/Go2 Controllers of drop32/82.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Configured 3rd party devices GE mark vi and RTO IO and corresponding IOIC drivers.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Performed a Download , Clear and Load operation of Pilot OCR1100 G04 Controller as well as G02 controllers.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Observed the Pilot OCR1100 G04 Controller came as healthy state.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the control sheets, verified the proper operation of PI, and other OVA applications.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus verified the issue was fixed on the Pilot module with the latest patch.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">However, while verifying OVA350-13 FINDING 37962:(Controller stays offline after rebooting when the firewall is enabled.) Pilot G04 controller went to failed state.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Also other findings of Controller Diagnostics 37640, 37704 are also failed with this patch.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus keeping this finding in monitoring state to test &amp; verify in the next patch.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Shall update the status after installing the next patch available.</span></p><p><font size=3 face="Times New Roman"> </font></p><p><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/11/2016</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch </span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">OVA350-131-11092016065424</span><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3> </font></span><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">on DBS drop#176. Downloaded, Cleared &amp; Loaded the Pilot G04 Controller/Go2 Controllers of drop25/75.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Configured 3rd party devices GE mark vi and RTO IO and corresponding IOIC drivers.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Performed a Download , Clear and Load operation of Pilot OCR1100 G04 Controller as well as G02 controllers.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Observed the Pilot OCR1100 G04 Controller came as healthy state.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the control sheets, verified the proper operation of PI, and other OVA applications.</span></p><p><font size=3 face="Times New Roman"> </font><span style="color:black;line-height:107%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus verified the issue was fixed on the Pilot module with the latest patch and closing the finding.</span></p><p><font size=3 face="Times New Roman"> </font></p> | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Configured 3rd party devices GE mark vi and RTO IO and corredponding IOIC drivers.</p><p>On performing a Download , Clear and Load operation OCR1100 G04 Controller switched to “Failed mode” during load operation .</p><p>Controller error log as well as the putty error showed as Coordinator Subsystem Error” followed by “Could not sync with ssv_task”.</p><p>Controller id not boot up with multiple hard boots. It came up only after deleting the flash files.</p> |  | OVA350131-07152016103842 |  |  | FINDING | [6 empty] | 105287
37704 | FINDING | G04 OCR1100 : Controller Type is seen as OCR1100 G01 in controller diagnostics on Ov3.5. 0 for both prototype and Pilot production modules. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-15 05:28 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-15 05:28 |  |  |  | 2016-11-15 05:28 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-10-04 23:24 |  | <p>Configured prototype OCR110 controller pairs 25/75 and Pilot production units 32/822 on Ov.3.5.0 for G04 testing with OCR1100 G04 as primary and G01 as partner.</p><p>&nbsp;</p><p>&nbsp;Controller Type is seen as OCR1100 G01 instead of OCR1100 G04 in controller diagnostics for both the above said types.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA350137 |  | Ov3.5.0 |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/9/2016</span></p><p><font size=3 face="Times New Roman"></font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch OVA350-131_1108 (Baytrail)on DBS drop#176. Downloaded, Clered, Loaded the Pilot G04 Controller/Go2 Controllers of drop32/82.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the Controller Diagnostic tool. Click on controller 32/82 . Here drop32 is pilot type. </span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Even after installing the latest patch OVA350-131_1108 (Baytrail), it still displays as G01 type instead of G04.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus Changing the state of this finding as open with state reason failed retest.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Also please find attached the snapshot.</span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;"><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">TN:11/15/2016</span></p><p><font size=3 face="Times New Roman"></font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Installed the latest patch OVA350-137-10252016133133 (Baytrail)on DBS drop#176 and EWS drop#231.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Opened the Controller Diagnostic tool. Click on controller 32/82&nbsp;and 25/75.&nbsp;Here drop32&nbsp; and drop25 are pilot type. </span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Verified that after installing the latest patch OVA350-137-10252016133133 (Baytrail), now the controller type displayed as G04.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">This has been verified both on DBS &amp; EWS.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">Thus closing the finding.</span></p></span></span><p><span style="color:black;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;"></span> </p><p><font size=3 face="Times New Roman"></font></p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Configured prototype OCR110 controller pairs 25/75 and Pilot production units 32/822 on Ov.3.5.0 for G04 testing with OCR1100 G04 as primary and G01 as partners.</p><p>However CD displays as G01 insttead of G04.</p> |  | OVA350131-07152016103842 |  |  | FINDING | [6 empty] | 105325
37715 | FINDING | SDR37365 OVA350134: Some limits are not enforced in Studio | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2016-10-07 12:00 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-10-07 12:00 |  |  |  | 2016-10-07 12:00 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-10-06 11:46 |  | SDR37365 OVA350134<br><br>The following attributes can be set to zero, but should not be less than 1:<br><br>Overspeed Limit (RPM)<br>Nominal Speed (RPM)<br>Mechanical Trip Speed (RPM)<br> |  |  |  |  | 0 |  |  |  | Not release-critical.&nbsp; SDR 37722 created.&nbsp; Closing finding.<br> | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.5.0 |  |  | System Deviation Report created | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA350134-09272016120152 |  |  | FINDING | [6 empty] | 103739
37766 | FINDING | G04 OCR1100: N2/N3 link status amber LED does not blink always. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 13:44 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 13:44 |  |  |  | 2016-11-28 13:44 |  |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-10-17 07:54 |  | <font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">On OCR1100 G04&nbsp; having N2/N3 configured for Ovation and&nbsp;N4 as dedicated cable. When N2 and N3 both are connected.</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Its observed that &nbsp;link status&nbsp; amber LED of any one of N2 or N3 is available not both at&nbsp;same time on H/W.</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Suppose Status diagram shows N2 as Green and N3 as yellow. At this time physical H/W will show LED of N2 as amber blinking and N3 as OFF.</font></span></p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman"><p><font color="#000000" size=3><br></font></p><p style="margin:0in 0in 0pt;"><span style=""><font color="#000000" face=Calibri size=3>cg (11/9) : An issue similar to the above&nbsp;was reported by Vijay Pandey via email dtd. 11/3/16.</font></span></p><p><font color="#000000" size=3> </font><span style=""><font color="#000000" face=Calibri size=3>SIS legacy testing is in progress on Ov 3.5.1. Primary Controller [1100G04]/ Partner controller [1100 G01]</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Controller&nbsp;having N1/N4 configured for SIS Network. When N1 and N4 both are connected.</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">In the case of 1100 G04 that the SIS network port is in &quot;backup&quot;, which in turn prevents the LED indicator from flashing.</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Its observed that &nbsp;link status&nbsp; amber LED of any one of N1 or N4 is available not both at&nbsp;same time on H/W.</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Note: In the case of 1100 G01 that the port is in &quot;backup&quot;, which in turn does not prevent the LED indicator from flashing.</font></span><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000"><br></font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Scenario observed for 1100 G04: </font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">If N1 port connect first then N4 port. At this time physical H/W will show LED of N1 as amber blinking and N4 as OFF.</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">If N4 port connect first then N1 port. At this time physical H/W will show LED of N4 as amber blinking and N1 as OFF.</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000"><br></font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Response from developers are as below:</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Mikolaj R. - in Legacy SIS, the controller ports N1 and N4 are bind by OHI as the N2, N3. (email dtd. 11/3/16).</font></span></p><p><font color="#000000" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><font color="#000000">Greg S. - If this is the case, then yes, one of the receivers (backup port) &nbsp;would be turned off which prevents the amber flashing LED. (email dtd. 11/3/16).</font></span></p><p><font color="#000000" size=3> <br></font></p></font><p><br></p></span><p><br></p><font face="Times New Roman" size=3> </font> | <p>cg (11/2) - Note to be added in DIR.</p><p>cg (11/16) - SDR#38016 created to track this finding.<br>IC 11/28/16&gt; added note to DIR. Closed SDR 38016 as WAD.&nbsp; </p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [8 empty] | Implementation |  |  | Ov3.5.0, OCR1100 G04, IOIC G02. |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Note added to DIR | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | This is working as we expect. &nbsp;<span style="font-size:12px;">In the case that the port is in &quot;backup&quot; the receiver is turned off which prevents data from being received, which in turn prevents the LED indicator from flashing.</span><div><br></div><div>From the Controller Manual:<div><br></div><div><span style="font-weight:bold;">Status LEDs for the Controller processor module:</span><div><br></div><div><span style="font-style:italic;">The Controller processor module (left side of Controller) provides nine indicator LEDs that display status information about the interface between the Controller and the Ovation network.&nbsp;</span></div><div><span style="font-style:italic;"><br></span></div><div><span style="font-style:italic;">There is a green power indicator (labeled P) and a pair of green and amber LEDs for each Ethernet port (labeled N1, N2, N3, and N4).&nbsp;</span></div><div><span style="font-style:italic;"><br></span></div><div><span style="font-style:italic;">The green power indicator lights when the Processor module is powered. Each Ethernet network port has two indicator LEDs (green and amber).&nbsp;</span></div><div><span style="font-style:italic;"><br></span></div><div><span style="font-style:italic;">The green indicator is the Link Integrity/Power LED and lights when the port is receiving power and flashes slowly when the module is linked with the network through that port.</span></div><div><span style="font-style:italic;"><br></span></div><div><span style="font-style:italic;">The amber indicator displays Link Activity status and <span style="text-decoration:underline;">flashes when the module is receiving or transmitting data on that port.</span></span><br></div></div></div> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA350131-07292016131405 |  |  | FINDING | [6 empty] | 105794
37805 | FINDING | G04 OCR1100: Controller on Ov3.5.0 fails on error initializing SOE command port after adding devices | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 7 | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-11-07 07:43 | [11 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-11-07 07:43 | 71367 |  |  | 2016-11-07 07:43 |  |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-10-20 09:09 |  | <p>While testing for G04 OCR 1100, Added Modbus-R and External Ovation I/O device.</p><p>Added corresponding Drivers. Downloaded Partner controller drop82 (G01 processor)&nbsp;which in&nbsp;Backup mode. Then Cleared and loaded&nbsp; with no error.</p><p>Tried same on Drop32(G04 Processor)&nbsp;but controller came up in failed CLR mode&nbsp; with SOE initialization error. Cannot do Putty&nbsp; to this drop, says Access denied after giving password.</p><p>Then cleared flash of drop32 and&nbsp;tried to restore back, but it is still failing.</p><p>After using clean Flash started logging HyperTerminal session connected to this controller. Following steps were done after&nbsp;putting clean Flash&nbsp;:</p><p>1) Downloaded successfully to drop32.</p><p>2) Rebooted&nbsp;this drop.&nbsp;</p><p>3) When controller comes up it is in failed state and give SOE Initialization error. Status diagram shows fault code 66,8,0,eH.For reference check drop32_1ST_failure.JPG and drop32_1ST_failure_error.JPG.</p><p>4)Cleared this failed drop 32.</p><p>5)Drop comes up in Backup CLR&nbsp;mode.</p><p>6) If loading is done from studio it fails with error in studio saying drop32 is unavailable although we can ping drop and status diagram also shows it in Backup CLR state.</p><p>7) After 5 minutes without doing any operation Controller will fail again with error &quot;Subsystem Group 1 error: Generic Fatal Error 0x2:0x2:0x1:0x0&quot;. Status diagram shows fault code:66,9,d,2H.</p><p>For reference check drop32_2nd_failure.JPG and drop32_2nd_failure_error.JPG.</p><p>8) Drop cannot be restored and kept in same state. Hyper Terminal session for above steps are attached.&nbsp;</p><p>9)Flash contents of drop32 are kept in following path:</p><p><a href="file://\\Uspit-fp05\ohara\ProductDevelopment\Share\GregS\G04-OCR1100">\\Uspit-fp05\ohara\ProductDevelopment\Share\GregS\G04-OCR1100</a></p><p><br></p><p>Remote login steps to this Network is also attached.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA350131, OVA351080 (26October) |  | Ov3.5.0, G04 OCR1100 pilot type module |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | SK:10/25:attached file (drop32_command.txt) is output from G04 OCR1100 using command <strong>iosFdShow </strong>when running healthy.<div><br></div><div>GS&gt; Increased the max number of file from 192 to 255 to match the OCR1100 G01</div><div>SK&gt;Tested with latest OVA350 (26th Oct) Patch and issue&nbsp;is resolved.&nbsp;</div> | 10 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Following steps were done after&nbsp;putting clean Flash&nbsp;:<p>1) Downloaded successfully to drop32.</p><p>2) Rebooted&nbsp;this drop.&nbsp;</p><p>3) When controller comes up it is in failed state and give SOE Initialization error. Status diagram shows fault code 66,8,0,eH.</p><p>4)Cleared this failed drop 32.</p><p>5)Drop comes up in Backup CLR&nbsp;mode.</p><p>6) If loading is done from studio it fails with error in studio saying drop32 is unavailable although we can ping drop and status diagram also shows it in Backup CLR state.</p><p>7) After 5 minutes without doing any operation Controller will fail again with error &quot;Subsystem Group 1 error: Generic Fatal Error 0x2:0x2:0x1:0x0&quot;. Status diagram shows fault code:66,9,d,2H.</p><p>8) Drop cannot be restored&nbsp; even after using another clean Flash.&nbsp;Same failure is recreated.</p> |  | OVA350131-07292016131405 |  |  | FINDING | [6 empty] | 105045
37961 | FINDING | G04 OCR1100: Controller stays offline after rebooting when the firewall is enabled. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-11-10 03:24 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-11-10 03:24 | 71559 |  |  | 2016-11-10 00:56 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-11-07 23:20 |  | <p>Controller stays offline after rebooting when the firewall is enabled.</p><p><br></p><p><br></p> |  |  |  | <p><span style="color:rgb(31, 73, 125);line-height:106%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [6 empty] | Implementation | OVA350-131-11092016065424 |  | Ovation 3.5.0 + <span style="line-height:105%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">OVA350-131-11042016075050 </span>+ Controller OCR1100 G04 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | <p>Fixed the arp packet structure to match the vxworks 6.9 version.</p><p><br></p><p>SDK 11/09 : Retest with new build patch OVA350-131_1108 and finding is not fixed in this patch.</p><p><br></p><p>SDK 11/10 : Controller offline issue is resolved in the new build patch OVA350-131-11092016065424 with pilot module hence finding closed.</p> | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;">Step to Reproduce :</p><p style="margin:0in 0in 0pt;">1. Change the control task scan time period.</p><p style="margin:0in 0in 0pt;">2. Download and reboot the controller.</p><p style="margin:0in 0in 0pt;">3. After reboot the controller is up with offline state and we cannot proceed the testing </p><p style="margin:0in 0in 0pt;"><br></p><span style="color:rgb(0, 32, 96);"><p style="margin:0in 0in 0pt;"><br></p><font face=Calibri size=3><p style="margin:0in 0in 0pt;"><br></p><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><font color="#000000" face="Times New Roman"><br></font></p></font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><br></p></span><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><br></p><font face="Times New Roman" size=3> </font> |  | OVA350-131-11042016075050 |  |  | FINDING | [6 empty] | 105244
38003 | FINDING | G04 OCR1100: N1, N3 and N4 interfaces always reports as 100Mbps full duplex in Ovation Error log. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-30 09:40 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-30 09:40 |  |  |  | 2016-11-30 09:40 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-11-15 05:52 |  | <p>Controller Interfaces N1, N3 and N4 when confiured for 3rd party IO communication always reports port parameters as 100Mbps full duplex, what ever may be the port configuration.</p> <p>The ports&nbsp;are configured for different combinations (100Mbps full duplex, 100Mbps&nbsp;half duplex, auto negotiate, etc.) and the 3rd party IO&nbsp;is also configured with same configuration, but still Ovation Error Log always reports 100Mbps full duplex on port Up or Down status messages.</p> <p>No communication issues observed with these communication settings.</p> <p>Please refer to attached snapshot.</p> <p>&nbsp;</p> <p>Same issue is also observed on Ov3.5.1 (OVA351-080-11092016065328)</p> <p>&nbsp;</p> <p>&nbsp;</p> <p>&nbsp;</p> <p>ASG, 11/21/16&gt; <span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI">Explored more by connecting a laptop directly to N1 port of OCR1100 G04 module through cross over cable and got similar results for Ov3.5.0 and Ov3.5.1 as below:</font></font></span></p> <p><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"></font></font></span>&nbsp;</p> <p> <table class=MsoNormalTable style="WIDTH:681pt;BORDER-COLLAPSE:collapse;MARGIN:auto auto auto -0.4pt;" cellspacing=0 cellpadding=0 width=908 border=0> <tbody> <tr style="HEIGHT:15.75pt;"> <td style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BACKGROUND:#002060;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1pt solid;PADDING-RIGHT:5.4pt;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><b><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:white;"><font face="Segoe UI"><font size=2>Controller Side</font></font></span></b></p></td> <td style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BACKGROUND:#002060;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><b><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:white;"><font face="Segoe UI"><font size=2>Laptop Side</font></font></span></b></p></td> <td style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BACKGROUND:#002060;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;" valign=bottom width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><b><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:white;"><font face="Segoe UI"><font size=2>Communication</font></font></span></b></p></td> <td style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BACKGROUND:#002060;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><b><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:white;"><font face="Segoe UI"><font size=2>Link Speed in Ovation Error Log</font></font></span></b></p></td> <td style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BACKGROUND:#002060;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><b><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:white;"><font face="Segoe UI"><font size=2>Comments</font></font></span></b></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>No message in Ovation Error Log</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>No message in Ovation Error Log</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" rowspan=5 width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Auto Negotiate</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>No message in Ovation Error Log</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>No message in Ovation Error Log</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>1Gb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" valign=bottom width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>No message in Ovation Error Log</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1.5pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" rowspan=4 width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Auto Negotiate</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>100 Mb Half Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Pass</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=211 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1.5pt solid;WIDTH:225.3pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=300 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font face="Segoe UI"><font size=2>Ovation Error Log displays 100Mbps full duplex</font></font></font></span></p></td></tr> <tr style="HEIGHT:14.25pt;"> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:103.8pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:windowtext 1.5pt solid;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=138 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;"><font face="Segoe UI"><font size=2>10 Mb Full Duplex</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:89.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width=119 nowrap=""> <p class=MsoNormal style="TEXT-ALIGN:center;MARGIN:0in 0in 0pt;LINE-HEIGHT:normal;" align=center><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:red;"><font face="Segoe UI"><font size=2>Fail</font></font></span></p></td> <td style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 1pt solid;WIDTH:158.55pt;BORDER-BOTTOM:windowtext 1pt solid;PADDING-BOTTOM:0in;PADDING-TOP:0in;PADDING-LEFT:5.4pt;BORDER-LEFT:#f0f0f0;PADDING-RIGHT:5.4pt;BACKGROUND-COLOR:transparent;" width |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kakroo, Tanisha EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | Ov3.5.0, Drop32/82 (Pilot module of OCR1100 G04) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <div><span style="font-size:12px;">This Finding should be closed. &nbsp;This is working as expected.</span></div><div><span style="font-size:12px;"><br></span></div><span style="font-size:12px;">The message shown in the Ovation Error Log reflects the current state\speed\duplex of the ethernet port. &nbsp;It does reflect the configured state. &nbsp; So if the port is configured for Auto-Negotiate, it will end up in any of the other modes, after the negotiation has taken place with the Ethernet Switch. &nbsp;</span><div style="font-size:12px;"><br></div><div style="font-size:12px;">Another way to test the controller when it is configured for Auto-Negotiate is to directly connect the port on the Controlller (i.e. N1) to a windows machine (i.e. a laptop) using a Crossover Cable. &nbsp;You can then change the Speed\Duplex on the windows machine and verify that the controller mode negotiates properly. &nbsp;See attachment &quot;mode.png&quot; for an example.</div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | OVA350-131-11092016065424 |  |  | FINDING | [6 empty] | 105880
38004 | FINDING | G04 OCR1100 : Login through Putty to G04 OCR1100 (drop32/drop82) giving "Access Denied" message | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-11-17 04:07 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-11-17 04:07 | 71678 |  |  | 2016-11-17 03:33 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-11-15 06:57 |  | <p>Putty is not allowing to login to controllers and giving &quot;Access denied&quot; (Refer screenshot Putty.jpg )message. This issue is observed with G04 OCR1100 Pilot and Prototype controller modules. However we are able to login through Putty&nbsp;to&nbsp;G01 OCR1100 type controller, same issue is observed with G04 OCR1100 controllers, both Pilot and Prototype modules in Ovation 3.5.1 also.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA350131/OVA351080 16 Nov |  | <p>Ov3.5.0</p><p>Ov3.5.1</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>fixed name of userid/pw callback function</p><p>SS</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.Open Putty and enter the hostname or IP of a G04 OCR1100 pilot type controller.</p><p>2.login as administrator</p><p>3.Enter password.</p><p>4.Press Enter.&nbsp;</p> |  | OVA350131/OVA350137 |  |  | FINDING | [6 empty] | 105448
38097 | FINDING | G04_CONTROLLER_SVTP_rev5.7_XX needs modification. | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-11-28 23:22 | [11 empty] | USPITTFSService | 2016-11-28 23:22 | [7 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-11-28 23:22 |  | <p>G04_CONTROLLER_SVTP_rev5.7_XX needs modification as below.</p><p><br></p><p><font face="Times New Roman" size=3> 1) </font><font face="Times New Roman" size=3>5.1.16.d,&nbsp; 5.1.16.e, 5.1.17.d, and &nbsp; 5.1.17.e, .-test cases of <span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">High Incremental Alarm, <span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">Low Incremental Alarm for Long and Deluxe digital and pack points are not applicable.</span></span></font></p><p><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">Hence to be removed or to&nbsp;be separated for analog and digital/packed points.&nbsp;</span></span></font></p><p><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">2) Test Notes in the test case -ie &quot;<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">By design, this feature is only in <u>OCR400</u> Controllers&quot;. On this note OCR 400 to be removed as this feature is applicable for both OCR400 &amp; OCR1100 .</span></span></span></font></p><p><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Test on OCR1100 is tested, verified &amp; passed the test case. (For the 1st time tester it confuses the tester.)</span></span></span></font></p><p><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><br></span></span></span></font></p><font face=Times><p><br></p><font size=3><p><br></p><p style="margin:0in 0in 0pt;"><br></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font></p></font><p style="margin:0in 0in 0pt;"></p></font><p style="margin:0in 0in 0pt;"></p><p><font face="Times New Roman" size=3> <br></font></p><br><br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | <p>G04 OCR1100 testing on Ov3.5.0</p> |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.5.0 |  |  | New Issue | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | SVTP to follow. |  | OVA350131 |  |  | FINDING | [6 empty] | 105808
43913 | FINDING | OVA350169: Post installing OVA350169, Controllers show 'Clear' state automatically and retains same state even after Download, Clear & Load operation | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 9 | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-04-30 22:16 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-04-30 22:16 |  |  |  | 2019-04-30 22:16 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-04-29 04:09 |  | <p>OVA350169: Post installing OVA350169, Controllers show 'Clear' state automatically and retains same state even after Download, Clear &amp; Load operation.</p><p><font face="Times New Roman" size=3> <font face=Calibri><font size=3>However Ovation error log reports <b>Load operation successful</b></font><font size=3> and Controller in </font><b><font size=3>control Matched condition</font></b><font size=3>. Also reports ‘</font><b><font size=3>Triggered Event Configuration file is found</font></b><font size=3>’.</font></font></font></p><p><font face=Calibri size=3>Actually, controller gets loaded and works like the one but in System viewer or Graphics reports 'Clear' state.</font></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  | Verify that the patch OVA360167 will not require a clear/load.<div>1) Uninstall OVA360167&nbsp;</div><div>2) Download/Clear-Reboot/Load</div><div>3) Verify the fields in Point Information for the Drop Status point record are non-zero &quot;DO&quot;, &quot;VN&quot;.</div><div>4) Install OVA360167&nbsp;</div><div>5) Download/Reboot (Do not clear/load)</div><div>6) Verify the fields in Point Information for the Drop Status point record are non-zero &quot;DO&quot;, &quot;VN&quot;.</div><div>7) Verify the drop does not indicate &quot;CLR&quot; in system viewer.</div> | 0 |  |  |  | <p>AR: 5/1/2019:</p><p>Verify that the patch OVA360167 will not require a clear/load.</p><div>1) Uninstall OVA360167&nbsp;</div><div>AR: Done.</div><div>2) Download/Clear-Reboot/Load</div><div>AR: Done</div><div>3) Verify the fields in Point Information for the Drop Status point record are non-zero &quot;DO&quot;, &quot;VN&quot;.</div><div>AR: DO &amp; VN fiels are non zero and snapshot is attached. Drop14_Dynamic.PNG</div><div>4) Install OVA360167&nbsp;</div><div>AR: Done.</div><div>5) Download/Reboot (Do not clear/load)</div><div>Ar: Done</div><div>6) Verify the fields in Point Information for the Drop Status point record are non-zero &quot;DO&quot;, &quot;VN&quot;.</div><div>AR: DO &amp; VN fiels are non zero and snapshot is attached.</div><div>7) Verify the drop does not indicate &quot;CLR&quot; in system viewer.</div><div>AR: No, it does not indicate CLR in system viewer snapshot attached, Drop14-64_Systemviewer.PNG.</div><div><br></div><div>Issue is resolved.</div> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Augustine, Lisa EMR SYSS PWS PITT |  |  |  |  | Implementation | OVA360167-30April2019 |  | <p>OV 3.5.0 Database server</p><p>OCR1100</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | Problem was in the controller patch OVA360167.<div><br></div><div>Corrected gni static data size calculation.</div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install the OVA350169.</p><p>2. Check the status in graphics/system viewer</p><p>3. Controller shows Clear state automatically.</p><p>4. Download, Clear &amp; Load the controller but still shows Clear status, but actually loaded.</p><p>5. Uninstall the patch and Download Clear Load, Controller becomes normal.</p> |  | OVA350167 |  |  | FINDING | [6 empty] | 141245
43914 | FINDING | OVA350167: Controller unable to send triggered Events to OPH scanner. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-05 21:35 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-05 21:35 |  |  |  | 2019-05-05 21:35 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-04-29 04:22 |  | <p>OVA350167: Controller unable to send triggered Events to OPH scanner.</p><p>After installing OVA350167 &amp; OVA350169,:</p><p><font face="Times New Roman" size=3> <br></font></p><ol type=1 style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="">Controller (OCR1100) works fine post installing OVA350167 and we are able to Download, Clear &amp; Load.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="">After installing OVA350169 (support of triggered events in developer studio), Controllers show <b>Clear state</b> automatically and retains same state even after Download, Clear &amp; Load operation.<font face="Times New Roman" size=3><font face="Times New Roman" size=3><font face=Calibri><font size=3>However Ovation error log reports <b>Load operation successful</b></font><font size=3> and Controller in </font><b><font size=3>control Matched condition</font></b><font size=3>. Also reports ‘</font><b><font size=3>Triggered Event Configuration file is found</font></b><font size=3>’. <span style=""><font face=Calibri size=3>Controller works like a loaded one and control logic executes perfectly (while showing CLR).<font face="Times New Roman"><span style=""><font face=Calibri size=3><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><font face="Times New Roman"><span style="">In Developer studio, we could get <b>Triggered Events</b> option and able to configure Triggered events, ‘Triggered Event Points’ &amp; Triggered event logger under controller.</span></font><p><font face="Times New Roman"><span style="">&gt;Downloaded, Clear &amp; loaded. Controllers keep showing CLR state in Graphics &amp; System Viewer.</span></font><font face="Times New Roman">&nbsp; </font></p></font></span></font></font></span></font></font></font></font></span></li></ol><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style=""><font face="Times New Roman" size=3><font face="Times New Roman" size=3><font face=Calibri><font size=3><span style=""><font face=Calibri size=3><font face="Times New Roman"><span style=""><font face=Calibri size=3><font face="Times New Roman"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&gt;Controller is not able to send Triggered events to the OPH scanner. Hence could not&nbsp;see events in&nbsp;Trend.</span><span style=""><font face=Calibri size=3><font face="Times New Roman"> </font></font></span></font></font></span></font></font></span></font></font></font></font></span></p><span style=""><font face="Times New Roman" size=3><font face="Times New Roman" size=3><font face=Calibri><font size=3><span style=""><font face=Calibri size=3><font face="Times New Roman"><span style=""><font face=Calibri size=3><font face="Times New Roman"><span style=""><font face=Calibri size=3><font face="Times New Roman"><p>SCAN_Data folder in OPH scanner <strong>D:/OvHist/Scan_data/</strong>....&nbsp;timestamp does not update with triggered Event, hence Events are not reaching to OPH scanner.</p><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"> <br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></span><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></span><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></span><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></font><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></span><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  | AR: 5/6/2019: With Patch OVA350167 (30thApr2019), Issue is resolved and OPH scanner is able to get events from controller. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | <p>OV 3.5.0 Database server</p><p>OCR1100</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install the OVA350167 &amp; OVA350169</p><p>2. Check the status in graphics/system viewer</p><p>3. Controller shows Clear state automatically.</p><p>4. Download, Clear &amp; Load the controller but still shows Clear status, but actually loaded.</p><p>5. Configure Triggered Events in Controller.</p><p>6. Configure Trigger Event logger.</p><p>7. Download Reboot Load/Download Clear Load.</p><p>8. triggered events are not sent to OPH scanner.</p><p>SCAN_Data folder in OPH scanner <strong>D:/OvHist/Scan_data/</strong>....&nbsp;timestamp does not update with triggered Event, hence Events are not reaching to OPH scanner.</p> |  | OVA350167 |  |  | FINDING | [6 empty] | 141465
43996 | FINDING | OVA350167: DATA files produced due to Triggered events do not have correct size, hence Trend Application is not able to read | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-13 08:22 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-13 08:22 |  |  |  | 2019-05-13 08:22 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-09 07:37 |  | <p>OVA350167: DATA files produced due to Triggered events do not have correct size, hence Trend Application is not able to read</p><p>Triggered events are generated and able to browse the same in Trend application.</p><p>Event Trend application is unable to generate graphs for the same due to incorrect data size of the triggered event data files.&nbsp;</p><p>Data size conclusion is defined by Trend developer as there is no problem seems to be on trend side.</p> |  |  |  |  | 0 |  |  |  | <p>AR: 5/13/2019&gt; C<span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">ontroller was configured with the same drop for Triggered Event Scanner 1 &amp; 2.&nbsp; </span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">This might have been causing a problem, since it makes the controller send the same event to the scanner 2 times.</span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">After Configuring Event Trigger logger 1 only, problem resolved.</span></p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Bargaje, Prashant C EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT |  |  |  |  | Implementation |  |  | <p>Ovation 3.5.0 </p><p>OCR1100</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | User Error | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Generate Triggered Events and launch the event trend</p><p>2. Browse the Events generated.</p><p>3. Launch the event&nbsp;trend for the triggered event.</p><p>4. Graph is not available on Trend.</p> |  | OVA350167 |  |  | FINDING | [6 empty] | 141706
44020 | FINDING | Ov 3.5.0: Same Event scanner should not be configured as Triggered Event Logger 1 & 2 and back to back Triggering causing some data distortion in Event graphs. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2019-05-15 22:26 | [11 empty] | USPITTFSService | 2019-05-15 22:26 | [7 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-15 22:26 |  | <p>Ov 3.5.0: Same Event scanner should not be configured as Triggered Event Logger 1 &amp; 2 and back to back Triggering causing some data distortion in Event graphs.</p><p>If configuring same drop for Triggered Event logger 1 &amp; 2,&nbsp; data files&nbsp; size become inappropriate for the Event trend application to read. since it makes the controller send the same event to the scanner 2 times.</p><p>Event trend shows the configuration of the Triggered events but not the graph for which Large size of data file is responsible.</p><p>Please refer snapshot Graphless_Event Trend.jpg</p><p><br></p><p>To avoid this discrepancy, there can be additional check in controller to&nbsp;prevent sending same event file to&nbsp;scanner&nbsp;if already sent one.</p><p>This additional check may avoid issues occurring after setting same scanner for both Event loggers.</p><p>Secondly,</p><p>when triggered events are made to trigger continuously (back to back), there is some distortion in Event trend graphs. Please refer <strong>Triggered Events_Recurring2.PNG</strong> &amp; <strong>Triggered Events_Recurring.PNG. </strong>If the Triggered event is triggered and reset, Event trend graph is fine but as soon as the triggered events happening every 3 minutes, we get some plane Graphs for the event trend variables.</p><p><strong>This finding will be converted into SDR once OVA350167 will be released.</strong></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Bargaje, Prashant C EMR SYSS PWS PITT |  |  |  | Implementation |  |  | Ovation3.5.0 with OVA350167&nbsp; OVA350168 &amp; OVA350169 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.5.0 |  |  | New Issue | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Configure same scanner for both the triggered Event loggers.</p><p>Generate Triggered Events.</p><p>See the Graph for triggered event variables.</p><p>for second issue,</p><p>Put the Triggering Point Set and see the events trend after every 3 mins.</p> |  | OVA350167 |  |  | FINDING | [6 empty] | 141826
44085 | FINDING | OVA350168: Configured 'Display' attributes of Triggered Event points in developer studio does not reflect in Trend application | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-22 07:03 | [8 empty] | FALSE |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-22 07:03 |  |  |  | 2019-05-22 07:03 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2019-05-22 00:57 |  | <p>OVA350168: Configured 'Display' attributes of Triggered Event points does not reflect in Trend application.</p><p>When Display attributes are configured in developer studio, for e.g. under Display:</p><p>Selection of <strong>'Display Pane'</strong> &amp; <strong>'Display Quadrant'</strong> in developer studio and applying the&nbsp;same following with Controller Download, Clear &amp; Load operation.</p><p>when verifying this functionality in Trend, we do not see its reflection in Event Trend Graph as we see in Ovation3.6.0 and later releases.</p><p><strong>Event Trend shows only&nbsp;Default pane and Quadrant even after configuring in develop studio</strong>.</p><p>Event trend graph does not comply with configuration in developer studio.</p><p>we get few indications in Pane and preceding the Event point name. Please refer attachments:</p> |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | <p>Ovation 3.5.0</p><p>OVA350168</p><p>Operator station and Database server</p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.5.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure Attributes of the Event point names under Triggered events of a Controller in developer studio.</p><p>2. Download Clear Load controller</p><p>3. Trigger an event.</p><p>4. See the Event trend in Trend application.</p><p>5. Event trend graph does not comply with configuration in developer studio</p><p><br></p> |  | OVA350168 |  |  | FINDING | [6 empty] | 142120

## Ovation 3.6.0
ID | Work Item Type | Title | Assigned To | State | Tags | Acceptance Criteria | Accepted By | Accepted Date | Activated By | Activated Date | Activity | Application Launch Instructions | Application Start Information | Application Type | Area ID | Area Path | Associated Context | Associated Context Code | Associated Context Owner | Associated Context Type | Attached File Count | Authorized As | Authorized Date | Automated Test Id | Automated Test Name | Automated Test Storage | Automated Test Type | Automation status | Backlog Priority | Blocked | Board Column | Board Column Done | Board Lane | Business Value | Changed By | Changed Date | Changeset | ChangeSet Number | Closed By | Closed Date | Closed Status | Closed Status Code | Closing Comment | Created By | Created Date | Created from FINDING | Description | DIR Information | Documentation Requirements | Effort | Emerson Affected Areas | External Link Count | Finish Date | Fix Released Date | Found In | History | Hyperlink Count | Integration Build | INTERNAL AssignedHierarchyPath | Internal Resolution | Issue | Iteration ID | Iteration Path | Legacy System Number | Local Data Source | Node Name | Notify User 1 | Notify User 2 | Notify User 3 | Notify User 4 | Notify User 5 | Notify User 6 | Notify User 7 | Notify User 8 | Parameters | Parent Hierarchy Path | Phase | Planned Release | Planned Release Date | Platform | Priority | Product | Product Category | Product Component | Product Problem Type | Product State | Product Version | Query Text | Rating | Reason | Related Link Count | Released In | Remaining Work | Reported By | Reporting Source | Repro Steps | Resolution | Rev | Reviewed By | Revised Date | Severity | SME Assigned To | Start Date | State Change Date | State Code | Steps | Steps to Reproduce | Submitting Organization | Subrelease | System Info | Target Date | Team Project | Test Suite Audit | Test Suite Type | Test Suite Type Id | TPNF Number | Validation Date | Validator | Watermark
28464 | FINDING | PWSIT - Fieldbus device alert does not report consistently on all FF devices | Pratley, Bob EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Costlow, Kim EMR SYSS PWS PITT | 2019-02-08 08:18 | [8 empty] | FALSE |  |  | Costlow, Kim EMR SYSS PWS PITT | 2019-02-08 08:18 | [7 empty] | USPITTFSService | 2015-06-12 04:01 |  | <p>QP =&gt; 10/12/2018</p><p>Update </p><p>AMS from 13.5 to 14.0.&nbsp; </p><p>Also update OPC OPC_AES_2.0_U0_11172015_CD to OPC_AES_2.0_05022016</p><p>Issue still exist.</p><p><br></p><p>QP =&gt; 9/20/2018</p><p>Same issue observed on Ovation 3.6 with FP4 and all patched support OCC100 controller.&nbsp; AMS 13.5.000.057&nbsp; See attached email</p><p><br></p><p>QP =&gt; 3/21/2018</p><p>Update issue for latest test on Ovation 3.6.0 with FP3, both device on regular branch on also on Remote Network Interface.</p><p>Sensor failure alert from Rosemount 644 Rev1:</p><p>- Alarm System (YES)</p><p>- Alert Monitor (NO)</p><p>- Device Manager Dashboard (YES)</p><p><br></p><p>Sensor failure alert from Rosemount 848T Rev 7 and 8:</p><p>- Alarm System (NO)</p><p>- Alert Monitor (NO)</p><p>- Device Manager Dashboard (YES)</p><p>======================================================</p><p>When simuldate PlantWeb alert on several different FF devices, note that alert from some devices came in consistently in Ovation Alarm System and AMS Alert Montior and some do not.<br>On some devices, download a port/device in FET will allow alert to come in but then it won&quot;t update after another alert is simulated.<br><br>PWSIT did a quick evaluation on devices available.<br><br>Devices that consistently come in w/o port/device download requirement in FET are:<br>Rosemount 3144 Rev2, 644 Rev1, 848T Rev5, 3095 Rev1<br>CSI 9210 Rev3<br>Valve Automation D3AO<br><br>Devices with alert that do not came in are:<br>Rosemount 752 Rev3, 3051 R23 (both Hornet and Mcore), 5300 Rev2, <br>Fisher Control DLC 3020 Rev1, DVC6000 Rev1, DVC6001 Rev2 (Phan, Quang Feb 4, 2011)</p> |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 2/7/11 - we entered this finding to track this issue as we investigate further on the Validation side. The AMS folks have also reported these types of issues with Ff alerts. Not sure if a problem exists or if its related to configuration/user error. (Capani, Nooch Feb 7, 2011) <br> |  | 35 | FINDING | 7334 |  | FINDING | Plymire, Alvan AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | Pratley, Bob EMR SYSS PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:8pt;">FP3, + patches + configurations</span> |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | OVA360FP4 |  |  | FINDING | [6 empty] | 138197
31106 | FINDING | PWTTS - FFISELX block from Rosemount 3051 Rev 20 shown incorrect calculation | Pratley, Bob EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 9 | Phan, Quang EMR ENT TECH AUS | 2018-03-23 12:55 | [8 empty] | FALSE |  |  | Phan, Quang EMR ENT TECH AUS | 2018-03-23 12:55 |  |  |  | 2015-06-12 04:06 |  |  |  | USPITTFSService | 2015-06-12 04:06 |  | <p>QP =&gt; Update 3/23/2018</p><p>Retest for Remote Network Interface with FP3.&nbsp; These function blocks still not calculate correctly.&nbsp; See attached for sample from RA 1066 Rev 1 and RM 2088 Rev 1.</p><p><br></p><p>Calculation on FFISELX from 3051 device shows incorrect calculation doesn&quot;t matter what calculation type selected (average, first good, max, min or middle). <br>Other FFISELX block from other devices on the same segment work as expected.<br>See attached screenshots for details.<br><br>Steps to reproduce:<br>Commission several devices on the same segment included a 3051 Rev 20 device.<br>Create a control sheet as show in attached example. (Phan, Quang Aug 2, 2013)<br><br>Note that FFISELX from DVC6000 initially calculated correctly. However, after some configuration was done on other blocks on the same segment and port download/controller load perform, output on this block return a bad calculation. (Phan, Quang Aug 5, 2013)</p><p><br></p><p>Reopen this issue for 3.6.0 Build U4.&nbsp; Configured same block from 4 different devices and all have wrong calculation.&nbsp; See attached email for detail.</p> |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | IC 8/6/13 mtg - alg item assign to Bob P. (Capani, Nooch Aug 6, 2013)<br><br>The Rosemount 3051 uses the FFISEL Ovation algorithm, not the FFISELX algorithm. In image ffisel.png it can be seen that the Ovation Developer&quot;s Studio indicates that the algorithm is FFISEL rather than FFISELX. Image sig-dgm.png is a fragment of a signal diagram showing the FFISEL Ovation algorithm working correctly with a Rosemount 3051. (Pratley, Bob Jun 30, 2014) <br> Retest using 2 different Rosemount 3051 Rev 23 devices. Configure device 1 using ISEL and device 2 using ISELX. Both have the same input and select type &quot;Average&quot;. Observed that block from both devices show good value and status in tuning window. However, on signal diagram, device 1 shown Unknown status and device 2 shown Good status but with wrong calculation. Please see attached &quot;ISEL retest.jpg&quot; for details. (Phan, Quang Jul 18, 2014)<br><br>Add attachment that shows block from 4 different device also has wrong calculation (Phan, Quang Jul 28, 2014) |  | 35 | FINDING | 9986 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | Plymire, Alvan AUTOSOL PWS PITT | [6 empty] | Implementation |  |  | <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:8pt;">FP3, + patches + configurations</span> |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Failed Retest | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | OVA360FP3 |  |  | FINDING | [6 empty] | 125821
31451 | FINDING | OSV -&gt R/C expand all takes more than 1minute on 1st instance. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-02-18 05:36 | [8 empty] | FALSE |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-02-18 05:36 | 65217 |  |  | 2016-02-18 05:36 |  |  |  | USPITTFSService | 2015-06-12 04:07 |  | With the new inclusion of Network details in hierarchy, when 1st time the application is opened and Unit is selected or right click Expand All is performed, it takes more than 1minute, approx 66seconds to open up. (Sachan, Pallavi Oct 31, 2013) |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Right now the attributes for the drops are read in one time.<br> They are read the first time a drop is exposed in the hierarchy.<br> There are a lot of start and stop processes that go on each time a drop is read in.<br><br>I am proposing a change in the next major release but not for 3.5.1. (Wozniak, Diane M. Nov 7, 2013)<br><br>If you propose to change this in next release, kindly change the ACTION field from WAD to MNR. Thanks! (Sachan, Pallavi Dec 12, 2013) <br> IC 2/14/14 &gt; MNR, if speed can&quot;t be improved, perhaps a message to indicate &quot;in progress&quot; can be considred. (Capani, Nooch Feb 14, 2014) |  | 35 | FINDING | 10331 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | PS18FEB16: It is observed that now in 3.6.0_U3, whenever the application is opened and Unit is selected or right click Expand All is performed, it is very fast approximately 8-10seconds. The issue is found fixed. Hence finding is closed.&nbsp; | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U2 |  |  | FINDING | [6 empty] | 92427
31767 | FINDING | OSV, the hierarchy freezes if the application is kept open under monitoring for long period. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:04 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:04 | 65217 |  |  | 2016-05-16 04:04 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | OSV, the hierarchy freezes if the application is kept open under monitoring for long period.<br>Previously it was observed only on Mid-tier PC hence kept under observation. But now this scenario is seen on DBS as well as EWS.<br>Kindly find attached &quot;OSV frozen hierarchy.jpeg&quot; for your review. (Sachan, Pallavi Dec 27, 2013)<br><br>1&gt;How long does it take to lock up?<br>2&gt;Have controllers been loaded while the system viewer was dormant?<br>3&gt;Are you positive there was not another dialog box demanding attention while the viewer was non-responsive?<br>4&gt;In the task manager, is the process busy and how much memory is it using?<br>5&gt;Is this the only program that became non-responsive (was PI still working?)?<br>- (Wozniak, Diane M. Jan 8, 2014)<br><br>In order to revert sequencially, i have numbered your queries, replies are as below:<br>1&gt; This was observed after 3-4 hrs.<br>2&gt; During this duration, the controllers are loaded, downloaded, and all operartions are performed by other users.<br>3&gt; Yes, I am sure there were no other dialog boxes demanding attention. Even another instance of OSV could be opened and operated successfully.<br>4&gt; No the task manager doesn&quot;t show being busy, no irregular CPU utilisation is observed as such.<br>5&gt; Yes, all the other applications are working fine, even in OSV, we could perform search, see details from the drop down summary. But the hierarchy pane is freezed. (Sachan, Pallavi Jan 13, 2014)<br><br>Is this a recreateable situation? Have you seen it more than once? If I can figure out how to recreate it, I can debug it. (Wozniak, Diane M. Jan 13, 2014)<br>I noticed on the .jpg that the icon beside IVALNET1 is not the alarm bell. it is the default icon. Can you tell me if that icon was ever the alarm bell before it froze? (Wozniak, Diane M. Jan 13, 2014)<br>Do you think this could be releated to a drop load? When the drops were being loaded, did the program read in the new files? Did it come up with the reload or automatic reload will occur message box? (Wozniak, Diane M. Jan 13, 2014)<br><br>Yes, we have observed it more than once. <br>After the hierarchy pane is found stuck, and we click on the available level of hierarchy, the alarm bell goes off and the icon seen in jpeg is seen on OSV window.<br>Every time someone loads the drop the Reload window occurs.<br>I guess that it could be during multiple drop loads. (We have multiple users using the controller and at times many configuration changes related to IOs take place, as of whole day today I have kept the OSV window under observation on 3-4 EWS, the pane is not observed to be freezed.) (Sachan, Pallavi Jan 14, 2014)<br><br>The next time it freezes, please let me know and do not reboot. <br>I need to be able to recreate this problem. Please let me know if you find <br>the steps to make this happen. (Wozniak, Diane M. Jan 14, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | Finally, the scenario is re-created on Net#9, Drop230. Kindly find the attached remote login details. (Sachan, Pallavi Feb 12, 2014)<br><br>Thank you for the login instructions. I was able to remote log into the drop and see the freeze. Unfortunately, I was not able to gather any additional information by looking at the problem directly. Until I can recreate the problem, I cannot fix it. I can only guess that it has to do with reloading the drops or changing the assets while the program is running. There is nothing more I can do right now for this finding. (Wozniak, Diane M. Feb 13, 2014)<br><br>right now I am assuming that a reload is causing this problem. This is a huge assumption. If you could let me know what the systemviewer looked like before the freeze and after the freeze, that would help me too. Do you know if the tree was expanded? what was displayed on the other tabs? (Wozniak, Diane M. Feb 13, 2014) <br> |  | 35 | FINDING | 10647 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font color="#000000">PS 15May16:&nbsp;Monitored the issue&nbsp;from U4 to&nbsp;U7 builds and issue is no more seen&nbsp;. Hence Finding is Closed.</font></span></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U2 |  |  | FINDING | [6 empty] | 96876
31961 | FINDING | OSV does not log events for fieldbus mode changes. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:35 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:35 | # |  |  | 2017-02-16 15:35 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | As a fix to F#10712, now OSV allows the change in FieldBus modes. But the proper mode change events are not logged.<br>However if there is failure in mode changes, those are logged in properly. Kindly find attached &quot;OSV-eventlogging for Mode change.jpeg&quot; for reference. (Sachan, Pallavi Feb 13, 2014) |  |  |  |  | 0 |  |  |  | IC 2/16/17&gt; entered SDR #38706 to track this issue, closed finding. | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10841 |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>PS: 24Feb16:&quot;<a class=caption href="https://uspit-tfs-v.emrsn.org/tfs/Quality/FINDING/_workitems/edit/35680">FINDING 35680:</a><span class=info-text>Fieldbus does not work in U3&quot; is written. Waiting for Field Bus support in Ov3.6.0 to verify this finding.</span></p> <p><span class=info-text></span>&nbsp;</p> <p><span class=info-text>PS 18Apr16: OSV allows the change in FieldBus modes as reported earlier. But the mode change events are not logged. The mode changes as AUTO/MAN/CAS, but the same is reported in Operator Event as &quot;Mode Change &lt;Failed&gt;&quot;. </span></p> <p><span class=info-text>Kindly find attached &quot;F31961-360_U6-OSV.jpeg&quot; for reference. Hence Finding State is changed to Open Failed Retest.</span></p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U2 |  |  | FINDING | [6 empty] | 108975
32097 | FINDING | The GE Genius task is stopping after the OCR boots. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 09:12 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 09:12 |  |  |  | 2016-06-08 09:12 |  |  |  | USPITTFSService | 2015-06-12 04:08 |  | OCR400 Controller 44/94 (EMILY) is configured with a GE Genius IO device. After bootup the following messages appear in the Ovation Error Log:<br>0x442b610 (ge_genius5): task 0x442b610 has had a failure and has been stopped.<br>0x442b610 (ge_genius5): fatal kernel task-level exception!<br><br>This began to occur after the point count in the OCR was increased from about 6,000 to about 30,000. (Brown, Sean Mar 11, 2014)<br><br>The OCR400 has a G02 CPU. (Brown, Sean Mar 11, 2014) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <br> |  | 35 | FINDING | 10977 |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation | SDR |  | IC 3/21/16 &gt; Originally reported against 3.5.1 (see Description). <br>Since it was never addressed, I've updated the version to&nbsp;3.6.0 and the Resp Eng to Greg.<br>IC 6/8/16&gt; closed finding, added to DIR, track as SDR 36739. |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | Confirmed problem appears to be parsing a null string in the &quot;TT Field&quot;. &nbsp;However GE Genius interface may approaching end of support, we will address this if and only if a customer requires it. | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 98404
33589 | FINDING | Ovation SIS Charms IO device type and Charms IO type are not updating in SRU and controller diagnostics. | Buzza, Sheri AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 15:50 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 15:50 |  |  |  | 2016-06-07 15:50 |  |  |  | USPITTFSService | 2015-06-12 04:12 |  | <p>In system registration utility,<br>Ovation 3.5.2 does not provide its SIS Charms (IO device and Charms IO type) detail to system registration utility. <br>Test case 5.2.1 and test case 5.2.2 mentioned in SVTP can not be tested. (Pandey, Vijay May 1, 2015)</p><p><br></p><p>IC 4/8/16&gt; issue exists in 3.6.0_U4 as well. Moved finding to 3.6.0 release since we are not fixing 3.5.2 findings. <br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | 5/22 Val+Dev mtg&gt; Mikolaj needs to make info available for SRU. (Capani, Nooch May 27, 2015) <br> |  | 35 | FINDING | 12469 |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Edward M EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | GEC Val Lab: Ov3.5.2+ SIS Charms controller drop27/77, DBS drop 250 |  | Ovation for Windows | Ovation | System Registration Utility | Software | In Validation | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>Retested in U9, no SIS charms info available&nbsp;in SRU.&nbsp;Finding is in Open (Failed Retest) state. For reference, SRU report is attached.<br><br>IC 6/7/16&gt; added note to DIR, closed Finding, track as SDR 36733. </p> | 14 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U4 |  |  | FINDING | [6 empty] | 98361
34447 | FINDING | Sync Opp List Generates Errno 22 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-01-04 08:31 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-01-04 08:31 |  |  |  | 2016-01-04 08:31 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2015-08-31 09:04 |  | <font size=2><p>Coming from:<p>opp_sync_opplist.c: <p>&nbsp;</p><font size=2><p>fprintf(stderr, </p></font><p><font color="#2a00ff" size=2><font color="#2a00ff" size=2>&quot;write(%s) of header failed, errno %d\n&quot;</font></font><font size=2>, orig_ptlist_file, errnoGet());</font></p><font size=2></font></font><p><font size=2></font>&nbsp;</p><p><font size=2></font>&nbsp;</p><p><font size=2></font>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 0 |  |  | FINDING | [6 empty] | 90400
34614 | FINDING | Ovation Graphics is crashing on performing: "Alarm Check on/off, Limit Check off/on and Scan on/off" Point Operations | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-02-24 00:27 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-02-24 00:27 | 63917 |  |  | 2016-02-24 00:27 |  |  |  | Nalwa, Varun AUTOSOL PWS NOIDA | 2015-09-23 23:44 |  | <p>The Ovation Graphics Application is crashing on performing the following point operations :</p><p>Alarm Check on/off, </p><p>Limit Check off/on and </p><p>Scan on/off</p><p>The graphics window crashes while performing these operations by right clicking on the process point.</p><p>However the same operations can be performed on the same points using Point information.</p><p>Please refer to the attached screenshots.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  | OV3.6.0 + Ovation Graphics |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Nalwa, Varun AUTOSOL PWS NOIDA | Validation |  | <p>Change to account for the increase of the ED field to 50 characters.</p><p><br></p><p>MS : Checked in U3 ( Performed steps mentioned in Steps to Reproduce), issue is fixed.</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; I am closing this finding.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Step 1: In the GBNT add an Analog point of a controller to the graphic using &quot;process point&quot;.</p><p>Step 2: Save &amp; compile the graphic and Download the Workstation drop.</p><p>Step 3: From the Workstation drop Open the Graphics Application and load the same graphic (modified in step1) --&gt; right click on the point --&gt; Select Point Operation --&gt; Click Alarm Check ON/OFF. </p><p>Graphics window will crash.</p><p>Application crash was also observed for Limit Check off/on and Scan on/off by performing the same steps.</p> |  | P0 |  |  | FINDING | [6 empty] | 92672
34635 | FINDING | Error appeared when it is tried to add any IO module at slot | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 |  |  |  | 2015-10-21 05:20 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-09-28 04:02 |  | Pkt conversion error appeared when it is tried to add any IO module at slot. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | WS12-R2 and WIN7 SP1&nbsp; |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>Already addressed&nbsp;in the next 3.6.0 update.&nbsp; Most Engineering Tools support had not been added to Ovation 3.6.0 at the time the software was initially released to Validation.</p><p><br></p><p>MS : Checked in U0 ,issue is fixed. I am closing this finding.&nbsp;</p> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Open the Developer's studio</p><p>2. Go to System&gt;Network&gt;Unit&gt;Drop(xx)&gt;IO device&gt;Branch&gt;Slot</p><p>3. Expand slot&nbsp;and&nbsp;Right click on&nbsp;Ovation Module and select insert new, error appeared &quot;Pkt conversion error&quot;</p><p>&nbsp;( please refer attached snapshot)</p><p>&nbsp;</p> |  | P0 |  |  | FINDING | [6 empty] | 87501
34644 | FINDING | Unable to launch Controller Diagnostics Application | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-23 03:59 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-23 03:59 | 63830 |  |  | 2015-10-23 03:59 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2015-09-29 04:09 |  | Unable to launch controller diagnostics application. (as it is unable find&nbsp;diagnostics.exe) |  |  |  | Launch Controller Diagnostics. Confirm no error messages appear.<div><br></div><div>SHS 10/23/2015&gt; Able to launch Controller Diagnostics. Finding fixed in U0 (Though a pop up appears stating help is disabled)</div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software | <p>Controller Diagnostics 3.6.0 code and projects ported&nbsp;to Qt 5.4.0</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [7 empty] | Implementation | 3.6.0_U0 |  | 3.6.0 P0 |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | Controller Diagnostics is now included in 3.6.0 | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Steps:<div>1. Launch Controller diagnostics from start menu &gt; Ovation&gt; Ovation Utilities ( from EWS or DBS).</div><div>2. An error pop up appears stating it is unable to find diagnostics.exe.</div><div><br></div><div>Observation:</div><div>1. Controller Diagnostics should launch without error. Also it was found that diagnostics.exe was not present at Ovation&gt; OvationBase&nbsp;</div><div><br></div><div>Please refer attached&nbsp;<i>Controller_Diagonistic.jpg</i></div> |  | P0 |  |  | FINDING | [6 empty] | 87220
34645 | FINDING | System Viewer crashes after launching giving an unhandled exception error | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Wozniak, Diane M EMR SYSS PWS PITT | 2016-01-07 07:24 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2016-01-07 07:24 | 65217 |  |  | 2016-01-07 06:30 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2015-09-29 04:33 |  | <p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">&nbsp;System Viewer application crashes within 60-90 seconds (approx.) after launching &amp; its giving an unhandled exception error.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">comments for the 3.6.0 release:</span></p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><font color=black face=Calibri size=2><span style="color:black;font-size:11pt;">The problem was that there were NO drop*.* files under c:\ovation\mmi\systemviewer.</span></font></p><p><font face="Times New Roman" size=3> </font><font color=black face=Calibri size=2><span style="color:black;font-size:11pt;">If there are no drop*.* files under this directory, the program will display an error message and terminate.</span></font></p><p><font face="Times New Roman" size=3> <br></font></p><p><font face="Times New Roman" size=3>this change was put in the build around 12/16/15. previous versions did not have the fix. </font></p><p><font face="Times New Roman" size=3>please let me know if you are testing a build that was made after 12/16/15.</font><font face="Times New Roman" size=3><br></font></p></span><p><br></p> |  |  |  | <div>SHS 01/07/2016&gt; Able to launch System Viewer and no unhandled exception error appears. Finding fixed in U2.<br></div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; The problem was that there were NO drop*.* files under c:\ovation\mmi\systemviewer.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=3>&nbsp; &nbsp;&nbsp;&nbsp;If there are no drop*.* files under this directory, the program will display an error message and terminate.</font></span></p><font face="Times New Roman" size=3> </font> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U2 |  | 3.6.0 P0 |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Steps:<div>1. Launch System Viewer from start menu &gt; Ovation&gt; Ovation Application ( from EWS or DBS).</div><div>2. System Viewer Launches.</div><div>3. After sometimes (60-90 seconds) unhandled exception error appears.</div><div>&nbsp;(Please refer attached screenshot).</div><div>4. Upon clicking the continue button of error , same error message appears.</div> |  | P0 |  |  | FINDING | [6 empty] | 90640
34646 | FINDING | Initializing window appearing after launching Ovation Developer Studio displays Ovation version as 3.5.2 | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-26 05:57 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-26 05:57 |  |  |  | 2015-10-26 05:57 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2015-09-29 04:55 |  | Initializing window appearing after launching Ovation Developer Studio displays Ovation version as 3.5.2 |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | 3.6.0 P0. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | Already addressed in the next 3.6.0 update. Most Engineering Tools support had not been added to Ovation 3.6.0 at the time the software was initially released to Validation.<div><br></div><div>SHS 10/26/2015&gt; Ovation version is not appearing as 3.5.2, but&nbsp;<span style="line-height:18px;">Number 3.6.0.64021 is displayed instead of 3.6.0 (For this&nbsp;separate&nbsp; finding (Finding 34745) has been raised)&nbsp;</span><br></div> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Steps:<br>1. Launch Ovation Developer Studio.<div>2. Initializing window of Ovation Developer studio displays Ovation version as 3.5.2.</div><div>(Please refer to attached screenshot)</div><div><br></div><div>Observation:</div><div>1. Ovation Version should be 3.6.0</div> |  | P0 |  |  | FINDING | [6 empty] | 87311
34647 | FINDING | VxWorks file is missing in VCH machine on Ov3.6.0 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-04 21:45 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-04 21:45 | 63755 |  |  | 2015-11-04 21:45 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-09-29 05:47 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>It is noticed that VxWorks file is missing in “OvationVirtual” directory of VCH machine on Ov3.6.0.</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | <p><a href="https://uspit-tfs-v.emrsn.org/tfs/Products/Ovation/_versionControl/changeset/63755">https://uspit-tfs-v.emrsn.org/tfs/Products/Ovation/_versionControl/changeset/63755</a></p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | U0 |  | <p>OS: Win7 SP1 64b</p><p>Ovation Version: 3.6.0_P0</p><p>Machine Name: Drop154 (VCH)</p> |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>kernel project for ss_rpc version of vxsim changed names to simpc as opposed to vxsim.</p><p><br></p><p>YJ (11/04/2015):&nbsp; VxWorks file is available in U0 but unable to download VC.</p><p>VC console log is attached which is gathered by running VC through VCOORDINATOR -r command via Command prompt (Not through vcoordinator service).</p><p>However we are able to ping VxSim Controllers, but unable to download.</p><p><br></p><p>IC per 11/3/15 Mtg : Yukta, if original issue is resolved, close original finding and open a new one to report the download problem. Thx!</p><p>IC 11/4/15&gt; Yukta, I just noticed that F#34859 already exists for the VC download issue. No need for a new finding.</p><p>YJ: OK Nooch, since the file is available, I am closing this finding</p> | 10 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;">1. Configure VCH on Drop154 (W7 SP1 64bit) as per document-OW352_57 (section 4).</p><p style="margin:0in 0in 10pt;">2. Open VxSim.exe placed at C:\Ovation\OvationVirtual and License file.</p><p style="margin:0in 0in 10pt;">3. After clicking “Finish Button”, a text file with information – “Cannot find C:\Ovation\OvationVirtual\VxWorks. Simulator Stopped” appeared.<span style="">&nbsp; </span>Please find the attached snapshot.</p><p style="margin:0in 0in 10pt;">Remote login details are also attached. </p><font face="Times New Roman" size=3> </font> |  | P0 |  |  | FINDING | [6 empty] | 87927
34648 | FINDING | Not able to configure OCR400 in Ovation 3.6.0_P0 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-10-27 06:07 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-10-27 06:07 |  |  |  | 2015-10-27 06:07 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-09-29 05:58 |  | Not able to configure&nbsp; OCR400 in Ovation 3.6.0_P0 |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>Ovation 3.6.0_P0 </p> |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | MS : Checked in U0 ,issue&nbsp;not found. OCR 400 was configured successfully. I am closing this finding.&nbsp; | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Configure OCR 400 as drop&nbsp;in39/89 in Developer's studio.</p><p>2. Inserted the cleared flash in drop39 &amp; reboot the drop.</p><p>3. In Ovation error log message appears &quot;RFC 1048 style reply<span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">&quot;,&nbsp;<font color="#000000">So not&nbsp;able to download the drop from studio.</font></span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000">&nbsp; ( please refer attached snapshot)</font></span></p> |  | P0 |  |  | FINDING | [6 empty] | 87428
34649 | FINDING | Exception error appeared during installation of Ovation Security Server | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 02:36 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 02:36 |  |  |  | 2015-11-25 02:36 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-09-29 06:50 |  | <p>&quot;Win 32 :Exception System can not find file specified&quot;&nbsp;error appeared during installation of Ovation Security Server.</p><p>Irrespective of the error set up completed &amp;&nbsp;Security Manager is opening without any issue.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | <p>Ovation&nbsp; : Ovation 3.6.0_P0</p><p>OS : WS12-R2</p><p>Hardware : Dell T320</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | MS : Checked in U1. Issue is fixed. Exception error not observed while installing Security&nbsp; Server.&nbsp;&nbsp;I am closing this finding. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install WS12_R2 (OS) &amp; configure&nbsp;active directory as per manual OW352_10 on drop103.</p><p>2.&nbsp;During installing Ovation&nbsp;Security Server ( as per section 6.3)&nbsp;on drop103 (after step 6.3.1.13) error appeared</p><p>&nbsp; &nbsp;&nbsp;&quot;Win 32 :Exception System can not find file specified&quot;&nbsp; (please refer attached snapshot)</p><p>3. On clicking &quot;OK&quot; button Finish screen appeared with Reboot prompt and after rebooting resuming setup appeared ( again step 6.3.1.13).</p><p>4. After Clicking &quot;Next&quot; set up wizard appeared with &quot;Finish&quot; option&nbsp;&amp; set up completed.</p><p><br></p><p>Note : &nbsp;Irrespective of the error set up completed &amp;&nbsp;Security Manager is opening without any issue.</p><p>&nbsp;</p> |  | P0 |  |  | FINDING | [6 empty] | 88883
34736 | FINDING | In NCV, "Char w" and "EU char w" are not working properly. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-03-28 02:00 | [11 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-03-28 02:00 | 64149 |  |  | 2016-03-28 02:00 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2015-10-15 05:57 |  | In NCV(Numeric Current Value), &quot;Char w&quot; and &quot;EU char w&quot; are not working properly. | Fixed a bug that caused very,very small NCV and NCV EU char widths (8 or 9 virtual pixels) to display larger than widths of 1-7 virtual pixels. Note that 8,9, 1-7 should all display as illegible! Now they all do as all will now map to 1 screen pixel charw!! |  |  | Very small virtual font widths should be illegible. Font charw of 8 or 9 should never look&nbsp;more illegible than a font charw of&nbsp;1-7. | 0 |  |  |  | <p>GA:-</p><p>Date:- 3/28/2016</p><p>Used Build:- Ov 3.6.0_U4</p><p><br></p><p>Issue has been resolved. Hence Finding is closed.</p> | 0 |  | Ovation for Windows/Operator Station/Graphics/Software | <p>IC 10/20/15&gt; per Patch Mtg : move to next release (3.6.0)</p><p><br></p><p>klj. When converting virtual charw to pixels, small numbers can become 0. When a 0 is passed to the Windows font routine[CreateFont()], it has a special meaning (means use a default width as opposed to 0). To prevent this, never pass a 0 to CreateFont() - always make it a 1 if it is 0 after converting virtuals to pixels! This is what we&nbsp;always have done&nbsp;for font height. Don't know why we didn't do it for font w also - maybe CreateFont() changed at some point, maybe just didn't realize that CreateFont() worked that way for the font charw also?!</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0u4 |  | <p>OV:- Ov 3.5.1</p><p>Used Patch:- OVA351-040-10142015142029</p> |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | <p>When converting virtual charw to pixels, small numbers can become 0. When a 0 is passed to the Windows font routine, it has a special meaning (means use a default width as opposed to 0). When a very small number is passed to the font routine, the font is just illegible (as it should be when very small virtual charw is used). Code changed to never pass a 0 to Windows font routine.</p> | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- Configured CVI (Current value indicator) , DOC(Director of change arrow) &amp; NCV(Numeric Current Value ).</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- CVI, DOC &amp; NCV are appearing in the High performance analog indicator.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- Select Pos (e.g.:- above indicator shape/doc).</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>4:- Configured char w:- 1.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; F</font></span><font size=3>or more information, please find the attached screen shot &quot;Char_w_1.jpg&quot;</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>5:- It is clear from the screen shots that characters width is more than configuration.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Same behavior is observed, if configured Char w from 1 to 6.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>6:- Now configured char w:- 7.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; F</font></span><font size=3>or more information, please find the attached screen shot &quot;Char_w_7.jpg&quot;</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>7:- It is clear from the screen shots that characters width is properly behave as per configuration.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Note:- Same issue is observed with &quot; EU Char w&quot; option.</font></p><font face="Times New Roman" size=3> </font> |  | U0 |  |  | FINDING | [6 empty] | 93896
34737 | FINDING | Occasionally, it is observed that while performing the copy & paste operation on HPAI, error message is popping. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-05-17 06:28 | [11 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-05-17 06:28 | 67269 |  |  | 2016-05-17 06:28 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2015-10-15 07:05 |  | Occasionally, it is observed that while performing the copy &amp; paste operation on HPAI, error message is popping. | Fixed a bug that allowed very small resize of HPAI to scale some included widths/heights to 0 - which would then not compile on the next file load. Put checks in to never allow this scenario to happen on a resize operation. |  |  | Test resizing HPAI's smaller in the width and height dimensions using a dash for the current value indicator and/or the control setpoint icons. Then, after resizing smaller, attempt to copy-n-paste, move, align/equispace, save/re-open graphic, compile source command in source editor, display properties/apply same properties, etc. Should never see compile errors/load errors/copy-paste errors again. | 0 |  |  |  | <p>GA:- </p><p>Date:- 5/17/2016</p><p>Used Build:- Ov 3.6.0_U7</p><p><br></p><p>Perform many times the copy and past operation, change the width and height of HPAI but did not get this error. Hence finding is closed.</p><p><br></p> | 0 |  | Ovation for Windows/Operator Station/Graphics/Software | HPAI resize code changed to never allow a 0 width or height for any element of the HPAI on a resize operation. Any width or height param that would scale to a 0 on a resize will be automatically changed to a 1. 0 is not a valid width/height. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0u7 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation 3.5.1</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Used patch: - OVA351-040-10142015142029</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | <p>Problem was that when a HPAI with dash current value indicator or dash setpoint icon was used, and the HPAI was resized smaller, the virtual dimension that was hard-coded =1 was being changed to 0 erroneously which would then not compile again (or copy-paste successfully). Once it changed to 0, it would never compile again - no matter what edit was performed on it (cause anything times 0 is still 0).</p><p><br></p><p>Sorry, my TFS issue. Somehow I checked in fix, and then 6 mins later checked in fix rollback (ie. undid the fix), and that was what you got ?!&nbsp; Checked in the fix again (no rollback this time). Again, sorry. Updated new changeset# above.</p> | 12 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- In Graphic Builder, Configured High performance analog indicator.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Resize the HPAI &amp; perform copy &amp; paste operation many number of times.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- While performing above operation on HPAI, occasionally error is popping up.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp; </font></span><font size=3>For more detail, please find the attached screen shots” HPAI_Error.jpg”.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>4:- Press Ok &amp; again try to paste it. Same error is popping up.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>5:- Closed the graphics &amp; again try to open it.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>6:- While opening the graphic following message is popping up.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>“ .src file could NOT be loaded; 1 or more errors found”.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>For more detail, please find the attached screen shots”Opening Messages .jpg”.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>7:- Press yes.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>8:- Compile Output message is popping up.as seen in the attachment “Compile Output message.jpg”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><font size=3>Note:- <span style="">&nbsp;</span></font><font size=3>1:- Dev can investigate this issue by using </font><span style=""><font size=3>&nbsp;</font></span><font size=3>AAAA.src </font><span style=""><font size=3>&nbsp;</font></span><font size=3>graphic.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><font size=3><span style="">&nbsp;</span><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font><font size=3>2:- Dev can login drop160 by using remote login. Remote logging detail is attached with this finding. </font></font></p><font face="Times New Roman" size=3> </font> |  | u0 |  |  | FINDING | [6 empty] | 97052
34741 | FINDING | Ovation 3.6.0. U0 build is showing License issue (degraded to trial Version) and also the Duplicity of feautres in drop down menu. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 6 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2015-10-28 08:01 |  |  |  | 2015-10-16 06:59 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-10-16 03:09 |  | <p>1. Ovation 3.6.0. U0 build is showing License issue -&nbsp;initial 3.6.0. build (i.e. P0 ) setup already&nbsp;had License&nbsp; for all features .</p><p>&nbsp;But&nbsp;after installation of U0, on the step of the Ovation license Manager,&nbsp;window&nbsp;is coming with trial version notification.</p><p>2.&nbsp;In Ovation license Manager, feature shown: &nbsp;for developer studio, graphics builder, control builder etc.&nbsp; is in&nbsp;duplicate form (refer attached&nbsp;Attachment1.JPG).</p><p>3. In Ovation license Manager,&nbsp;feature shown:&nbsp; 'Virtual&nbsp;Controller Hosts'&nbsp; is showing no. of Licenses = 60 in right pane (refer attached&nbsp;Attachment2.JPG). </p><p>&nbsp;&nbsp; In Ovation license Manager,&nbsp;feature shown:&nbsp; 'Virtual&nbsp;Controllers' is showing no. of Licenses =&nbsp;3 in right pane (refer attached&nbsp;Attachment3.JPG).This&nbsp;seems to be vice versa i.e VC is 60 and VCH is 3</p><p>&nbsp;&nbsp;Please refer attached Attachment4 to view the License file&nbsp;of Build U0 (Ov3.6.0.). just for reference.</p><p><strong>4.When doing step of license installation&nbsp;on DBS, &nbsp;it is observed in the license tab&nbsp;that Locking code of drop100 is modified by itself to some unknown number</strong> (refer attached&nbsp;Attachment5.JPG). <strong>.</strong></p><p><strong><br></strong></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <ul><li>Ovation 3.6.0. build U0. on the Windows Server 2012 R2 - Hardware Machine&nbsp;R720</li></ul> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | 3.6.0 contains a new version of License Mgr that was released in U0.&nbsp; Obtain new licenses from Mati | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Install the Ovation 3.6.0. U0. on m/c having 3.6.0. P0, using conventional steps.</p><p>2. When proceeded further&nbsp;to License setup window, it shows the Trial Version.</p><p>3.&nbsp;Ovation can be downloaded on this DBS and is&nbsp;successfully installed and drop can be loaded. But studio shows trial version for license (refer attached&nbsp;Attachment6.JPG).</p> |  | U0 (Build) |  |  | FINDING | [6 empty] | 87501
34745 | FINDING | Version of developer studio is not displayed appropriately on launching. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-16 07:27 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-16 07:27 |  |  |  | 2015-11-16 07:27 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-10-16 04:53 |  | <p>Version of developer studio is not displayed appropriately on launching.&nbsp;Number 3.6.0.64021 is displayed instead of 3.6.0 and it&nbsp;overlaps the text.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OS: WS2012 R2</p><p>Machine Type: DBS</p><p>Machine Name: Drop100</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>msb 11/16 - OK in Ov-3.6.0_U1 - </p> <p>&nbsp;&nbsp; Developer studio 3.6.0</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open Developer studio --&gt; While&nbsp;launching, version is not correct. &nbsp; |  | U0 |  |  | FINDING | [6 empty] | 88411
34755 | FINDING | “Select” feature is not working in “Import Operation” window under “control options”. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-25 01:58 | [8 empty] | FALSE |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-25 01:58 |  |  |  | 2015-11-25 01:58 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-10-19 06:47 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>“Select” feature is not working in “Import Operation” window. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Selection of any parent check box is not selecting corresponding child check boxes. Thus it makes harder to import large amount of control sheets at a time since we need to select each manually one by one.</font></p><font face="Times New Roman" size=3> </font> |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Control Options/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Ovation3.6.0_U0 Database server</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Control Options | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font size=3><font face=Calibri>Right click on “control task” of any live controller </font><span><span style="font-family:Wingdings;">à</span></span></font><font face=Calibri size=3> Select “Control Options” </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri size=3> Select Import Operation </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri size=3> under “Data Directory” tab; browse the path from where control sheets need to import </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri><font size=3>Selection of either check box- Control function, Drop xx or Control Task x is not </font><span><font size=3>&nbsp;</font></span><font size=3>selecting corresponding child (all .svg files under selected control task) check boxes.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Please find the attached snapshot for more clarity.</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>In addition to this, it has also been observed that issue also persists with other control function- &quot;compile&quot; operation.</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>YJ: Issue fixed in U1, hence finding closed.</font></p><font face="Times New Roman" size=3> </font> |  | U0 |  |  | FINDING | [6 empty] | 88881
34773 | FINDING | GEGenius: Cannot edit I/O Block. Unassigning LA point causes Studio to crash. | Swartz, Mark EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2015-11-24 13:53 | [8 empty] | FALSE |  |  | Brown, Sean EMR SYSS PWS PITT | 2015-11-24 13:53 | [7 empty] | Brown, Sean EMR SYSS PWS PITT | 2015-10-22 09:41 |  | <span style="font-style:italic;"><span style="font-weight:bold;">This finding cannot be completely retested until after the new Oracle is installed and a binary import of the system can be performed.</span></span><br><br>OCR1100 Controller 35/85 (Emily) is configured with GEGenius.&nbsp; After upgrading the controller with 3.6.0_U0 the controller is failing with messages related to GEGenius.<br><br>While investigating the configuration it was found that I/O Blocks cannot be edited.&nbsp; Attempting to un-assign analog points cause Studio to crash.&nbsp; Please refer to the attached file <span style="font-weight:bold;">GEGenius.zip</span>.<br> |  | No Action Required |  | <p>The database script where these errors reside (synonyms.sql)&nbsp;is executed during the initial build of an Ovation database and during a do_ptadmin_import Oracle binary import operation.</p><p>Testing should include verification that GE Genius I/O Block can be added/edited following an initial build of an Ovation database.&nbsp; These tests should also be repeated following a do_ptadmin_import operation.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirming Issue is Resolved | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>This is a result of several improperly specified database synonyms -- all specific to GE Genius reference tables/views.&nbsp; </p><p>This occurred during the initial build of the Ovation database and/or the rebuild of the Ovation database during a do_ptadmin_import Oracle binary import operation.</p><p>After the fix has been released, any existing database can be corrected by exporting and re-importing the database via sequential execution of do_ptadmin_export and do_ptadmin_import.</p><p><br></p><p>More Information Required: Can the I/O Block be opened in Ovation Developer Studio?</p><p>More Information Supplied:&nbsp; No.&nbsp; The resulting error is in the attached ZIP file.</p><p><br></p><p>Changed State to Monitoring.&nbsp; A binary export/import is required to verify the resolution of this finding, which would be disruptive at this time.&nbsp; The synonyms.sql file was executed to allow successful partial testing to be performed.&nbsp; After this was done it was possible to edit Blocks and Channel points.&nbsp; This finding will be fully re-tested after the new Oracle has been provided and installed.<br></p> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U0 |  |  | FINDING | [6 empty] | 88856
34779 | FINDING | Ovation 3.6.0. U0 is showing Duplicity of feautres in Ovation License Manager & the wrong license limits for VCH's & VC's . | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | McMaster, James External Artech | 2015-10-28 10:30 | [8 empty] | FALSE |  |  | McMaster, James External Artech | 2015-10-28 10:30 |  |  |  | 2015-10-28 10:30 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-10-23 05:03 |  | <p>1. In Ovation license Manager, feature shown:&nbsp; for developer studio, graphics builder, control builder etc.&nbsp; is in duplicate form (refer attached Attachment1.JPG).<br>2. In Ovation license Manager, feature shown:&nbsp; 'Virtual Controller Hosts'&nbsp; is showing no. of Licenses = 60 (should be 3) in right pane (refer attached Attachment2.JPG). </p><p>&nbsp;&nbsp; In Ovation license Manager, feature shown:&nbsp; 'Virtual Controllers' is showing no. of Licenses = 3(should be 60) in right pane (refer attached Attachment3.JPG).This seems to be vice versa i.e VC is 60 and VCH is 3</p><p><br></p> |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 1. Ovation 3.6.0. build U0. on the Windows Server 2012 R2 - Hardware Machine R720 |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | <p>This is duplicate of 34741 which I closed with the following explanation. 3.6.0 contains a new version of License Mgr that was released in U0.&nbsp; Obtain new licenses from Mati</p><p><br></p><p>Not sure why you wrote another finding.</p> | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install the Ovation 3.6.0. U0. on m/c having 3.6.0. P0, using conventional steps.</p><p>2. When proceeded further to License setup window, in the License manager it shows the duplicity of the features &amp; the wrong license No.<br></p> |  | U0 (Build) |  |  | FINDING | [6 empty] | 87532
34789 | FINDING | do_ptadmin_import/export reports an error. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-24 16:01 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-24 16:01 |  |  |  | 2015-11-24 16:01 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-10-23 13:39 |  | <p>Export or importing the oracle database by using do_ptadin_export / do_ptadmin_import reports the following error message :</p><p>C:\Users\ADMINI~1.VAL\AppData\Local\Temp\1\FIND_ORA_HOME.VBS(7, 1) WshShell.RegRead: Invalid root in registry key &quot;HKEY_<br>LOCAL_MACHINE\SOFTWARE\oracle\KEY_OraDb11g_home1\ORACLE_HOME&quot;.</p><p><br></p><p>The function does continue after reporting this message. <br></p> |  |  |  | <p>The affected area is in the portion of the batch files which reference to Oracle registry.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0_U1 |  | Ovation 3.6.0 U0 |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The two batch files (do_ptadmin_import.bat and do_ptadmin_export.bat) mistakenly reference a registry which is applicable to Oracle 11g, not Oracle 12c (which is utilized in Ovation 3.6.0).&nbsp; The batch files will be modified to reference the proper Oracle 12c registery. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open command tool and run either of the above listed commands to export /import the database. |  | U0 |  |  | FINDING | [6 empty] | 88869
34791 | FINDING | Ovation License Manager crashes when deleting certain licenses. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Swartz, Mark EMR SYSS PWS PITT | 2015-10-26 07:55 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2015-10-26 07:55 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2015-10-23 15:09 |  | Using License Manager, Manage License File, to delete a license can cause the service to crash.&nbsp;&nbsp;The service&nbsp;does not restart afterwards.&nbsp; This issue was demonstrated to Dev. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Spillane, Donal AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.6.0 U0 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Use License Manger, Manage License file, to delete licenses. |  | U0 |  |  | FINDING | [6 empty] | 87321
34792 | FINDING | License Manager is missing descriptions for some features | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 15:29 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 15:29 |  |  |  | 2016-03-31 15:29 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-10-23 15:18 |  | License Manager is missing descriptions for some of the features.&nbsp; Features without descriptions that have been seen so far are 54, 55, 77, 78, 79, 81. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Spillane, Donal AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.6.0 U0 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>There will be times that the license manager does not have a description for a license feature, in these cases the feature number will be displayed.</p><p>New features can be added at any time, these features will have feature numbers that the license server will not recognize, all we can do is to display the number.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Review features within License Manager |  | U0 |  |  | FINDING | [6 empty] | 94141
34793 | FINDING | OSR is unable to generate the .epm file | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:05 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:05 | 65727 |  |  | 2016-02-02 02:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-26 04:40 |  | <p>OSR is throwing an error&nbsp; &quot;dynamic link library initialization routine failed&quot; when user tries to generate the .epm file.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U3 |  | <p>Ovation 3.6.0_U0</p><p>&nbsp;</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB 02/02/16- Verified on Ovation3.6.0_U3 and observed that OSR is generating the .epm file. Hence this finding is closed by validation. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce:</p><p>1)Launch the OSR utility</p><p>2)Try to generate the .epm file</p><p>Screenshot is also attached for your reference</p> |  | U0 |  |  | FINDING | [6 empty] | 91806
34794 | FINDING | OSR is printing wrong Ovation version. | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-03 00:36 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-03 00:36 |  |  |  | 2016-05-02 09:48 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-26 04:51 |  | OSR is printing Ovation version as 3.5.2 under Controller drop Software Revision field.&nbsp;But in actual installed ovation software is Ovation 3.6.0.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; |  |  |  |  | 0 |  |  |  | This issue was observed and reported on Ovation3.6.0_U0 but in later builds&nbsp;it got&nbsp;resolved. OSR report generated on Ovation3.6.0_U0 is attached for your reference. | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U0 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are steps to reproduce:</p><p>1)Generate the OSR Report.</p><p>2)Verify the Controller drop Software Revision field.</p> |  | U0 |  |  | FINDING | [6 empty] | 96108
34795 | FINDING | Oracle Version is wrong in installation wizard of Ov3.6.0 setup. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-17 02:23 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-17 02:23 |  |  |  | 2015-11-17 02:23 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-10-26 06:24 |  | <p>Oracle version in installer shows&nbsp;-Oracle11g although&nbsp;during installation destination path shows-Ora12c.&nbsp;It is also been confirmed from path: C:\Oracle.</p><p>Please also see the attached snapshots.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  | Ovation3.6.0_U0 Database server |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>The description will be changed to reference Oracle 12c.</p><p><br></p><p>YJ: issue fixed.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Issue was seen during installation of Ov3.6.0 database server.</p> |  | U0 |  |  | FINDING | [6 empty] | 88475
34796 | FINDING | SureService Ovation System Registration version is printed wrong in OSR report. | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:11 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:11 | 64576 |  |  | 2015-11-17 03:11 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-26 07:26 |  | Version of SureService Ovation System Registration is 1.5 but in report it is printed as &quot;SureService Ovation System Registration 1.4 Report&quot; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  | Ovation3.6.0_U0 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Corrected version information.</p><p>&nbsp;</p><p>LB 11/17/15-Verifed on Ovation 3.6.0_U1 and observed that OSR is printing its correct version on report. Hence this finding is closed by validation.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Following are the steps to reproduce:</p><p>1)Generate the OSR report.</p><p>2)Verify the SureService Ovation System Registration version under heading &quot;&nbsp;User information &quot; field name -Report name.</p> |  | U0 |  |  | FINDING | [6 empty] | 88481
34800 | FINDING | CB Editor will crash if a control sheet is opened and 'Algorithms' is selected from Edit menu | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Lal, Ramesh External | 2016-03-18 06:32 | [11 empty] | Lal, Ramesh External | 2016-03-18 06:32 | 66662 |  |  | 2016-03-18 06:32 |  |  |  | Lal, Ramesh External | 2015-10-26 10:59 |  | <p>In Unified Control Builder create a new control sheet and save it or open an existing control sheet. From the Tool Bar select Edit &gt; Algorithms. At this point Control Builder will crash.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U4 |  | EWS, Win 7 SP1, 64 bit |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>Does U1 do this ?</p><p>&nbsp;RL: 11/24/2015 - Checked in 3.6.0_U1. CB still crashes.</p><p>IC 3/17/16&gt; please retest in U4. </p><p><br></p><p>RL: 3/18/2016: Retested in 3.6.0_U4 and found O.K. . Finding closed.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Developer Studio</p><p>2. In Unified Control Builder create a new control sheet and save it or open an existing control sheet. </p><p>3. From the Tool Bar select Edit &gt; Algorithms. </p><p>At this point Control Builder will crash.</p> |  | 3.6.0_U0 |  |  | FINDING | [6 empty] | 93536
34806 | FINDING | Unexpected behavior is observed when user minimize and then maximize the SureService Ovation System Registration window. | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:15 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:15 | 64571 |  |  | 2015-11-17 03:15 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-26 23:29 |  | <p>Unexpected behavior is observed when user minimize and then maximize the SureService Ovation System Registration window.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  | Ovation 3.6.0_U0 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Form no longer changes size on minimize/restore.</p><p>LB 11/17/15-Verifed on Ovation 3.6.0_U1 and observed that&nbsp; SureService Ovation System Registration window behavior is fine during Minimize, Maximize operation. Hence this finding is closed by validation.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Launch the SureService Ovation System Registration utility.</p><p>2)Minimize the window and then try to maximize it.</p><p>Screenshot is also attached for your reference.</p> |  | U0 |  |  | FINDING | [6 empty] | 88483
34810 | FINDING | Control Logic Navigator is not supported in 3.6.0. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | McMaster, James External Artech | 2016-02-16 14:53 | [11 empty] | McMaster, James External Artech | 2016-02-16 14:53 |  |  |  | 2016-02-16 14:53 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-27 01:01 |  | <div>Unable to launch Control Logic Navigator (CLN) from both point search option and Ovation &gt; Ovation Utilities &gt; Control Logic Navigator.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | Ovation 3.6.0 + U0 |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | This program is not supported in 3.6.0.&nbsp;&nbsp; The shortcut will be removed in U4 | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>Steps:</div><div>Unable to Launch CLN from Ovation&gt;Ovation Utilities&gt; Control Logic Navigator in Windows 7.<br></div><div><ol><li>Open CLN from &nbsp;Ovation&gt;Ovation Utilities&gt; Control Logic Navigator.<br></li><li>A pop up appears stating &quot;Windows is searching for ctrl_navigator.exe. To locate the file yourself, click browse.&quot; (Please refer screenshot <span style="font-style:italic;">Control_Logic_Navigator_Win7.png</span>)<br></li></ol></div><div>Unable to Launch CLN from Ovation&gt;Ovation Utilities&gt; Control Logic Navigator in Windows 2012.<br></div><div><ol><li>Open CLN from &nbsp;Ovation&gt;Ovation Utilities&gt; Control Logic Navigator.<br></li><li>A pop up appears stating &quot;The app can't run on yout PC. To find a version for your PC, check with Software Publisher&quot; (Please refer screenshot&nbsp;<span style="font-style:italic;">Control_Logic_Navigator_Win2012.png</span>)<br></li></ol></div><div>Unable to Launch CLN from Point search in Windows 7 and Windows 2012.<br></div><div><ol><li>Open CLN by right clicking the point and going to point search in signal diagram.<br></li><li>Nothing opens.<br></li></ol></div><div>&nbsp;</div> | Validaiton | U0 |  |  | FINDING | [6 empty] | 92353
34811 | FINDING | OSR is not printing the installed license details. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 6 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-16 06:50 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-16 06:50 | 67053, 67552, 67634 |  |  | 2016-04-04 09:35 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-27 01:20 |  | OSR is not printing the installed license details. |  |  |  |  | 0 |  |  |  | LB 05/16/16-OPC event server license is printed as &quot;DROPID: 130, OPC Event Server (Feature=OPC_EVENT_SERVER), Type: Trial, Number of licenses: 2097150&quot; but in actual single normal license is installed. At the end of license section an error &quot;A problem occurred retrieving standalone licensing information. VLSgetFeatureInfo failed for feature OPC_SERVER, ret = 0xFFFFFFFF&quot; is observed screnshot, OSR report,drop130 license details is attached for your reference. Same thing is observed for drop149. | 0 |  | Ovation for Windows/System Registration Utility/Software | 2016-04-28 RStaab: SRU was updated to use the newer licensing libraries. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | Ovation 3.6.0_U0 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce:</p><p>1)Generate the OSR Report.</p><p>2)Verify the license details of drop with OSR report.</p><p>Installed license details and OSR report is also attached for your reference.</p><p>&nbsp;</p><p><u></u>&nbsp;</p> |  | U0 |  |  | FINDING | [6 empty] | 96894
34814 | FINDING | Point review application does not review the points, which are configured in the “PDS Point Group” | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-11-24 22:50 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-11-24 22:50 | 64310 |  |  | 2015-11-24 22:50 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-10-27 03:05 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Point review application does not review the points, which are configured in the “PDS Point Group”</span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  | <p>The loading and saving of the review filters has been updated.&nbsp; The Point Group Type is now saved.&nbsp; If there is no point group type in the file it is defaulted to 0 (PDS Point Group Type)</p><p><br></p><p>SDK :This issue is fixed in Ovation3.6.0_U1 Build hence finding closed.&nbsp;</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U1 |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ovation 3.6.0_U0 +OS-Win7+64 Bit</span> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | <p>I added a point group and added two analog points that already existed in the system.&nbsp; I started a new Point Review Application and performed a point review of the newly created PDS Group.&nbsp; The points were displayed in Point Review. Did you have any other filters set that would have filtered out the points, such as record types? Are the points that are members of the point group that you created&nbsp;loaded?&nbsp; Do they appear in PI? Does the system know about them?</p><p><br></p><p>SDK 28Oct15: The drop was cleared and loaded fresh today. And all the points could be seen on PI as well as on Point Review.</p><p><br></p><p>The new observation in Point Review is sorting &nbsp;Filters are set for Point Groups. </p><p>Result is Ok as required. </p><p>Save the filter setting as PDS-Groups.rvt.</p><p>Now Review another set of points using different filters. Save as SDK-1.rvt.</p><p>Now, load the previously saved PDS-Groups.rvt. &amp; start point Review: Result is not as expected. </p><p>The filters are loaded as desired, but the result is for the whole system as if no filters were applied.</p><p>The issue was that the filtering method was not set correctly and the Point Group Type was not previously saved or loaded from the review file.&nbsp; The default is now set to PDS Point Group Type.</p><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">1. Create a PDS point group in developer studio with some point group member. <span style="">&nbsp;</span></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">2. Download the point group configuration in the system.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">3. Open point review application --&gt;selected configured point groups tab under the source database then click on start point review.</span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">It does not result in any points .</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3> <br></font></p></span><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  | U0 |  |  | FINDING | [6 empty] | 88875
34819 | FINDING | Point information, Value/Mode Ribbon Tab does not display some special characters under digital value option. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Augustine, Lisa EMR SYSS PWS PITT | 2015-10-29 08:42 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2015-10-29 08:42 |  |  |  | 2015-10-29 08:42 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-28 05:23 |  | <p>Point information, Value/Mode Ribbon Tab does not display&nbsp;special character (&amp;)&nbsp;under digital value option.</p><p>While other characters are displaying properly.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | Ovation 3.6.0_U0; |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>WIW No plans to fix - The '&amp;' is the short cut key.&nbsp; Do not use it for the set/reset description.</p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Create a digital point under display Tab assign SET and RESET description using special characters&nbsp;e.g. &amp;RF&amp;QWERTYUI and QWERT$@!^&amp;*(.</p><p>2)Load the controller and open the point in Point information window.</p><p>3)Match the SET and RESET description mention under display Tab with Value/Mode Ribbon Tab-digital value option.</p><p>4)The &amp; character cannot be displayed rest available characters are seen OK.</p><p>Screenshot is also attached for your reference.</p> |  | U0 |  |  | FINDING | [6 empty] | 87629
34820 | FINDING | Controller fails with fatal error when it is cleared | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 02:30 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-11-25 02:30 | 64348 |  |  | 2015-11-25 02:30 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-10-28 06:08 |  | Controller (OCR 400 &amp; OCR 1100) fails with fatal error&nbsp;when it is cleared. |  |  |  |  | 0 |  |  |  |  | 0 |  |  | Sync_opp_list was being called with zero points during a drop clear.&nbsp; When this happens, sync_opp_list must delete the file. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0_U1 |  | Ovation 3.6.0 : OCR 400 &amp; OCR 1100 |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | MS : Checked in U1. Issue is fixed, I am closing this finding.&nbsp; | 9 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Steps:</p><ol><li>Consider drop36 (OCR 1100) is&nbsp;loaded &amp; in&nbsp;control state &amp; drop86 (OCR 1100)&nbsp;is loaded &amp;&nbsp;in back up state.</li><li>Perform clear operation of drop36&nbsp;(from developer's studio).</li><li>Drop 86 changed to control state but&nbsp;drop36 came up in&nbsp;failed state.</li></ol><p>&nbsp;&nbsp;&nbsp;&nbsp; (please refer attached snapshots)</p><p><br></p><p>Observation:</p><ol><li>&nbsp;DU Point Fault Code :&nbsp;FC-66, FK-7,FS-0,FO-12&nbsp;&nbsp;</li><li>It is require to&nbsp;clear the flash to restore the failed controller.</li><li>This issue is seen in both OCR 400 &amp; 1100.</li></ol> |  | U0 |  |  | FINDING | [6 empty] | 88882
34824 | FINDING | Ovation Point review -> alarm/limit tab -> limit check option does not show correct options . | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-11-24 21:52 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-11-24 21:52 | 64334 |  |  | 2015-11-24 21:52 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-10-28 23:13 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ovation Point review -&gt; alarm/limit tab -&gt; limit check option does not show correct options.</span></p><font face="Times New Roman" size=3><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Set limit check tab are showing options as “UNSHELVE/SHELVE “in the point review Alarm/limit tab.</span></p><p> <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">The set limit check should be updated with ON/OFF options in the point review application.</span></p><p> <br></p></font><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U1 |  | Ovation 3.6.0 |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | <p>SDK(11/25/2015) : Yes,&nbsp;This issue&nbsp;is fixed in Ovation 3.6.0_U1 build.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Open Ovation Point review application&nbsp;-&gt; select alarm/limit tab -&gt; and check the set limit check option&nbsp;under the ALARM/LIMIT tab.&nbsp;.</span></p><p><font face="Times New Roman" size=3> <br></font></p> |  | U0 |  |  | FINDING | [6 empty] | 88874
34825 | FINDING | Point Review filter is not working properly for RM points. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Augustine, Lisa EMR SYSS PWS PITT | 2015-10-29 08:40 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2015-10-29 08:40 |  |  |  | 2015-10-29 08:40 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-29 00:46 |  | RM point does not have quality but its quality is showing good in point review. when we try to search RM points using point review,it comes in search list with good quality. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <p>Ovation 3.6.0_U0</p><p>OS-Win7 64 bit</p> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Open point review application, select filter tab.</p><p>2)Select record type as Module(RM).do not select anything on quality filter.</p><p>3)Click on start button to initiate search option.</p><p>4)After this Module point got searched with good quality but in actual we have not select any quality in quality filter option.</p><p>5) This is true&nbsp;if Quality is Set to Good or none of the Quality is selected.</p><p>&nbsp;</p> |  | U0 |  |  | FINDING | [6 empty] | 87627
34826 | FINDING | Operator functions are showing wrong ovation version. | Spillane, Donal AUTOSOL PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 14:46 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 14:46 | 65556 | [6 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-10-29 03:22 |  | <p><font face="Times New Roman" size=3><br></font></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Operator functions are showing wrong ovation version.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ovation PI/PR/Alarm systems/system viewer /online graphics/Error log are showing Ov.3.5.2 version instead of 3.6.0 .</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PI, Review, Alarm, Ovation Session Manager, System Viewer and Error Log Viewer have been updated. Graphics still need updated.</span></p><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | <p>Ovation 3.6.0_U0</p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U0 |  |  | FINDING | [6 empty] | 94137
34828 | FINDING | OSR is unable to collect EWS details. | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:20 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 03:20 | 6444864606 |  |  | 2015-11-17 03:20 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-10-29 06:17 |  | <p>OSR is unable to collect server as well as operator station drop details. </p><p>During investigation it is observed that Ovation System Registration Agent service is not available on operator as well as server drop. Hence OvSysRegAgent is not seen as running on any EWS drops.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | Path to the .NET service installer changed from:<div><i>WINDIR ^ &quot;Microsoft.NET\\Framework&quot; ^ DOTNET_FRAMEWORK_4_0_DIR ^ SERVICE_INSTALLER</i></div><div>to</div><div><i>FOLDER_DOTNET_40 ^ SERVICE_INSTALLER</i><br></div><div><div><br></div></div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U1 |  | <p>Ovation 3.6.0_U0</p><p>OS-Win7 64 bit, Windows server 2012.</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Corrected directory references in install shield.</p><p>&nbsp;</p><p>LB 11/17/15-Verifed on Ovation 3.6.0_U1 and observed that&nbsp; OSR is collecting workstation drop details. Hence this finding is closed by validation.</p> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Following are the steps to reproduce:</p><p>1)Generate the OSR report.</p><p>2)Verify the server, operator drop details.</p><p>&nbsp;</p><p>&nbsp;</p> |  | U0 |  |  | FINDING | [6 empty] | 88484
34829 | FINDING | Software Versions tab in Controller Diagnostics still displays the versions as "3.5.2" | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-02-10 04:27 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-02-10 04:27 | 64389 |  |  | 2016-02-10 04:27 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2015-10-29 06:26 |  | Software Versions tab in Controller Diagnostics still displays the versions as &quot;3.5.2&quot; for both Binary and Library module versions instead of 3.6.0.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [5 empty] | Implementation | 3.6.0_U1 |  | Ovation 3.6.0 + U0 |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>The version string is now updated to &quot;3.6.0&quot;</p><p>SHS 2/10/2016&gt; Finding has been verified in 3.6.0 U3 and found to be fixed.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Steps:<div><ol><li>Open a Controller Diagnostics application.</li><li>Select a controller and go to Software Version tab.</li></ol><div>Observation:</div></div><div><ol><li>Binary and Library Module versions are displayed as &quot;3.5.2&quot; instead of &quot;3.6.0&quot; (Please refer to attachment <span style="font-style:italic;">Controller Diagonistc Version.jpg</span>)</li></ol></div> |  | U0 |  |  | FINDING | [6 empty] | 92072
34830 | FINDING | Controller Failure (due to GE Mark table build error) | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Wood, Thomas T AUTOSOL PWS PITT | 2015-11-24 11:41 | [11 empty] | Wood, Thomas T AUTOSOL PWS PITT | 2015-11-24 11:41 | 64579 |  |  | 2015-11-24 11:41 |  |  |  | Wood, Thomas T AUTOSOL PWS PITT | 2015-10-29 08:29 |  | Controller fails when loading. See attached Error Log. <br><br>Per error log, issue seems to be related to GE Mark: <br>coord: GE Mark 5/6 IO Driver : table build error: /ata0/wdpf/dpu/data/gett.wrk doesn&amp;apos;t exist.&lt;/Err&gt;<br> |  |  |  |  | 0 |  |  |  |  | 0 |  |  | <p>What system? What drop? Does the controller fail when the GE driver is removed?</p><p><br></p><p>I attached a serial cable to drop32 to observe the failure. When the drop is cleared it comes up not in fault. When a load is performed it gets stuck loading sheets and will eventually fault. Using printErrorBuffer I can see that the first fault reported is Flash Memory Subsystem Error: Flash Memory Error, 0x04 02 18 0. This is called in the EMEMOpenFlash routine in flash_supp.c. The controller is unable to open a file in flash memory.</p><p><br></p><p>This is a flash memory subsystem problem, not a GE driver problem.</p><p><br></p><p><br></p><font size=2><p><br></p></font> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0.U1 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  | Ran out of file descriptors.&nbsp; Increased maximum number from 192 to 1024 in the Kernel Configuration. | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U1 |  |  | FINDING | [6 empty] | 88850
34840 | FINDING | Firewall missing from controllers | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-26 21:04 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-26 21:04 | 67648 |  |  | 2016-05-26 21:04 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2015-11-02 06:45 |  | <p>&quot;ipfirewall_version&quot; returns &quot;unknown symbol&quot; on the OCR1100,&nbsp;indicating the firewall is missing.</p> |  |  |  | Perform Achilles Level 1 Cert Tests on OCR1100. | 0 |  |  |  | <p>As per developer &quot;The OCR400 is not meant to have a firewall at this time.&quot;</p><p>and firewall is working in OCR1100.</p><p>Hence I am closing this finding.</p> | 0 |  |  | included the missing kernel components,&nbsp;uncommented the firewall registration function calls |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Validation |  | The firewall is now enabled for the OCR1100. | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | In the controller console, type &quot;ipfirewall_version&quot; (no quotes). The console reports &quot;unknown symbol&quot; when the firewall is missing.&nbsp;If a value is returned, the firewall is present. OCR1100 only. |  | U0 |  |  | FINDING | [6 empty] | 97876
34841 | FINDING | Can't ssh into controllers | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2015-11-09 08:54 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2015-11-09 08:54 |  |  |  | 2015-11-09 08:54 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2015-11-02 06:47 |  | Duplicated finding in F34939 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U1 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U0 |  |  | FINDING | [6 empty] | 88194
34848 | FINDING | Few Test cases in 3.6.0_SRF1725_SVTP_rev1.2_AR can be marked as N/A | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-07-07 08:55 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-07-07 08:55 |  |  |  | 2016-07-07 08:55 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-03 03:46 |  | <p>In the Test case 3.6.0_SRF1725_SVTP_rev1.2_AR following discrepancies are found-</p><p>1. In point 5.1.14, Deluxe analog, Deluxe digital, Deluxe Packed &amp; Packed Digital points are to be created from Control builder&nbsp; --- Points for these&nbsp; Record Types cannot be created from <strong>control builder, hence can be marked as N/A</strong></p><p>2. In&nbsp;point (7) of section&nbsp;5.1.15, points description need to be checked in System viewer for points created from control builder. - Soft points cannot be viewed in the system viewer, points have to be associated with hardware. hence can be marked as N/A.&nbsp; Same With point 7 of section 5.1.17.</p><p>3. In point 5.1.15, points description of Algorithm point&nbsp;need to be&nbsp;verified in Alarm, Trend, Alarm Guidance,. - LC points cannot be viewed in the&nbsp;Alarm, Trend, Alarm Guidance.<strong>&nbsp;</strong> hence can be marked as N/A. Same With 5.1.17.</p><p>4. &nbsp;In point 5.1.21,&nbsp; Deluxe analog, Deluxe digital, Deluxe Packed, Packed Digital points, Drop Point, module point, Node Point's description has to be shown in signal diagram -<strong> </strong>Not Possible, since these points cannot be created in CB, hence can't be seen in Signal Diagram. Hence can be marked as N/A.</p><p>5. &nbsp;In point 5.3.3, for deluxe digital point, not possible to show RS &amp; ST field in&nbsp;Signal Review (should be signal diagram in test case) &amp; system Viewer - As the&nbsp;point is not&nbsp;created in CB (as per test case)&nbsp;and not associated with hardware. Hence can be marked as N/A.</p><p>6. In point 5.3.5, RS &amp; ST field cannot be given to the Deluxe digital as they can't be created from CB. Hence can be marked as N/A.</p><p>7. In point 5.3.6.1 RS &amp; ST field cannot be shown into system viewer -As the&nbsp;point is to be made from CB and not&nbsp;associated with hardware. Hence can be marked as N/A.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | <p>Test case 3.6.0_SRF1725_SVTP_rev1.2_AR </p><p>3.6.0_STP_rev1.1-10-16-15</p> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | u0 |  |  | FINDING | [6 empty] | 99331
34855 | FINDING | English Description(ED) From Control Builder is limited to 30 characters | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-24 21:08 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-24 21:08 |  |  |  | 2015-11-24 21:08 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-03 07:45 |  | Points are created from&nbsp; control builder and 50 characters description&nbsp;is given from control builder and following observations are seen-<ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Point description from the control builder can be given (50 characters can be given from control builder), but, it cannot be seen in the point when it is opened in developer studio(only upto 30 characters are seen). While giving the description from Developer studio, it is possible to give 50 characters description and also can be seen throughout.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">&nbsp;So the test case is Pass for the English Description from Developer Studio, but fail for English&nbsp; description from Control Builder for 50 characters.</p></li></ol><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | Ovation 3.6.0. build U0. on the Windows Server 2012 R2 and EWS on W7(64bit) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the Developer studio.</p><p>2. Make a control sheet.</p><p>3. Create a point in control builder, and give the description with 50 characters.</p> |  | U0 |  |  | FINDING | [6 empty] | 88872
34859 | FINDING | New Virtual Controller can not be downloaded | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-15 09:56 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-15 09:56 |  |  |  | 2016-01-15 09:56 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-03 13:29 |  | <p>A newly created virtual controller (one that has no existing directory), will not come up.&nbsp; It cannot be downloaded.&nbsp; The following error is seen:</p><p>&nbsp;&nbsp; spawning ss_rpc<br>Cannot register service: RPC: Timed out<br>unable to register (FILE_COPY_PGM, FILE_COPY_VERSION, udp).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Shiferaw, Tedla AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.6.0 U0 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Add a new virtual controller and attempt to download.&nbsp; Or delete an existing Virtual controller folder (C:\Ovation\dropX), restart virtual controller and attempt to download. </p> |  | U0 |  |  | FINDING | [6 empty] | 91242
34869 | FINDING | Test Case 5.4.1 of SVTP 3.6.0_ST_BASIC_FUNCTIONS_SVTP_rev1.P_PA.doc cannot be tested as QLI and QLJ Interface Cards are not available in GEC for testing XPID algorithm | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Arora, Priyanka AUTOSOL PWS NOIDA | 2015-11-04 03:38 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2015-11-04 03:38 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2015-11-04 03:37 |  | Test Case 5.4.1 of SVTP 3.6.0_ST_BASIC_FUNCTIONS_SVTP_rev1.P_PA.doc cannot be tested as QLI and QLJ Interface Cards are not available in GEC for testing XPID algorithm. So this Test Case can be marked as NA in SVTP. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 35 | FINDING |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U0 |  |  | FINDING | [6 empty] | 87868
34870 | FINDING | Discrepancy in System Viewer's Print Preview Toolbar | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wozniak, Diane M EMR SYSS PWS PITT | 2016-03-21 07:38 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2016-03-21 07:38 |  |  |  | 2016-03-21 07:38 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-04 04:16 |  | <p>In&nbsp;System Viewer of&nbsp;3.6.0. U0&nbsp;applications, it is found that, in the print preview menu, Customize option is greyed out and unable to fetch customize option from the toolbar.</p><p>It becomes healthy when accessed through Menu bar- Print&gt;Preview&gt;View&gt;Customize.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0. build U0. on the Windows Server 2012 R2 |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the System viewer.</p><p>2. Go to Print option.</p><p>3. In print option go to preview.</p><p>4. In preview, go to the toolbar and click on Customize icon.</p> |  | U0 |  |  | FINDING | [6 empty] | 93682
34871 | FINDING | Online graphics window is crashing on upgraded ovation network of 3.6.0 and ovation session manager is also not opening | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-19 02:16 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-19 02:16 | 64534 |  |  | 2015-11-19 02:16 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-04 04:20 |  | <p>Online graphics window&nbsp;stopped working &nbsp;on upgraded ovation network of 3.6.0 and ovation session manger is also not opening</p><p>The same is observed in work stations also.</p><p>Please find attached the error details copied in text file and also the snapshot of event viewer that shows active directory web service error&nbsp;&nbsp;and graphics window</p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U1 |  | OV 3.6.0 Net26 |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>The issue is the low level SPD call to the Remote Data Server.</p><p><br></p><p>Verified in U1 and found to be resolved</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Go&nbsp; to-&gt; Ovation&nbsp; applications-&gt;click on graphics</p><p>Then there pops up a window Graphics MFC&nbsp; Application has stopped working</p><p><br></p><p><br></p><p>Problem details are :-</p><p>Problem signature:<br>&nbsp; Problem Event Name:&nbsp;APPCRASH<br>&nbsp; Application Name:&nbsp;graphics.exe<br>&nbsp; Application Version:&nbsp;3.6.0.63970<br>&nbsp; Application Timestamp:&nbsp;561f571c<br>&nbsp; Fault Module Name:&nbsp;StackHash_7fa3<br>&nbsp; Fault Module Version:&nbsp;6.3.9600.17031<br>&nbsp; Fault Module Timestamp:&nbsp;5308893d<br>&nbsp; Exception Code:&nbsp;c0000374<br>&nbsp; Exception Offset:&nbsp;PCH_05_FROM_ntdll+0x0003D72C<br>&nbsp; OS Version:&nbsp;6.3.9600.2.0.0.272.7<br>&nbsp; Locale ID:&nbsp;1033<br>&nbsp; Additional Information 1:&nbsp;7fa3<br>&nbsp; Additional Information 2:&nbsp;7fa362edce9a28f0431a675370743824<br>&nbsp; Additional Information 3:&nbsp;88aa<br>&nbsp; Additional Information 4:&nbsp;88aaedbe8de0b4e7158559b347fede71</p><p>Read our privacy statement online:<br>&nbsp; <a href="http://go.microsoft.com/fwlink/?linkid=280262">http://go.microsoft.com/fwlink/?linkid=280262</a></p><p>If the online privacy statement is not available, please read our privacy statement offline:<br>&nbsp; C:\Windows\system32\en-US\erofflps.txt</p> |  | U0 |  |  | FINDING | [6 empty] | 88585
34872 | FINDING | ELC1.3 protocol analyzer tool is not opening on WS12-R2. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 15:29 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 15:29 |  |  |  | 2016-06-07 15:29 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-04 04:49 |  | <p>Protocol Analyzer of ELC 1.3 software&nbsp;not open in&nbsp;DBS&nbsp;&nbsp;(OS : WS12-R2 ).</p><p>While opening it gives Microsoft dot net error.</p><p>(please refer attached snapshot for more details)</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Plymire, Alvan AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | ELC1.3.0 with Ovation 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p><font face="Times New Roman" size=3> IC 6/7/16 &gt; closed finding, track issue as SDR 36732. Updated ELC 1.3.0 DIR with work-around: </font></p><p style="margin:0in 0in 0pt;"><b><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br>Steps to “Enable .NET Framework 3.5 by using the Add Roles and Features Wizard”</span></b></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><b><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><a title="Click to collapse. Double-click to collapse all."><font color="#0000ff">Requirements</font></a></span></b></p><p><font face="Times New Roman" size=3> <br></font></p><ul><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Windows&nbsp;Server 2012 R2 </span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Installation media</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Administrator user rights. The current user must be a member of the local Administrators group to add or remove Windows features.</span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><b><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><a title="Click to collapse. Double-click to collapse all."><font color="#0000ff">Steps</font></a></span></b></p><p><font face="Times New Roman" size=3> <br></font></p><ol type=1 start=1><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">In Server Manager, click <b>Manage</b> and then select <b>Add Roles and Features</b> to start the Add Roles and Features Wizard.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select installation type</b> screen, select <b>Role-based or feature-based installation</b>.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Select the target server.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select features</b> screen, check the box next to <b>.Net Framework 3.5 Features</b>.</span></li><font face="Times New Roman" size=3> </font></ol><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Confirm installation selections</b> screen, a warning will be displayed asking <b>Do you need to specify an alternate source path?</b>. </span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">If the target computer does not have access to Windows Update, click the <b>Specify an alternate source path</b> link to specify the path to the <b>\sources\sxs</b> folder on the installation media and then click <b>OK</b>. </span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">After you have specified the alternate source, or if the target computer has access to Windows Update, click the <b>X</b> next to the warning, and then click <b>Install</b>. <br> <br> </span></p><p><font face="Times New Roman" size=3> <br></font></p> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Loaded the ELC 1.3.0 software in drop100 (DBS-&nbsp;OS- WS 2012 R2)</p><p>2. Opened the Protocol Analyzer tool&nbsp;from&nbsp; C:\ProgramData\Microsoft\Windows\Start Menu\Ovation\Ethernet Link Controller</p><p>&nbsp;&nbsp;&nbsp;&nbsp; Microsoft dot net error appeared.</p> | Validation | U0 |  |  | FINDING | [6 empty] | 98358
34873 | FINDING | Multinetwork could not be configured in Ov3.6.0 (GEC Net#36) | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | McMaster, James External Artech | 2015-11-05 14:02 | [11 empty] | McMaster, James External Artech | 2015-11-05 14:02 |  |  |  | 2015-11-05 14:02 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2015-11-04 06:49 |  | Invalid remote alarm network configuration is reported while downloading the configuration. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>DBS of Ov3.6.0 Winserver2012R12.</p> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | If your drop is configured to talk to alarm collector xyz and alarm collector xyz is configured to get alarms from neta and netb, your drop must also be configured to be able to access networks neta and netb. This is the error that is being reported. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <table style="width:119pt;border-collapse:collapse;" border=0 cellspacing=0 cellpadding=0 width=159> <colgroup><col style="width:119pt;" width=159> <tbody><tr style="height:158.4pt;" height=211> <td style="border:0px black;width:119pt;height:158.4pt;background-color:transparent;" class=xl67 height=211 width=159><p><font face=Calibri>1 . Define Local Data Server<span>&nbsp; </span></font></p><p><font face=Calibri><span></span><font size=3>2.Define Local Alarm Collector .</font></font></p><p><font face=Calibri><font size=3>3 Define ExternaNetworks. </font></font></p><p><font face=Calibri><font size=3>4.DefineAlarCollectorDropinAlarmconfiguration under Networkval36.</font></font></p><p><font face=Calibri><font size=3>5.Download the drops</font></font></p><p><font face=Calibri><font size=3>&nbsp;6.</font></font><font face=Calibri><font size=3>&nbsp;This gives error. Attached multinetworkconfig-error.jpg for reference.</font></font></p><p><font size=3 face=Calibri>step no.4-Defining the Alarm collector under system level removes the error whiledownloading the drops. How ever after defining all the steps, downloading, rebooting the DBS &amp; Local Data &amp; Alarm collector drops multinetwork coniguration is not yet completed.</font></p></td><font size=3> </font></tr><font size=3> </font></tbody></table> |  | U0 |  |  | FINDING | [6 empty] | 88014
34906 | FINDING | Ovation Net Device-Configuration Tool of sycon for Profibus or DeviceNet module configuration is not working properly | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-10 23:40 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-10 23:40 | 65043 |  |  | 2016-04-10 23:40 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-11-06 03:08 |  | <p>It has been observed that net device configuration tool is not working properly. While configuring the individual ports (P01 &amp; P02) of a&nbsp;PROFIBUS or DEVICENET module through netDevice-configuration tool, certain entries are not getting saved properly as described below.</p><p>1. Configured Active Scan Range ( IP start Address: <strong>192.168.26.24</strong> &amp; IP END address: <strong>192.168.26.74</strong>) and Scan Time (10000 ms)&nbsp;of PROFIBUS module P01 port (master) from netDevice-Configuration tool and save the settings. Again reopen the netDevice-Configuration tool for the same port of the module, previously saved settings will be set to default as IP start Address: <strong>0.0.0.0 </strong>&amp;<strong>&nbsp;</strong> IP END address: ---<strong>.---.---.---, </strong>Scan Time: <strong>1500 ms</strong>. Please check the attached snapshot <strong>netDevice.jpg.</strong></p><p><strong><br></strong></p><p>2. Since these settings are not getting saved properly PROFIBUS module ports are showing its state as <strong>OFFLINE</strong> always. Please check the attached snapshot <strong>Controller Diagnostic.jpg</strong></p><p>3. Same settings are also not getting saved while configuring a DeviceNet module.</p> | <p>Driver configuration was not being saved in registry.</p><p>This would require the start and end IP addresses to need to be reentered.</p><p><br></p> |  |  | <p>Attach a serial cable to the controller and get a VxWorks prompt.</p><p>Set odm_test_mode = 3</p><p>This will produce status messages showing what the ODM driver is doing.</p><p>Repeat the test.</p><p>Send a text file with the status messages to me.</p><p><br></p><p>First do lkup &quot;odm_test&quot; to ensure the ODM driver was loaded.</p><p>ST:11/26: Text file containing status messages is attached as <strong>st_odm.txt.</strong></p><p><br></p><p><br></p><p><br></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software | <p>Problem was introduced when the boost library was removed for 3.6.</p><p>ST: 12/23/2015:- Active Scan range is now getting saved through ovation NetDevice configuration tool and problem mentioned in this finding has got resolved in Ov3.6.0_U2 build.&nbsp;So closing this finding.</p><p><br></p><p>ST: 04/07/2016:- In OCR400 Controller (G03IOIC) Active Scan Range is getting saved properly and associated Profibus and DeviceNet devices are getting scanned correctly in NetDevice Configuration tool. However in case of OCR1100 controller (G02IOIC) although&nbsp;Active Scan Range is saved properly but associated Profibus and DeviceNet devices are not getting scanned. Please refer the attached snapshots.</p><p><br></p><p>In view of this, the finding is being reopened for OCR1100 controllers.</p><p><br></p><p>ST: 04/11/2016:- As per developer's comments in Resolution field of this finding separate finding 36146 has been entered for this issue. So closing this finding.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U2 |  | <p>GEC Lab, Ov3.6.0_U0, </p><p>OCR400 (G03_IOIC):Drop24/74</p><p>DBS220</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>These master device configurations are passed to the Emerson ODM TCP Driver which stores the values in its own area (Registry?).&nbsp; The attachment netDevice.jpg shows that the Driver is installed (OCR400 TCP), however, the configuration settings are not being retained.&nbsp; The issue is likely in the ODM TCP Driver itself, and not the Ovation Developer Studio Engineering UI.</p><p><br></p><p>This is a different issue that what was reported in the original finding. The original finding should be closed and a new one opened. The original finding concerned a very specific registry issue that was corrected.</p><p><br></p><p><br></p><p><br></p> | 14 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Performed Below&nbsp;steps:</p><p>1. Added an I/O Driver and I/O Device&nbsp;for PROFIBUS module.</p><p>2.Added a PROFIBUS module to a slot and assigned a module point to it. &amp; assigned&nbsp;node points to its nodes. (P01 &amp; P02)</p><p>3. Clicked <strong>Engineer</strong> option from right click context menu of P01 port of module. SYCON tool opens</p><p>4. Added a WAGO device to the P01 segment and assigned a node point to the device.</p><p>5. Clicked <strong>Configuration&nbsp;</strong>option from right click context context menu of PROFIBUS master device, net Device configuration tool opens</p><p>6. Configured Active Scan Range ( IP start Address: <strong>192.168.26.24</strong> &amp; IP END address: <strong>192.168.26.74</strong>) and Scan Time (10000 ms)</p><p>&nbsp;of PROFIBUS module P01 port (master) from netDevice-Configuration tool and save the settings. Again reopen the netDevice-Configuration tool</p><p>&nbsp;for the same port of the module, previously saved settings will be set to default as IP start Address: <strong>0.0.0.0 </strong>&amp;<strong>&nbsp;</strong> IP END address: ---<strong>.---.---.---, </strong></p><p><strong>&nbsp;</strong>Scan Time: <strong>1500 ms</strong>. Please check the attached snapshot <strong>netDevice.jpg.</strong></p><p>7. Configured WAGO device and assigned a ovation point to one of digital inputs of WAGO device.</p><p>8. Saved settings and performed Download, Clear, Load operation to controller pair.</p><p>9. Ovation points quality is good but PORT status in controller diagnostic is showing OFFLINE.</p><p>10. Values of this ovation point is also not getting updated.</p> |  | U0 |  |  | FINDING | [6 empty] | 94700
34936 | FINDING | Few Discrepancies in Test case 3.6.0_SysViewer_SVTP_rev2.1 | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2015-11-09 05:27 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2015-11-09 05:27 | [7 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-09 04:03 |  | <p>1. In the section 5.4 of the test case 3.6.0_SysViewer_SVTP_rev2.1, <u>5.4.6.e</u>&nbsp;sequence no. &nbsp;is given to&nbsp; two different points.<strong> </strong></p><p>2. As per the document, in&nbsp;Section&nbsp;5.4..6.f, on selection of the DROP, Point Attributes window does not appear.(same in Ov3.5.2).</p><p>3. As per the document, in&nbsp;Section&nbsp;5.4..6.g, on selection of I/O Device X IOIC or Node or Slot, in the Status point Window, <strong>Mode option </strong>is not available.(may be by mistaken written in the document)</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Test Case 3.6.0_SysViewer_SVTP_rev2.1 |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U0 |  |  | FINDING | [6 empty] | 88173
34938 | FINDING | Ov-3.6.0_U0: OvSessionManager crashes on DBS drops upon Server reboot | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-16 07:18 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-16 07:18 |  |  |  | 2015-11-16 07:18 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-09 07:57 |  | <p>OvSessionManager crashes on both Ov-3.6.0_U0 DBS drops upon Server reboot.</p> <p>---</p> <p>Popup:&nbsp; </p> <p>OvSessionManager has stopped Working</p> <p>Probelm Event Name:&nbsp;&nbsp; APPCRASH</p> <p>---</p> <p>EventViewer -&gt; Application -&gt;&nbsp;Error:</p> <p>----------------------------</p><span lang=EN> <p>Faulting application name: OvSessionManager.exe, version: 3.6.0.61992, time stamp: 0x561f569e</p> <p>Faulting module name: ntdll.dll, version: 6.3.9600.18007, time stamp: 0x55c4bc8e</p> <p>Exception code: 0xc0000374</p> <p>Fault offset: 0x000e5904</p> <p>Faulting process id: 0xca4</p> <p>Faulting application start time: 0x01d11af3fab2a7e1</p> <p>Faulting application path: C:\Ovation\OvationBase\OvSessionManager.exe</p> <p>Faulting module path: C:\Windows\SYSTEM32\ntdll.dll</p> <p>Report Id: 44c098d6-86e7-11e5-80e9-549f3505bfc4</p> <p>Faulting package full name: </p> <p>Faulting package-relative application ID: </p></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | msb - 11/16 - Ok in Ov-3.6.0_U1 | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U0 |  |  | FINDING | [6 empty] | 88410
34939 | FINDING | Ov-3.6.0_U0 - Cannot use the Radius protocol to login to the Controllers | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-13 09:34 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-13 09:34 | 67647 |  |  | 2016-05-13 09:34 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-09 08:13 |  | <p>In Ov-3.6.0_U0 - We cannot use the Radius protocol to login to the Controllers.</p> <p>---</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">We followed steps of configuring RADIUS server (section 16, OW352_40) </span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">and tried logging to controllers through PUTTY&nbsp; </span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">Error&nbsp;from any Controller:</span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">&nbsp;&nbsp; “Network error: Connection refused”</span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>4/1 - Added sshd support and defined the default rsa and dsa key names.</p> <p>&nbsp;</p> <p>----</p> <p>&nbsp;</p> <p>msb - 4/15 - In U6: Partially failed</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp; </font><font size=3><font color="#000000"><font face=Calibri>Radius login to Controllers (via Putty – SSH) is now available </font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>&nbsp; On DC8:</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>&nbsp;&nbsp; &nbsp;Emily – Ov-3.6.0 Network (ID &amp; PW are not required in U6)</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>&nbsp;&nbsp;&nbsp; Dave – Ov-3.5.1 Network (ID: Administrator, PW: Ovation1 – are required)</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp;&nbsp;&nbsp; </font><font size=3><font color="#000000"><font face=Calibri>Only OCR1100 Controllers are currently active on both networks. No OCR400 Controllers</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp; On DC12:</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp;&nbsp;&nbsp; Tim - Ov-3.6.0 Network -</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ssh to OCR400 (43/93) failes, Err: Connection refused.</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; No OCR1100 Controllers.</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>---</font></p> <p>msb 5/13/2016 - Login using Radius (ssh by putty) is wotking for OCR1100 &amp; OCR400 in Ov-3.6.0_U7</p> | 10 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U0 |  |  | FINDING | [6 empty] | 96827
34943 | FINDING | SPD error seen for some points in Signal Diagram. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 7 | Lal, Ramesh External | 2016-03-18 06:34 | [11 empty] | Lal, Ramesh External | 2016-03-18 06:34 | 65903 |  |  | 2016-03-18 06:34 |  |  |  | Lal, Ramesh External | 2015-11-10 10:34 |  | <p>Created a control sheet for CalcBlockD algorithm. Originated 8 input points in controller Drop39/Drop89 e.g. D39-CALD-IN1&nbsp;~ D39-CALD-IN8. Saved the control sheet, compiled it and loaded the controller. When this sheet is opened in Signal Diagram Viewer it was observed that only points D39-CALD-IN1&nbsp;~ D39-CALD-IN4&nbsp; are originated correctly whereas for points D39-CALD-IN5&nbsp;~ D39-CALD-IN8&nbsp;&nbsp;there is error &nbsp;&quot;The specified point is not in the SPD&quot;. These points will not show up in Pont Info. </p><p>The problem is not consistent. Sometimes all the points are originated correctly. It may be noted that similar problem was noticed in Ovation 3.5.2 as well.</p><p>Please refer the attached snapshot for reference.</p> |  |  |  | <p>Clear the MMI before running any tests.</p><p><br></p><p>follow the procedure above in steps to reproduce.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>The xmit server has been updated in U2.&nbsp; </p><p><br></p><p>To correct current condition, Clear any and all MMIs that are experiencing this issue.</p><p><br></p><p>Retest by creating a new sheet and loading the controller.</p><p><br></p><p>If it is NOT this repeatable in U2 ...</p><blockquote style="margin-right:0px;" dir=ltr><p>Mark the finding as monitoring and close it in 4 weeks.<br></p></blockquote><p>If it is repeatable in U2 ....</p><blockquote style="margin-right:0px;" dir=ltr><p>Mark the finding as failed retest.</p><p>Note the local time of the load that failed in the description.</p><p>Attach the ovation error logs of the database server and mmi.</p><p>Attach the xmitserver.out from the server.</p></blockquote><p>2/05/2016: RL- Tested in 3.6.0_U2. The control sheet which was giving problem looked O.K. on DBS and EWS</p><p>Tested in 3.6.0_U3. The control sheet which was giving problem looked O.K. on DBS and EWS</p><p>Created new control sheet. It works fine on Database Server.&nbsp;But SPD&nbsp;error was reported on&nbsp;EWS. However, after clearing EWS the problem was solved.</p><p>Therefore, this finding is not fully fixed. </p><p>The local time of Controller load: 10:43 AM. on 5-Feb-2016</p><p>Ovation Error log on dbs: DBS_Drop135_Error_020516 attached</p><p>Ovation Error log on EWS: EWS_Drop126_Error_020516 attached</p><p>XmiServer.out : attached.</p><p><br></p><p>3/18/2016:RL - Retested in 3.6.0_U4 and found OK. Finding closed.<br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  | <p>Ovation 3.6.0, EWS Win 7 SP1, 64 bit</p> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  |  | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a control sheet for CalcBlockD algorithm. </p><p>2. Originate 8 input points in controller.</p><p>3. Save the control sheet, compile it and load the controller.</p><p>4.&nbsp;Open this sheet&nbsp; in Signal Diagram Viewer.</p><p>5. You will noticed that for few points there is an error&nbsp;&quot;The specified point is not in the SPD&quot;. </p><p>6. Open Point Info.These points will not show up in Pont Info. </p> |  | 3.6.0_U0 |  |  | FINDING | [6 empty] | 93537
34955 | FINDING | Virtual Controller WRTAP can not be installed on Windows Server 2012 R2 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-02 09:38 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-02 09:38 |  |  |  | 2016-05-02 09:38 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-11 11:00 |  | <p>Virtual Controllers can not be configured on Windows Server 2012 R2.&nbsp; This OS is <u>required</u> for DBS and is also valid for and EWS. The wrtap installation fails with only the message 'Installation failed'.&nbsp;</p><p>MP 11/12/15 - This was tracked down to the .inf file.&nbsp; Having the max_buffers set to 2000 causes this issue on 2012 R2. Modifying the .inf file to 20 (the original value) allows the driver to install, but 2000 is the required value.&nbsp; The driver does install properly with 2000 on Windows 7.</p><p>MP 5/2/16 - The wrtap can be installed in U6.&nbsp; The inf file is set to have the max_buffers to 20.&nbsp;&nbsp; The document has been updated to have the user configure the max_buffers manually to 2000.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Shiferaw, Tedla AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | Windows Server 2012 R2 + Ovation 3.6.0 U0 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Run wrtap64.bat.&nbsp; View results from wrtapinstaller.exe. |  | U0 |  |  | FINDING | [6 empty] | 96049
34968 | FINDING | Fieldbus module download causes module to be inoperative | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wood, Thomas T AUTOSOL PWS PITT | 2016-03-07 09:29 | [11 empty] | Wood, Thomas T AUTOSOL PWS PITT | 2016-03-07 09:29 | 64817, 65410 |  |  | 2016-03-07 09:29 |  |  |  | Wood, Thomas T AUTOSOL PWS PITT | 2015-11-13 09:26 |  | The latest firmware was downloaded to the fieldbus modules and after they were rebooted the modules did not recover. |  |  |  | <p>If the Fieldbus module is currently inoperative, you will have to follow the process for bus module recovery before retesting the firmware.</p><p><br></p><p>Download firmware and verify the fieldbus module boots.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="color:rgb(31, 73, 125);"><font face=Arial size=3>, the “ovation_xxx.x” files are part of the at91 BSP because the boards contain FPGAs. The ovation files provide the support for those FPGAs. FPGA support belongs in the BSP, not in the application layer. That way the application doesn’t have to change when running on different platforms (e.g. the node software currently runs on at91 and p1010, and will also run on the xynq.)</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="color:rgb(31, 73, 125);"><font face=Arial size=3>The at91 board is used in both module and node applications and the FPGAs are different in the different applications. There are separate kernel projects for modules and nodes. The module kernel is configured to include support for the module FPGAs, and the node kernel is configured to include support for the node FPGAs.</font></span></p><font face="Times New Roman" size=3> </font> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  | The kernel project was missing some files.&nbsp; However, after the kernel project was fixed, there was a SIGBUS violation in one of the fieldbus tasks (TS_FF_CONFIRMATIONS).&nbsp; This looks to be due to some kind of memory alignment issue, right now the fix is to add padding to the structure that was producing the violation, however, if more SIGBUS errors occur, then we probably need to address something in the compiler. | 9 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U0 |  |  | FINDING | [6 empty] | 93028
34979 | FINDING | Control builder is crashing when user canceled add an algorithm with a right click or ESC. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 22:02 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 22:02 | 64763 |  |  | 2015-12-21 22:02 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-16 22:57 |  | Control builder is crashing when user canceled&nbsp;add an algorithm with a right click.. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,Win7</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB-12/22/15: Verified on Ovation 3.6.0_U2 and observed that Control builder is not&nbsp;crashing when user canceled&nbsp;add an algorithm with a right click.Hence this finding is closed by validation.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce</p><p>1)Make a control sheet.</p><p>2)Open the control sheet and select an algorithm say&nbsp;AND gate&nbsp;from add control algorithm library.</p><p>3)Before dropping the algorithm on control sheet, just <strong><em>right click</em></strong> on control sheet cause control builder to crash.</p><p>Screenshot is also attached for your reference.</p><p>&nbsp;</p> |  | U1 |  |  | FINDING | [6 empty] | 90066
34980 | FINDING | Lines in Images are light grey for preview and recover window | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 22:16 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 22:16 | 65018 |  |  | 2015-12-21 22:16 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 00:07 |  | <p style="margin-right:0px;" dir=ltr>when user open the same control sheet twice. cbEditor displays message &quot;The file you tried to open is locked by administrator&quot; user selects unlock. after this cbEditor ask for recovering the file at this instance images of original version of the file and recovered version of file is not visible clearly . In addition&nbsp;to this when user tries to open the file &nbsp;from control builder&gt;file&gt;open&gt;select any sheet on right hand side and observe the preview image on left hand side. Image will not visible clearly.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>Ovation 3.6.0_U1.</p><p>OS-Win7,WS12</p><p>&nbsp;</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-12/22/15: Verified on Ovation 3.6.0_U2 and observed that Lines in Images are&nbsp;black for preview and recover window. Hence this finding is closed by validation. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Following are the steps to reproduce.</p><p>1)Make a control sheet and add an algorithm.</p><p>2)Open the control sheet.</p><p>3)Try to open the same control sheet again. cbEditor displays message &quot;The file you tried to open is locked by administrator&quot; select unlock. after this cbEditor ask for recovering the file at this instance images of original version of the file and recovered version of file is not visible clearly.</p><p>Screenshot is also attached for your reference</p> |  | U1 |  |  | FINDING | [6 empty] | 90068
34981 | FINDING | Some Algorithm Slides have white backgrounds with clipped boarders | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2015-12-01 14:03 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2015-12-01 14:03 |  |  |  | 2015-12-01 14:03 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 00:22 |  | <p>Algorithm symbols are indicated with different background or shapes on&nbsp;Control algorithm Library.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1.</p><p>OS-Win7,WS12</p><p>&nbsp;</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB 11/18/15-In Ovation 3.5.2 and earlier releases all algorithms are&nbsp;indicated by a common background and borders.</p><p>LB 11/18/15-All algorithm are indicated by a common background and borders in earlier releases to provide a consistent appearance. but in ovation 3.6.0 algorithm are indicated by different and incomplete background and borders. Please verify the background and borders of all algorithm available on ovation 3.6.0.</p><p>LB 11/19/15-Problem got fixed after Deleting all the PNGs under the C:\Ovation\CtrlBldr\Symbols.</p><p><br></p><p><br></p><p>Is this fixed?</p><p>LB 11/27/15-Yes,Problem got fixed after Deleting all the PNGs under the C:\Ovation\CtrlBldr\Symbols.</p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Verify the shapes and symbols of algorithm available on Control algorithm Library.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 89123
34982 | FINDING | Algorithm anchors functionality of control builder application not working properly | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-02-07 21:11 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-02-07 21:11 | 65018 |  |  | 2016-02-07 21:11 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-11-17 00:29 |  | It has been observed that after selecting multiple algorithm in a control sheet, algorithm anchors of the individual algorithm are visible, but after clicking on the&nbsp;blank area of the control builder, anchors will not be visible on the algorithms and moves to some other location of the control sheet. Same behaviour is observed with the selection of single algorithm also. Please check the attached snapshot. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>GEC Lab,</p><p>Drop220, DBS, Ov3.6.0_U1,</p><p>Controller OCR400 Drop24/74</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | ST:12/23/2015: Checked the functionality on Drop127 having Ovation3.6.0_U2 build installed and is working fine. So closing this finding. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Performed below mentioned steps:</p><p>1. Insert a control sheet to any control task of the controller.</p><p>2. Add multiple or single algorithm to the sheet.</p><p>3. select multiple or single algorithms.</p><p>4. click on the blank area of the sheet. anchors of the algorithms will move to some other location.</p><p><br></p> |  | U1 |  |  | FINDING | [6 empty] | 91976
34983 | FINDING | 'SURE SERVICE " title is missing on OSR window. | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:30 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:30 |  |  |  | 2016-05-13 04:30 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 00:47 |  | &quot;SURE SERVICE &quot;&nbsp;title line is missing on OSR window. Also icon of&nbsp;OSR is different. |  |  |  | <p><br></p><p>MM(4/25/16): Check section 3.1.2 and 3.1.9 in the OW360_11.pdf. Check the pdf at : \\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</p><p>Screen shots have been changed. Check the online help too.</p> | 0 |  |  |  | LB 05/13/16-Verified on Ovation3.6.0_U7 and observed that OSR help is updated with latest OSR images. Hence this finding is closed by validation | 0 |  | Ovation for Windows/System Registration Utility/Documentation | <p><br></p><p>MM(4/25/16): Check section 3.1.2 and 3.1.9 in the OW360_11.pdf. Check the pdf at : \\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</p><p>Screen shots have been changed. Check the online help too.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | <p>Ovation 3.6.0_U1.</p><p>OS-WS12</p><p>&nbsp;</p> |  | Ovation for Windows | Ovation | System Registration Utility | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>In September we were told about the Emerson Process Management Branding Initiative.&nbsp; They looked at our software and told us to take out the SureService logo.</p><p>We said in the weekly 3.6.0 meeting we will be putting in the new icons for the 3.6.0 system.&nbsp; This is it's new icon.</p><p><br></p><p>&nbsp;</p><p>LB 11/18/15- Good to know about this. Since you are removing the SureService logo and new icons are used .So all the documents related to&nbsp;this needs to updated. So instead of closing this finding you can move it to documentation.</p><p><br></p><p>kac- Since this finding was incorrectly classified the originator can change it to documentation.</p><p>&nbsp;</p><p>LB 11/19/15-Changed the problem type as documentation.</p><p><br></p><p>MM(4/25/16): The fix will be available in 3.6.0_U7 built.&nbsp;</p><p><br></p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Verify the icon of OSR. Launch the OSR and verify the information available on OSR window.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 96772
34984 | FINDING | User encountered an error “Cell output is not connected” when tries to connect parallel input on ladder advanced edit window. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-18 04:13 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-18 04:13 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 02:48 |  | <font face="Times New Roman" size=3> </font><span style="color:rgb(79, 129, 189);"><font size=3><font face=Calibri>User encountered an error “Cell output is not connected”&nbsp;when&nbsp; tries to connect parallel input on ladder advanced edit window. Same thing tried on ovation 3.5.2 and ovation 3.5.1 and observed that user can easily connect the parallel input in ladder advanced edit window.</font></font></span><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(79, 129, 189);"><font face=Calibri size=3>&nbsp;</font></span></p><span style="color:rgb(79, 129, 189);"><font face=Calibri><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font size=3>I have few more observations:</font></span></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font color="#000000" face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><font size=3>1) While exporting the ladder file nothing is available on save as type option pull down menu.</font></span></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font color="#000000" face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><font size=3>2) While importing the ladder file, Ladder is unable to identify the file kept inside the folder.</font></span></p></font><p class=MsoNormal style="margin:0in 0in 0pt;"><font color="#000000" face="Times New Roman" size=3> </font></p></span><p class=MsoNormal style="margin:0in 0in 0pt;">&nbsp;</p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p><span style="color:rgb(79, 129, 189);"><font size=3><font face=Calibri>Ovation 3.6.0_U1</font></font></span></p><p><span style="color:rgb(79, 129, 189);"><font face=Calibri size=3>OS-WS12,Win7</font></span></p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(79, 129, 189);"><font size=3><font face=Calibri>Steps to recreate-</font></font></span></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(79, 129, 189);"><font size=3><font face=Calibri>1) Make a control sheet and add LADDER algorithm. Right click on LADDER algorithm and select advanced edit.</font></font></span></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(79, 129, 189);"><font size=3><font face=Calibri>2) After this new window will open, try to connect parallel input.</font></font></span></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;"><span style="color:rgb(79, 129, 189);"><font face=Calibri size=3>Screenshot is also attached for your reference.</font></span></p><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 88555
34985 | FINDING | Algorithms Select parameter filter operation not working properly | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-12-22 22:22 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-12-22 22:22 | 65018 |  |  | 2015-12-22 22:22 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-11-17 03:31 |  | <p>Selecting any of the options&nbsp;like <strong>Add&nbsp;Control Pin, Algorithm Value, Point Description, Point reference, Algorithm Value Indicator, Point Status Indicator</strong>&nbsp; from right click context menu of an algorithm, &nbsp;<strong>Select Parameter window</strong> appears, it has been observed that <strong>Filters </strong>for Input, Output, Dual Parameter etc. is not working properly. Suppose performing Add Control Pin operation, if only Input filter is selected in the select parameter window, only input pins&nbsp;which are not added to the algorithm should be available in the left pane of the select parameter window, but window shows other parameters also. Same behaviour can be seen for other operations like Algorithm value, Point Description etc. also. Please check the attached snapshot.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>GEC Lab, Ov3.6.0_U1,</p><p>Drop220, DBS, Controller Drop24/74</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | ST:12/23/2015: Checked the functionality on Drop127 having Ovation3.6.0_U2 build installed and is working fine. So closing this finding. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Performed below mentioned operations:</p><p>1. Add a control sheet to any of the control task area of a controller.</p><p>2. Add an algorithm to it for example: AND algorithm having three inputs.</p><p>3. Right click and select Algorithm Value options, Select Parameter window appears having all the filters selected.</p><p>4. Deselect Input Filter option, from the left pane of window all the inputs should disappear but inputs are still visible.</p><p>5. Same behaviour is also observed&nbsp;for other filter options also.</p> |  | U1 |  |  | FINDING | [6 empty] | 90106
34986 | FINDING | Error Appears when a File->Print Report operation is canceled. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-25 03:29 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-25 03:29 | 65018 |  |  | 2016-04-02 06:01 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2015-11-17 04:30 |  | <p>It has been observed that while performing Print Report Operation for <strong>Algorithm Details, Connector Information, Execution Order or Title Page </strong>of a control sheet from File menu option of control builder application, if the operation is cancelled in between (before completing the operation) some errors for different input/output external points appears in error list as<strong> &quot;Unit not found in database&quot; or No Active Unit available.&nbsp;</strong>Please note that before performing this operation sheet was not having any errors. <strong>This issue has been observed only on engineering station drops (EWS). </strong>Please check the attached snapshots</p> |  |  |  |  | 0 |  |  |  | <p>ST(05/25/2016): Closed the control builder and reopened the sheet, again error appears when File-&gt; Print operation is cancelled. Other engineers are doing basic&nbsp;engineering and operator function testing on the system. Please find the below mentioned remote login details if you want to investigate further.</p><p><font face="Times New Roman" size=3> </font><b style=""><font face=Calibri size=3>Gateway Drop: </font></b></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>IP Address: 10.132.184.7</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>User Name: Administrator</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Password: Welcome@1234</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Domain: Val9Dc9</font></p><font face=Calibri size=3><p><strong>Ovation3.6.0 Net26 DBS Drop220:</strong></p><p><font face=Calibri size=3>IP Address: 192.168.26.220</font></p><p><font face=Calibri size=3>User Name: Administrator</font></p><p><font face="Times New Roman" size=3></font><font face=Calibri size=3>Password: Welcome@1234</font></p><p><font face="Times New Roman" size=3></font><font face=Calibri size=3>Domain: Val26Dc26</font></p></font><p><b style=""><font face=Calibri size=3>Ovation3.6.0 Net26 EWS Drop195:</font></b></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>IP Address: 192.168.26.195</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>User Name: Administrator</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Password: Welcome@1234</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Domain: Val26Dc26</font></p><p><font face="Times New Roman" size=3> <br></font></p> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  | <p>GEC Lab, Ov3.6.0_U1</p><p>Drop195, W7#64bit, EWS,</p><p>Controller OCR400 Drop24/74</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>Please retest with U3.&nbsp; I think this is fixed as the result of other changes.</p><p>ST(02/05/2016): Retested with U3, issue is still there.</p><p><br></p><p>SBH 3/29/2016 - Please Retest - Tested in U4 cannot duplicate.</p><p><br></p><p>ST(04/02/2016): Retested with U4, issue got resolved. So closing this finding.</p><p><br></p><p>ST(04/14/2016): I was doing some basic functionality testing on EWS drop, checked this functionality issue again appears with U6 build. So reopening this finding.</p> | 14 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Performed below mentioned steps:</p><p>1. Add a control sheet to any of the control task area of a controller from an Engineering station drop.</p><p>2. add some algorithms and external points (Input and Output points)&nbsp;in the sheet and compile the sheet to make it error free.</p><p>3. From File menu--&gt; Print Report option Click on any of Algorithm Details, Connector Information, Execution Order or Title Page options.</p><p>4. Print Operation window appears, click cancel button.</p><p>5. Error for different external points appears in the error list. </p> |  | U1 |  |  | FINDING | [6 empty] | 97673
34987 | FINDING | OSR is unable to report some installed software details. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 03:16 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 03:16 | 67587, 67621, 67622, 67634 | [6 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 04:48 |  | Some installed softwares like Kaspersky Endpoint Security 10 for windows, Lumension End point management and security suite agent,&nbsp;&nbsp;Microsoft Visual C++ 2010 x64 redistributable are not reported by OSR.&nbsp; In addition to this Microsoft .Net framework 4.5.1,Microsoft Silverlight, Microsoft Visual C++ 2008 x64 redistributable, Intel (R) Network connections drivers are also not reported by OSR. |  |  |  |  | 0 |  |  |  | LB 05/17/16-Verified on Ovation 3.6.0_U7 and observed that OSR is still not reporting Microsoft Silverlight, Lumension End point management and security suite agent,&nbsp;Microsoft Visual C++ 2010 x64 redistributable, Microsoft Visual C++ 2008 x64 redistributable,Intel (R) Network connections. OSR Report is also attached for your reference. | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS2012.Win07.</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Generate the OSR report.</p><p>2)Verify the report with installed software details.</p> |  | U1 |  |  | FINDING | [6 empty] | 97027
34988 | FINDING | OSR is reporting wrong software details. | Buzza, Sheri AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-22 04:02 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-22 04:02 | 67077 |  |  | 2016-04-22 04:02 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-17 04:55 |  | <p>In drop220 and drop100 Internet explorer 11 is installed but OSR is reporting it as Internet explorer 9.</p> |  |  |  |  | 0 |  |  |  | <p>LB 04/22/16-Verified on ovation3.6.0_U6 and observed that correct version of Internet explorer was printed on OSR report. Hence this finding is closed by validation</p> | 0 |  | Ovation for Windows/System Registration Utility/Software | 2016-04-21 RStaab: The SRU now reports the version according to IE's svcVersion registry key under:<div>HKEY_LOCAL_MACHINE\SOFTWARE\Microsoft\Internet Explorer</div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Staab, Randy AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U5 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS2012.</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Generate the OSR report.</p><p>2)Verify the report with installed software details.</p> |  | U1 |  |  | FINDING | [6 empty] | 95424
34989 | FINDING | Some Test Cases of 3.6.0_SysViewer_SVTP_rev2.1_xxx cannot be tested and testcases needs corrections | Joshi, Parmesh EMR SYSS PWS NOIDA | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Joshi, Parmesh EMR SYSS PWS NOIDA | 2018-12-10 03:09 | [11 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2018-12-10 03:09 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-17 05:11 |  | <p>Following test cases of TR &quot;3.6.0_SysViewer_SVTP_rev2.1_xx&quot; needs some modifications.</p> <p>&nbsp;</p> <p>1. Testcase 5.5.3-a</p> <p><span style="FONT-SIZE:10pt;FONT-FAMILY:'Times New Roman','serif';"><font color="#000000" face="Segoe UI">If an Ovation Drop is configured as Historian, it’s status is visible in System Viewer (similar to other Ovation Drops) but&nbsp;if an External&nbsp;Historian is configured, then only it’s status is not visible in System Viewer.</font></span></p> <p><span style="FONT-SIZE:10pt;FONT-FAMILY:'Times New Roman','serif';"><font color="#000000" face="Segoe UI">So testcase should mention to verify this step for External Historian only.</font></span></p> <p>&nbsp;</p> <p>2. Testcase 5.6.1-a and 5.7.1-b<br>Where used functions are not available in System Viewer application.</p> <p>&nbsp;</p> <p>3. Testcase 5.6.1-g<br>Word 'and' should be removed from the sentence as it creates confusion.<br>Additionally following sub-testcases can be added:<br>&nbsp; i) Verify when cursor is hovered on Drop Status, Status Codes pop up is displayed.<br>&nbsp; ii) Verify whenever cursor is hovered on Fault Code, Fault Info pop up for the selected Drop is displayed </p> <p>&nbsp;</p> <p>4. <span style="FONT-SIZE:11pt;FONT-FAMILY:'Calibri','sans-serif';"><font color="#000000">Test Case 5.7.1-d </font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:'Calibri','sans-serif';"><font color="#000000">Remove this section from SVTP as it is not applicable.</font></span></p> <p>&nbsp;</p> <p>5. Testcase 5.8<br>Numbering of test cases (a to l) is incorrect, numbering h and i are repeated which should be continued with j and k.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Operator Station/System Viewer | SVTP/STP | In Validation | 3.6.0 |  |  | Released to Library | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | PJ 12/10/2018&gt; Attached SVTP rev 2.3 addresses the issue. Please verify | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 135365
34990 | FINDING | Pin/Unpin button for grid is not available in System Viewer. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:29 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:29 |  |  |  | 2015-12-18 09:29 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-17 05:17 |  | <p>Section 5.8 Testcase8: SysViewer-Sorting and Filtering, step 5.8-h<br>Pin/Unpin button for grid is not available in System Viewer.</p><p><br></p><p>for the 3.6.0 release:</p><p>this is the way&nbsp; it works. <span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">Only the hierarchy can be pinned and unpinned.</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | In Validation | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 89944
34991 | FINDING | Option to change height of Hierarchy not available in System Viewer | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:28 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:28 |  |  |  | 2015-12-18 09:28 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-17 05:21 |  | <p>Section 5.8 Testcase8: SysViewer-Sorting and Filtering, step 5.8-i-i<br>Height of Hierarchy cannot be changed. However, width is changeable.</p><p><br></p><p>for the 3.6.0 release:</p><p>this is the way it works</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1. Go to Heirarchy area in System Viewer and try to change the height of Heirarchy by drag-drop at the top or bottom of the Heirarchy area. By drag and drop at the bottom of Heirarchy area, the height of Heirarchy Area and Grid area changes altogether.<br>2. Go to Heirarchy area in System Viewer and try to change the width of Heirarchy by drag-drop at the right end of the Heirarchy area. The width of Heirarchy Area area alone changes. | EPM Validation | U1 |  |  | FINDING | [6 empty] | 89943
34992 | FINDING | Option to dock-undock the gird is not available in System Viewer | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:27 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2015-12-18 09:27 |  |  |  | 2015-12-18 09:27 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-17 05:23 |  | <p>Section 5.8 Testcase8: SysViewer-Sorting and Filtering, step 5.8-j<br>Grid can be moved but cannot be redocked. Basically Grid cannot be un-docked.</p><p><br></p><p>for the 3.6.0 release:</p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">the grid is not supposed to be redocked using a double click.</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">the grid can be undocked by using the left mouse on a tab and dragging it to the appropriate area.</span></span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">Please see the documentation for the system viewer (dockable tabs) for more details.</span></span></span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><br></span></span></span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><br></span></span></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Try to un-dock the grid by double click followed by dragging the grid bar. It is not possible to un-dock the grid. | EPM Validation | U1 |  |  | FINDING | [6 empty] | 89942
34995 | FINDING | Ov-3.6.0 - Big system (>200k Pts) may not perform DBxmit distribution after upgrade | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2015-12-21 08:16 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2015-12-21 08:16 |  |  |  | 2015-12-21 08:16 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2015-11-17 10:08 |  | <p>Ov-3.6.0 - Big system (&gt;200k Pts) - Emily Network in Pgh does not perform DBxmit distribution to the DBS</p> <p>and Opstations after upgarde to U1.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>msb 11/18 - new &quot;db_xmit_client.exe 11/17/2015 1:49 pm&nbsp; 62 kb&quot; was manually placed&nbsp;in C:\Ovation\OvationBase on all Emily's Workstations</p> <p>&nbsp;to resolve issue in Ov-3.6.0_U1.</p> <p>---</p> <p>msb 12/21 - OK in Ov-3.6.0_U2&nbsp;</p> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U1 |  |  | FINDING | [6 empty] | 90037
35001 | FINDING | Discrepancy in System Viewer on DBS drop100 (NET#36) | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 15:45 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 15:45 |  |  |  | 2016-06-08 08:22 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-18 00:14 |  | <p>Discrepancy in System Viewer in DBS (NET#36), , </p><p>1. On the selection of any I/O points in the System Viewer, the Right Click context menu appears non-functional for some features like&nbsp;Point Information, Trend, Developer Studio.</p><p>This discrepancy is seen exclusively on the NET#36 DBS i.e. Drop100. </p><p>Clients of the NET#36 DBS are working fine and so&nbsp;are NET#26 DBS+DC and its clients. </p><p>For Remote Login details, refer attached file.</p><p><font face="Times New Roman" size=3><br></font></p><p style="margin:0in 0in 0pt;"><u><span style="color:black;font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3></font></span></u></p><p><span><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</font></span></p><p><font face="Times New Roman" size=3> <br></font></p> | IC 6/8/16&gt; Only KAV 10 SP1 must be used with 3.6.0. |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software | After uninstalling KES 10 (antivirus) from the drop100, the problem is resolved. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | DBS drop100 with Server 2012R2 |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | IC 1/5/16 per discussion with OSC team, we should require Ovation 3.6.0 users to use KAV 10 SP1 only (not KAV 10) to avoid this issue.<br>Also, an issue related to the Alarm Viewer has been observed when KAV 10 was installed but not with KAV 10 SP1 installed. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install &amp; configure the module in Developer studio.</p><p>2. Configure a point (AI/AO/DI/DO).</p><p>3.Open the System viewer.</p><p>4. Select the configured Point, right click and try to open right context menu features.</p> |  | U1 |  |  | FINDING | [6 empty] | 98434
35008 | FINDING | License Manager becomes non-functional on EWS after OPC CLM 1.11 is installed on it. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2015-12-08 09:23 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2015-12-08 09:23 |  |  |  | 2015-12-08 09:23 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-11-19 03:10 |  | <p>The license manager is confirmed to be working on EWS.</p><p>After installation of OPC CLM 1.11 on EWS, the License Manager available in Dev. studio display a message &lt;Unable to find an entry point named &quot;VLScontrolRemoteSession&quot; in DLL &quot;lsapiw33.dll&quot;&gt;</p><p><br></p><p>This is true for both DBS Net#26 which has OPC CLM license &amp; DBS Net#36 which does not have the OPC CLM license. </p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p>OV3.6.0_ U1&nbsp;; </p><p>OS W764B ; </p><p>OPC CLM 1.11 ;</p> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>New version of OPC CLM is required, you were not supposed to test with this version.</p><p>PS 7Dec15: As per &quot;3.6.0_STP_rev1.1&quot;, The validation was to be performed with OPCDAS4.1 &amp; OPC CLM1.11.</p><p>Hence this finding is re-opened and kept under monitoring till next version of OPC CLM is available.</p><p>IC 12/8/15&gt; CAT 2 is confusing metrics, close and re-open if issue exists with new CLM version. </p><p><br></p><p><br></p> | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Step1&gt; Open Dev. Studio , verify licensing is working fine.<br>Step2&gt; Install optional software OPC CLM 1.11. (this fetches license from DBS drop)<br>Step3&gt; After successful installation, open&nbsp;Dev.Studio -&gt;&nbsp;License Manager&nbsp;a message &lt;Unable to find an entry point named &quot;VLScontrolRemoteSession&quot; in DLL &quot;lsapiw33.dll&quot;&gt; is displayed. <br>Step4&gt; Click OK the popup window disappears and license manager exits. License Manager unable to open.jpg is attached for reference.<br></p> |  | U1 |  |  | FINDING | [6 empty] | 89431
35009 | FINDING | Ovation OPC Data Access Service is stopped when an item is added to OPC client. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-12-07 03:01 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-12-07 03:01 |  |  |  | 2015-12-07 03:01 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-11-19 03:18 |  | Adding points to the group in the OPC server returns error &quot;0x800706be&quot; and Ovation OPC Data Access Service is stopped. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p>OV3.6.0_ U1 ; <br>OS W764B ;&nbsp; OS WS2012R2<br>OPC CLM 1.11 ;</p><p>OPCDAS 4.1</p> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>New version of OPC&nbsp;DA is required, you were not supposed to test with this version.</p><p>PS 7Dec15: As per &quot;3.6.0_STP_rev1.1&quot;, The validation was to be performed with OPCDAS4.1 &amp; OPC CLM1.11.</p><p>However, a new version of OPCDAS 4.2 is available and the issue is no longer seen. Hence finding is Closed.</p> | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Step1&gt; Add Server to the OPC Client.<br>Step2&gt; Add Group to the server.<br>Step3&gt; Connect the server. The Ovation Error log confirms that OPC Server is connected.<br>Step4&gt; Add Item to the group. This gives PWSOPCClient pop-up message as &lt;Error 0x800706be returned when adding item&gt;. The error log shows Killed Orphan User message. And the Ovation OPC data Acess Service Configuration Window shows service as stopped.<br> |  | U1 |  |  | FINDING | [6 empty] | 89312
35010 | FINDING | Ovation OPC Configuration tool crashes on browsing the ovation field in OPC CLM. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | McMaster, James External Artech | 2015-11-27 09:28 | [11 empty] | McMaster, James External Artech | 2015-11-27 09:28 |  |  |  | 2015-11-27 09:28 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-11-19 03:23 |  | Ovation OPC Configuration tool crashes on browsing the ovation field in OPC CLM. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | OV3.6.0_ U1 ; <br>OS W764B ; <br>OPC CLM 1.11 ; |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>New version of OPC CLM is required, you were not supposed to test with this version</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Step1&gt;Open Ovation OPC Configuration tool.<br>Step2&gt; Add Group to the server.<br>Step3&gt; Connect the server. The Ovation Error log confirms that OPC Server is connected.<br>Step4&gt; Add item -&gt; OK. Now, Browse OPC item ID -&gt; OK. Now, Browse Ovation Point to be mapped -&gt; OK. Now, Browse Ovation Field -&gt; This crashes the OPC Config tool. Attached CLM stopped working.jpg for reference. The error log shows Killed Orphan User message. |  | U1 |  |  | FINDING | [6 empty] | 89004
35011 | FINDING | drop loader is passing consistency check when a hardware node (Local QLine) is missing a node point. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Swartz, Mark EMR SYSS PWS PITT | 2015-11-19 07:50 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2015-11-19 07:50 |  |  |  | 2015-11-19 07:50 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-19 04:07 |  | If we configure hardware nodes such as an IOIC and Remote I/O nodes, the node record points that are required to monitor them should be there and attached to the physical hardware defined in studio. If these points are not build and connected to the hardware then the controller may not work as expected. If an IOIC is missing a node record it will load and when rebooted it will not be able to going into control. If a remote node is built without a node record to monitor it, it will run fine until a failure mode occurs and since there is no point to monitor the remote node the controller cannot fail over to the backup, since it dos not know the failure has occurred. Since this is required for proper operation developers studio should not allow a drop load to occur with these properly configured. drop loader consistency check is working fine for IOIC,Remote I/O nodes Ovation SIS, and Ovation SIS CHARMs. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U1 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Per information from controller group, if a Node record is assigned to I/O Interface 3 localQline and there is no other configuration/hardware associated with the interface, the controller will fail.&nbsp; As such, the consistency check would have to take into consideration that extra hardware actually exists in the controller.&nbsp; Since this is associated with the infrequently used Q-Line interface, the additional special-case consistency checks are not being included.&nbsp; </p><p><br></p><p>This extra check will not be added until the additional information requested in the applicable SDR 34596 has been supplied.</p> | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Following are the steps to reproduce.</p><p>1) Open the developer studio select a controller drop and add I/O device as I/O device number 0 and I/O device type IOIC.</p><p>2)Do not add node record point name on I/O Interface 3 localQline.</p><p>3)Perform consistency check operation on that particular drop.</p> |  | U1 |  |  | FINDING | [6 empty] | 88604
35014 | FINDING | Rebooting of the redundant virtual controller that is in control leaves a period where no one is in control. | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-15 10:31 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-15 10:31 | 65048 |  |  | 2016-01-15 10:31 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-19 10:20 |  | Rebooting of&nbsp;the redundant virtual controller that is in control leaves a period where no one is in control.&nbsp; <br>After rebooting the 'in control' VC, the backup takes over, but then reboots when the partner starts coming back on the highway.<br> At this point it is still in startup mode. This causes neither of the VCs to be in control for a few seconds.&nbsp; The 'backup' controller should not be rebooting at all during this process. |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Shiferaw, Tedla AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U2 |  | Ovation 3.6.0 U1 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>IC 1/13/16&gt; updated Planned Release = U2 as was in RR. RR should not be used/created for Findings since Findings are a release record themselves.</p><p><br></p><p>MP 1/15/15 - Retested in U2. The described problem appears to be fixed. The partner drop is not rebooting as described. But bumpless failover is not occurring. Trended values revert to 0 on failover. A new finding will be created for this matter. </p> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Create the 'in control' VC of&nbsp; a redundant pair.&nbsp; Reboot the primary VC and view the system status to see that for some reason the partner reboots also and that there is a time where no VC is in control. |  | U1 |  |  | FINDING | [6 empty] | 91244
35015 | FINDING | Previously saved snapshots are loaded incorrectly by SimControl 'Load' command | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:54 | [11 empty] | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:54 | [7 empty] | Lal, Ramesh External | 2015-11-19 15:25 |  | Drop24/Drop74 (OCR400) are defined as Redundant Sim Controllers. Point simulation&nbsp;is working fine. SimControl GUI commands e.g. Freeze, Save,&nbsp;Run are also working. However, Load command doesn't load previously saved snapshot&nbsp;correctly&nbsp;if multiple snapshots were saved. For example:&nbsp;if there are&nbsp;snapshots AV000, AV001, AV002, AV003 and an attempt is made to load AV001 it will load with values which were saved in AV000, if AV002 is loaded it will load with values of AV001 and so on. Please refer attached document whish may help to understand the issue. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Sim Operator Station: Win7&nbsp; 64 bit, Controllers : OCR400 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.&nbsp; Defined&nbsp; Redundant Sim Controllers e.g. Drop24/Drop64</p><p>2.&nbsp;&nbsp;Configure&nbsp; simulation points and make sure simulation is working</p><p>3.&nbsp; Save snapshots with different point values e.g. AV000, AV001, AV002, AV003 ...</p><p>4. Load snapshot say AV002, it will load with values saved in snapshot AV001.</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 94065
35016 | FINDING | Sim Control commands do not show acknowlegement messages from receiving drops in SimControl GUI | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:54 | [11 empty] | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:54 | [7 empty] | Lal, Ramesh External | 2015-11-19 15:42 |  | <p>In Sim Control GUI there are no acknowledgement messages from sim controllers when Freeze, Save , Load, Run command is given to simulator controllers. The sim Controllers are listed in drops.cfg file.</p><p>Refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Sim Operator Station: Win 7, 64 ,&nbsp; Redundant Sim Controllers: OCR400 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.&nbsp;Configure SimControllers and define drops.cfg&nbsp;file</p><p>2. Open SimControl GUI.</p><p>3.&nbsp;Give Freeze, Save, Run, Load command and observe the response messages in&nbsp;GUI.&nbsp;</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 94064
35017 | FINDING | Saved snapshot will not load if backup sim controllers assumes control in Redundant Sim Controllers | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:55 | [11 empty] | Bush, Kirt T EMR SYSS PWS PITT | 2016-03-30 09:55 | [7 empty] | Lal, Ramesh External | 2015-11-19 15:58 |  | In Redundant&nbsp;Sim Controller&nbsp; the snapshot saved when Primary Sim Controller is in control will not Load when Backup Sim Controller assumes control. |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Operator Station: Win7, 64 bits. Redundant Sim Controllers: OCR400</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. In Redundant Sim Controller set up&nbsp;&nbsp;put Primary Sim Controller is in control</p><p>2. Save a snapshot</p><p>3. Put Backup Sim Controller in control</p><p>4. Try to load the snapshot saved in step 2.</p><p>The snapshot will not be loaded.</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 94066
35023 | FINDING | Remote I/O node point may support for redundancy status of Ovation remote I/O node. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 14:44 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 14:44 |  |  |  | 2016-03-30 14:44 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-20 03:06 |  | <p>If we configure hardware nodes such as a Remote I/O nodes, the node record points&nbsp;is used to monitor the health of that particular node.&nbsp;But when a remote node failover occurs, user/operator&nbsp;cannot monitor it because </p><p>i) No bit is available in node point to show the status of redundancy of Remote I/O node. i.e. which RNC in control or backup.</p><p>ii) Alarm is not generated&nbsp;for redundancy lost of remote I/O node. i.e. any one of redundant RNC module&nbsp; is bad.</p><p>So&nbsp;User/operator may not know about&nbsp;redundancy status of remote I/O node&nbsp;and failover of Remote I/O node. </p> |  |  |  | It may not be feasible to update the &quot;classic&quot; remote nodes. &nbsp;Ethernet based remote nodes will have this feature. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | Durbin, Michael EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | Ovation 3.6.0_U1 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>More information required.&nbsp; Is this in reference to the Ethernet-based Remote Nodes or to the classic remote nodes which exist in Ovation releases prior to Ovation 3.6.0?</p><p>Note that the engineering tools CURRENTLY defines the upper 5 RN point bits for the Ethernet-based Remote Node&nbsp;as follows:</p><p>bit 11:&nbsp; IM INCTRL (indicates this RNC is in control of the I/O Bus)</p><p>bit 12: PART INCTL (indicates that the redundant RNC is in control of the I/O Bus).</p><p>bit 13 RED FAILURE (indicates the RNC has failed when control request was issued - Alarm on 1)</p><p>bit 14: unused</p><p>bit 15: I/O communications problem - Alarm on 1.</p><p>&nbsp;</p><p>LB 11/23/15-this is reference to the classic remote nodes which exist in Ovation releases prior to Ovation 3.6.0.</p><p>&nbsp;</p><p>Following are my test and observation</p><p>1)System details-Drop27/77,Controller used is OCR1100, Drop27 is configured as primary drop,Drop77 is configured as secondary drop,</p><p>drop27 is in control and drop77 is in backup mode-</p><p>Value of node point is 2885H and system is in healthy state.</p><p>Bit11-1<br>Bit12-0<br>Bit13-1<br>Bit15-0</p><p>After disconnecting the backup Remote I/O node(Removing the R3 Cable).Status of bit remains same also alarm is not generated. So how operator knows that backup Remote I/O node got failed?</p><p>After disconnecting both the Remote I/O node backup(Removing the R3 Cable) as well as control(Removing the R3 Cable).Status of bit remains same and sensor alarm is generated.</p><p>Screenshot showing the status of node point &nbsp;is also attached for your reference.</p><p><br></p><p>Please note that the above descriptions of bits 11 through 15 are applicable for the new Ethernet-based Remote Nodes, not for the classic remote nodes as this Finding has now indicated.&nbsp; This Finding is truly an Enhancement request and will be treated as such -- especially since changes would be required across multiple areas of Ovation software (e.g., controller, engineering tools, perhaps firmware?).</p><p><br></p><p>Transferring to controller group, where the bulk of the tasks would be performed (if this enhancement were to be pursued).<br></p> | 7 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p><u>Following are the steps to reproduce-</u></p><p>1) Configure a redundant remote node and assign a node point to it.</p><p>2)Monitor the status of node point after failover of Remote node controller.</p><p>3)Status of node point remains same before and after Remote node controller failover also node point does not go in alarm after Remote node controller failover.</p><p><u></u>&nbsp;</p><p><u></u>&nbsp;</p> |  | U1 |  |  | FINDING | [6 empty] | 94104
35024 | FINDING | "Manage Database Users" option in Ovation Security Manager window is not showing list of users. | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 03:18 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 03:18 |  |  |  | 2016-04-13 03:18 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-20 03:30 |  | It has been observed that, no details regarding users are appearing in &quot;Manage Database Users&quot; option in the Ovation Security Manager window of Ov-3.6.0, Instead of users details, following message is appearing-<br>&quot;The type initializer for &quot;Ovation.Engineering.Data.PtDb.Connection.Strings&quot; threw an exception&quot;.<br>However, on clicking at Manage Database Users Option in Security Manager of Ov-3.5.1,Ov-3.5.2 details of users are displaying properly such as PTADMIN, PTAUDIT, PTXML etc.<br><br>Screenshot of Security Manager of Ovation-3.6.0 (Drop-100 DBS) is attached for reference. |  |  |  |  | 0 |  |  |  | <div class=message-content><div class=message-content>LB 04/13/16-Verified on Ovation3.6.0_U6 Ovation security manager and observed that &quot;Manage Database Users&quot; option in Ovation Security Manager window is&nbsp;displaying list of ovation and other users&nbsp;. Hence this finding is closed by validation.</div></div> | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-03/15/16- Verified on Ovation3.6.0_U4 and observed that an error &quot;A connection attempt failed because the connected party did not properly respond after a period of time&quot; appears on selecting manage database Users option.Hence this finding is&nbsp;failed by validation. Screenshot is also attached for both DBS and domain controller drop.<div><br></div><div>UT-03/22/16 - Problem has been fixed and should be ok in U5.</div> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Developer Studio at DBS Drop of Ovation-3.6.0</p><p>&nbsp;2. Open Ovation Security manager. </p><p>3. Click on Manage Database Users task.</p> |  | U1 |  |  | FINDING | [6 empty] | 94823
35025 | FINDING | OSR is reporting incorrect driver version of audio device. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2015-11-20 07:15 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2015-11-20 07:15 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-20 04:55 |  | OSR is reporting incorrect driver version of audio device. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U1 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Generate the OSR report.</p><p>2)Verify the version of driver installed&nbsp;on drop&nbsp;with the version printed on OSR report.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 88655
35041 | FINDING | Control Builder displays error messages during printing of control sheet | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-24 08:50 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-24 08:50 |  |  |  | 2015-11-24 08:50 |  |  |  | Lal, Ramesh External | 2015-11-20 14:45 |  | <p>Open a control sheet. From the File menu select Print. List of available printers window will pop up. Select a printer and click on cancel button. A number of error messages will pop up &quot;Unit not found in database&quot; &nbsp;although the&nbsp; sheet is properly saved and compiled.&nbsp;Though it doesn't affect the control sheet in any way it is a nuissance message and should be suppressed.</p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Operator Station, Wn 7, 64 bit. |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Lal, Ramesh External | Validation |  | Duplicate of &nbsp;34986 | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open a control sheet</p><p>2. From the File menu select Print</p><p>3. Select a printer from the list of available printers</p><p>4. Click on cancel button</p><p>Error messages will be displayed.</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 88834
35044 | FINDING | OSR is not reporting the installed OPH patches. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Costlow, Kim EMR SYSS PWS PITT | 2015-11-23 07:22 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2015-11-23 07:22 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-22 22:21 |  | OSR is not reporting the installed OPH patches. drop 250 is OPH drop which is configured as&nbsp;non ovation drop in OSR Utility. After that report is generated and observed that OPH patches are not reported by OSR. But in actual OPH patches&nbsp;were installed and&nbsp;present&nbsp;on drop250. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,WS08</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Add the drop on OSR utility in which OPH patches&nbsp;were installed.</p><p>2)Generate the OSR report and verify that OPH patches&nbsp;were reported&nbsp;on OSR&nbsp;report or not.</p> |  | U1 |  |  | FINDING | [6 empty] | 88753
35046 | FINDING | Editor Crashes when the object browser is empty and performing Order Algorithm Operation | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-30 22:20 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-30 22:20 | 65018 |  |  | 2015-12-30 22:20 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2015-11-22 22:44 |  | <p>The contents of object browser are not appearing. There is an empty object&nbsp;browser box on the control builder screen when we open a control sheet.</p><p>When we select algorithm ordering from the view menu of the control builder and then&nbsp;when we click on&nbsp;any &nbsp;algorithm on the sheet control builder crashes.</p><p>In order to view the contents of object browser and prevent control builder from crashing open a control sheet&nbsp; left click on somewhere outside the control builder and then left click on somewhere inside the control builder the contents of object browser will appear.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open a control sheet from developer studio.</p><p>2. Go to the view menu in the upper right corner of the menu bar.</p><p>3. Select object browser from the drop down menu.</p><p>4. An empty object browser box appears.</p><p>5. Again go to the view menu and select Algorithm order from the drop down menu.</p><p>6. Now go to any algorithm on the control sheet and left click, the control builder will crash</p><p>7. Now again open a control sheet left click on somewhere outside the control builder and then left click on somewhere inside the control builder. The contents of object browser will be visible and now control builder will not crash on algorithm ordering.</p><p>&nbsp;</p> |  | U1 |  |  | FINDING | [6 empty] | 90315
35047 | FINDING | OSR may report AMS device manager,OPC Core components Redistributable software under other ovation software catagory | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Staab, Randy AUTOSOL PWS PITT | 2016-04-28 07:48 | [11 empty] | Staab, Randy AUTOSOL PWS PITT | 2016-04-28 07:48 |  |  |  | 2016-04-28 07:48 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-23 00:33 |  | <p>like APC toolkit, OPC,AHA software. OSR may report AMS device manager ,OPC Core components Redistributable software under other ovation software category. At present OSR is reporting these software under other installed software category.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | <p>2016-04-28 RStaab:</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p>To be listed under the &quot;Other Ovation Software&quot; category the mentioned software should identify itself as an OvationAddOn in their product's Uninstall registry entry.</p> <p>They would do this by&nbsp;creating a <strong>DWORD</strong> subkey named <strong>OvationAddOn</strong> with a value of <strong>1</strong> within their <strong>HKEY_LOCAL_MACHINE\Software\Microsoft\Windows\CurrentVersion\Uninstall\{YOUR_PRODUCT_GUID}</strong> entry.</p> <p>Developers can find further details here: <a href="http://pwsintra.emersonprocess.com/sites/crossroads/productdev/projects/Knowledge%20Base/System%20Registration%20Utility%20Checklist.aspx">http://pwsintra.emersonprocess.com/sites/crossroads/productdev/projects/Knowledge%20Base/System%20Registration%20Utility%20Checklist.aspx</a></p> <p>&nbsp;</p> <p><strong></strong>&nbsp;</p></blockquote> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1.Generate the OSR report.</p><p>2.Verify the details of AMS device manager ,OPC Core components Redistributable software inside the&nbsp;OSR report.</p> |  | U1 |  |  | FINDING | [6 empty] | 95878
35049 | FINDING | Configuration Option-> “Use Black color for printing chart titles and X-Axis” is not working in [Trend Options] dialog of Ovation Trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jain, Yukta AUTOSOL PWS NOIDA | 2015-12-28 23:41 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2015-12-28 23:41 | 64889 |  |  | 2015-12-28 23:41 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-23 02:52 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-size:12pt;"><font face=Calibri>A new feature of &quot;Print Colors&quot; tab with three configuration options are added to Ov 3.6.0 Trend option dialog to set the default background, Title and x-axis color while printing trend. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-size:12pt;"><font face=Calibri>Three options available are-<br> Option 1) Use White color for printing background<br> Option 2) Use Black color for printing chart titles and X-axis<br> Option 3) Use above options only for Black background setting</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><span style="line-height:115%;font-size:12pt;">Multiple combinations in different </span><font size=3>Test Environment</font><span style="line-height:115%;font-size:12pt;"> are verified for this feature. It is found that option 2 alone i.e. </span><font size=3>Use Black color for printing chart titles and X-Axis</font><span style="line-height:115%;font-size:12pt;"> is not working as expected. Details of combinations which are not working are listed below:</span></font></p><font face="Times New Roman" size=3> </font><table width=673 style="border:currentColor;width:504.9pt;border-collapse:collapse;" border=1 cellspacing=0 cellpadding=0><font face="Times New Roman" size=3> </font><tbody><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="padding:0in 5.4pt;border:1pt solid windowtext;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>Test Environment</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:1pt 1pt 1pt 0px;border-style:solid solid solid none;border-color:windowtext windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>Expected Result</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:1pt 1pt 1pt 0px;border-style:solid solid solid none;border-color:windowtext windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>Actual result</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=216 valign=top style="border-width:1pt 1pt 1pt 0px;border-style:solid solid solid none;border-color:windowtext windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:2.25in;background-color:transparent;"><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>Issue</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0in 5.4pt;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Trend Type- Live</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- White</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title Color- White or Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>X-Axis Color- Green</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- White</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title - Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- White</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title - Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis- Green</font></p><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=216 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:2.25in;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis color in printed trend should be black instead of green</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Reference- 1.xps </font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0in 5.4pt;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Trend Type- Live</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title Color- White or Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>X-Axis Color- Gray</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title - Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=138 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:103.5pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>BG Color- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Title - Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis- Gray</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font><td width=216 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0in 5.4pt;width:2.25in;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Axis color in printed trend should be black instead of gray</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Reference- 2.xps</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font></tbody></table><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-size:12pt;"><font face=Calibri><span style="">&nbsp;</span><span style="">&nbsp;</span><span style="">&nbsp;</span></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-size:12pt;"><font face=Calibri>Please find the attached XPS printing samples of above mentioned case. </font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software | IF condition was corrected in code. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>Machine type: Ovation-360 EWS</p><p>Ovation Application- Trend</p><p>OS- Win7 64bit&nbsp;</p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: please see my comments mentioned below:<p>1) The x-axis is green because the 3rd preference 'Use above Options only for Black background setting' is checked. Black background setting is under Format tab/Chart Options. If this 3rd preference is not checked then x-axis will always be black/gray on print.</p><p>YJ: as mentioned in description area, on selecting&nbsp;option 2 only&nbsp;i.e. “Use Black color for printing chart titles and X-Axis”. Expected result&nbsp;is Chart titles &amp; x-Axis color should be printed in black color for both black &amp; white back ground condition but in actual X-axis color is not printed in black. </p><p>For e.g as mentioned in 1st test environment, I set the x-axis color as green in trend window and select option 2 only to print&nbsp;x-axis in black color. Similarly in test environment 2, x-axis color is gray which should be printed in black when I select option 2 only. </p><p>&nbsp;</p><p>2)&nbsp;Trend app&nbsp;actually uses a gray color (that is close to black color), instead of totally black color, because the total black color appears very eye caching. It is just that it calls it black in user preference setting.</p><p>YJ: Trend application is printing axis in black color correctly for the&nbsp;case when option 2 is used along with&nbsp;other options (&quot;<font face=Calibri>Use White color for printing background&quot; or/and&nbsp;&quot;Use above options only for Black background setting&quot;</font>).&nbsp;</p><p>select option 1 &amp; 2 in print colors tab and you&nbsp;will get the x-axis color printed in black.&nbsp;It is observed that option 2 is not working well when only used.&nbsp;</p><p><br></p><p>yj (12/29/15): issue fixed in U2.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Open trend --&gt; Set trend settings as below --&gt; Go to Trend Option --&gt; Go to Print Colors tab --&gt; Select Option 2 only (Use Black color for printing chart titles and X-Axis) --&gt; Print the trend from Trend Menu -- Print option --&gt; Save print as XPS document --&gt; X-Axis is not printing in Black color.</p><p><font face="Times New Roman" size=3> <br></font></p><table width=673 style="border:currentColor;width:504.9pt;border-collapse:collapse;" border=1 cellspacing=0 cellpadding=0><font face="Times New Roman" size=3> </font><tbody><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="padding:0in 5.4pt;border:1pt solid windowtext;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p align=center style="margin:0in 0in 0pt;text-align:center;line-height:normal;"><font face=Calibri size=3>Trend Setting</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0in 5.4pt;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1 ) Trend Type- Live</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; BG Color- White&nbsp; </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; Title Color- White or Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; X-Axis Color- Green</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font><tr style=""><font face="Times New Roman" size=3> </font><td width=181 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0in 5.4pt;width:135.9pt;background-color:transparent;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2) Trend Type- Live</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; BG Color- Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; Title Color- White or Black</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp; X-Axis Color- Gray</font></p><font face="Times New Roman" size=3> </font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font></tbody></table><p><font face="Times New Roman" size=3> <br></font></p><p><br></p> |  | U1 |  |  | FINDING | [6 empty] | 90210
35050 | FINDING | OSR is reporting .NET Framework security updates under other installed software category. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2015-11-23 07:26 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2015-11-23 07:26 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-23 03:13 |  | <p>OSR is reporting .NET Framework security updates under other installed software category. while other security updates are reporting under Operating system Hotfixes</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Generate the OSR report </p><p>2)Verify the details of .NET Framework security updates.</p><p>OSR Report is also attached for your reference</p> |  | U1 |  |  | FINDING | [6 empty] | 88754
35051 | FINDING | [Trend type] button is missing from Quick access tool bar in Historical trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jain, Yukta AUTOSOL PWS NOIDA | 2015-12-28 23:27 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2015-12-28 23:27 | 3.6.0 U2, 65049 |  |  | 2015-12-28 23:27 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2015-11-23 03:30 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><br></p><font face=Calibri size=3><p style="margin:0in 0in 10pt;">Quick Access tool bar of historical trend GUI is missing &quot;Trend type&quot; button, however it is present in Live Trend window. . Trend Type button is quick way to switch over between live and historical trend. <font face="Times New Roman"> </font></p><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">It is also verified that Ov 352 &amp; Ov351 Historical Trend window have [trend type] button in Quick Access tool bar.</span></p></font><p style="margin:0in 0in 10pt;"><br></p><p style="margin:0in 0in 10pt;"><br></p><font face=Calibri size=3><p style="margin:0in 0in 10pt;"><br></p><p style="margin:0in 0in 10pt;"><br></p><p style="margin:0in 0in 10pt;"><br></p><p style="margin:0in 0in 10pt;"><br></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 10pt;"><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software | Corrected if condition. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Contento, James AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U2 |  | <font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Machine type: Ovation-360 EWS</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Ovation Application- Trend</font></span></p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">OS- Win7 64bit&nbsp;</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Kindly follow the steps mentioned under Steps to reproduce field. I also attached the snapshot showing comparison&nbsp;between Ov352 &amp; 360&nbsp;historical trend.&nbsp;&nbsp;<div>YJ (12/29/15): Issue verified on DBS and EWS and find fixed.</div> | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Open Trend </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri><font size=3> Live trend will be opened by default&nbsp;</font><span><font size=3>&nbsp;</font></span></font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri size=3> Click on Trend type button from Quick access tool bar of live trend </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri size=3> Select Historical Trend </font><span><span style="font-family:Wingdings;"><font size=3>à</font></span></span><font face=Calibri size=3> In Historical trend, Trend type button is missing from Quick access tool bar.</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Please see the attached snapshot.</font></p><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 90209
35057 | FINDING | crashing of control builder | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-24 08:48 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-24 08:48 |  |  |  | 2015-11-24 08:48 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2015-11-24 00:40 |  | when we select any algorithm from add algorithm box in the control builder and before placing the algorithm on the control sheet, we press ESC button from the keyboard the control builder crashes. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | Duplicate of 34979 - ESC cancels the add algorithm. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. open a control sheet from the developer studio.</p><p>2. Click the add control&nbsp;algorithm symbol in the tool bar of the control builder. Add algorithm box opens.</p><p>3. select any algorithm from the add algorithm box and press ok.</p><p>4. Now before placing the algorithm on the control sheet press ESC button from the keyboard.</p><p>5. The control builder will crash.</p><p>&nbsp;</p> |  | U1 |  |  | FINDING | [6 empty] | 88833
35058 | FINDING | OSR is not reporting SIM Controller details | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-01-12 15:44 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-01-12 15:44 |  |  |  | 2016-01-12 15:44 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-24 02:58 |  | <p>OSR is not reporting&nbsp;SIM Controller details. Drop27/77 is configured as SIM controller, Local as well as remote I/O is connected to drop27/77 but OSR is not reporting these I/O.&nbsp;Similarly software revision ,hardware revision, electronic index fields are also not reported. Previously this controller was configured as a normal controller at that time everything was reported fine. &nbsp;But when it is changed to Sim Controller these details are missing in OSR report.</p><p>kac-12/7/15 - Can you provide me screenshots of what Controller Diagnostic shows for the&nbsp;Sim controller?&nbsp; Both the OSR and Controller Diagnostic should report the same data.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>The only issue I see with the report is the Serial Number and EID should be N/A.&nbsp; What data do expect to be in the report?</p><p>LB-11/27/15-Like real controllers user can define I/O devices and add I/O modules on&nbsp; Sim controllers ,with the help of&nbsp;sim controllers user is able to do the simulation work .User can define I/O devices, modules on Studio for simulation work. Customer uses these controllers mainly for simulation and testing purpose.&nbsp;OSR is not reporting these details.</p><p><br></p><p>kac-1-12-16 According to the original developer the OSR should report the same information as the Controller Diagnostic. Therefore the OSR works the way it was designed. &nbsp;If you think the SIM controller IO details should be provided then a CAT 5 SDR should be created. &nbsp;It will require the controller to provide such details to the OSR which at this time it doesn't.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Generate the OSR report.</p><p>2)Verify the details of SIM Controller.</p><p>OSR Report is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 90981
35059 | FINDING | Editor Crashes when Perfoming Style Operations from the Object Browser Context Menu | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-02-23 21:13 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-02-23 21:13 | 65018 |  |  | 2016-02-23 21:13 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-24 03:19 |  | <p>OVation control builder stops working on following style operation</p><p><br></p><p>Open any control sheet , go to object browser then right click on styles , click on style then select export style sheet ,, a window will open to save the file name in 'css format&quot; .</p><p>Give the file name and click the save operation , suddenly a message pop up &quot;Edit ovation control builder document has stopped working'.</p><p>Attached the image for reference</p><p><br></p><p>For reference style operation after selecting the &quot;reference style sheet&quot; just click the cancel button then also the same error message &quot;Edit ovation control builder document has stopped working' </p><p>pop up in control builder window .</p><p><br></p><p>Cancelling the Import style operation also gives the same error message.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U2 |  | OV 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | Verified in U2 and now it is ok | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Open any control sheet . </p><p>Go to object browser</p><p>Right click on styles</p><p>click on styles</p><p>click import external style sheet</p><p>Instead of selecting any &quot;css&quot; file just cancel it </p><p>then error message popup in control builder.</p><p><br></p><p>click on export style operation </p><p>give any reference file name </p><p>click on save button </p><p>Same error message popup in control builder</p> |  | U1 |  |  | FINDING | [6 empty] | 92666
35060 | FINDING | OSR is not reporting Virtual Controller details | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-01-03 12:59 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-01-03 12:59 |  |  |  | 2016-01-03 12:59 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-24 04:10 |  | OSR is not reporting&nbsp;Virtual Controller details. Drop1 is configured as&nbsp;Virtual controller, Virtual Local as well as remote I/O is configured on &nbsp;drop1, but OSR is not reporting these I/O.&nbsp;Similarly software revision field are also not reported. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>The only issue I see with the report is the Serial Number and EID should be N/A.&nbsp; What data do expect to be in the report?</p><p>LB-11/27/15-Virtual controller is not a real hardware&nbsp;so Serial number and EID&nbsp;should be&nbsp;N/A. Like real controllers user can define I/O devices and add I/o modules on virtual controllers .with the help of virtual controllers user is able to do the simulation work .User can define I/O devices, modules on Studio for simulation work. OSR is not reporting these details.</p><p>kac-12/7/15 - Can you provide me screenshots of what Controller Diagnostic shows for the Virtual controller?&nbsp; Both the OSR and Controller Diagnostic should report the same data.</p><p>&nbsp;</p><p>LB-12/29/15-We cannot see the virtual controller details on controller diagnostic. we can define virtual controller details on studio, OSR&nbsp;may report the same. Consider an example of real controller suppose user has configured a real controller drop, some I/O are also connected on the same drop. Now generate the OSR report, OSR will report the controller drop details as well as I/O details. Now remove the controller drop and I/O physically not from the studio. Again generate the OSR report ,&nbsp;OSR will report the controller drop details as well as I/O details configured on developer studio .In the same way OSR may report the virtual controller details.</p><p><br></p><p>kac-1-3-16 According to the original developer the OSR should report the same information as the Controller Diagnostic. Therefore the OSR works the way it was designed. &nbsp;If you think the Virtual Controller IO details should be provided then a CAT 5 SDR should be created. &nbsp;It will require the controller to provide such details to the OSR which at this time it doesn't.</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Generate the OSR report.</p><p>2)Verify the details of&nbsp;Virtual Controller.</p><p>OSR Report is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 90364
35066 | FINDING | OV 3.6.0 Group policy :Control panel Policies prohibits accesss to control panel directly even when setting is disabled. | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Costlow, Kim EMR SYSS PWS PITT | 2016-04-26 14:31 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-04-26 14:31 |  |  |  | 2016-04-26 14:31 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2015-11-25 00:46 |  | <p>Unable to open control panel directly from Start Menu and Settings when logged in from Engineer and Operator user when the setting is disabled in Users and Computer group policies. </p><p>However , Control panel can be accessed by first accessing any Control Panel items like Program and Features and then navigating to Control Panel.</p><p>This scenario is specific to Windows 2012-R2 (64-bit).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0 - EWS</p><p>Windows 2012-R2 64 bit<br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | <p>Cannot reproduce the error as described above. After disabling the setting, the access to control panel from settings is working fine without any restrictions pop-up windows.</p> <p>&nbsp;</p> <p>TK 18-March-2016: Was able to reproduced the issue on drop121 in PGH lab</p> <p>Please find the remote login details :</p> <p>Drop121 (Windows Server 2012- R2 ):</p> <p>IP: 172.16.136.121<br>User : Val1dc8\TK-Engineer</p> <p>Password: Ovation1&nbsp;</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>On DBS:<br>1) Open Ovation Security Manager in Ovation Developer Studio.<br>2) Navigate to Manage Group Policies<br>3) Open properties of Engineer/Operator user .<br>4) Navigate to Control Panel &gt; Prohibit access to the control panel<br>5) Change value to disabled.<br>6) Click on apply and Ok.<br>7) Close Ovation Security Manager<br>8) Now run gpupdate command on command prompt.</p><p>On EWS:</p><p>On Windows 2012 R2 machine (Drop 149) login with Engineer/Operator User.<br>1) Access control panel from settings. <br>Observation: A pop-up window appears stating &quot;Restrictions: This operation has been cancelled due to restrictions in effect on this computer. Please contact your system administrator.&quot;</p><p>2) Type &quot;Programs and Features&quot; in search menu.<br>Observation: Program and features window opens&nbsp; up and you can navigate to Control Panel from this window.</p><p>On Windows 7 machine (Drop 171) login with Engineer/Operator User.<br>1) Access Control Panel from start menu.<br>Observation: Control Panel window opens.</p> |  | U1 |  |  | FINDING | [6 empty] | 95727
35067 | FINDING | OV 3.6.0 Group policy : Force Classic Start Menu setting when enabled or disabled does not have any effect. | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-03-18 10:54 | [11 empty] | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-03-18 10:54 |  |  |  | 2016-03-18 10:54 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2015-11-25 00:49 |  | User is able to switch between both the new style start menu and classic style menu even when &quot;Force Classic Start Menu&quot; is disabled. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0 - EWS</p><p>Windows 2012-R2 64 bit<br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | The Force classic Start Menu option is meant to configure whether the common icons like &quot;Documents&quot;, &quot;Pictures&quot;, &quot;Computer&quot;, &quot;Network&quot;, etc are placed as shortcuts in the DESKTOP or inside the START page.<div>If enabled, it shows these shortcuts in the DESKTOP; otherwise it shows only in the START page. That's the way it was on Windows Server 2008, Windows 7, and earlier releases.</div><div>Starting with windows server 2012, this setting has no effect because this feature has been removed by Microsoft.<br></div><div>By clicking on the windows button in Windows Server 2012, you are actually switching between DESKTOP &amp; TILE mode.</div><div>These modes are introduced in Windows Server 2012, which is totally different than the forcing classic start menu setting in earlier windows versions.<br></div> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>On DBS:<br>1) Open Ovation Security Manager in Ovation Developer Studio.<br>2) Navigate to Manage Group Policies<br>3) Open properties of Engineer/Operator user .<br>4) Navigate to Start Menu and Taskbar &gt;Force classic Start Manu<br>5) Change value to disabled.<br>6) Click on apply and Ok.<br>7) Close Ovation Security Manager<br>8) Now run gpupdate command on command prompt.</p><p>On EWS:</p><p>On Windows 2012 R2 machine (Drop 149) login with Engineer/Operator User.<br>Observation: Classic desktop window displays on login. User can switch between new style and classic style by pressing on windows button.</p> |  | U1 |  |  | FINDING | [6 empty] | 93573
35068 | FINDING | The user is able to set BTSC tuned value higher than the TPSC Tuned Value and than also able to enter a higher value for Set point than the defined TPSC tuned Value in Set point Algorithm. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-30 07:00 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2015-11-30 07:00 |  |  |  | 2015-11-30 07:00 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2015-11-25 03:26 |  | The user is able to set BTSC tuned value higher than the TPSC Tuned Value and&nbsp;after that user&nbsp;is able to enter a higher value for Set point than the defined TPSC tuned Value in Set point Algorithm. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p> <p>Net#36&nbsp;EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | It has always worked this way. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Insert a new Control Sheet, Create a logic having a Set Point Algorithm.<br>2. Save the Control Sheet and Load the Controller Drops.<br>3. Open the Signal Diagram for Control Sheet created in step1.<br>4. Select the Set point Algorithm and Go to Properties Summary.<br>5. Verify that the TPSC current value is 100 and BTSC current value is 0.<br>6. Now change the BTSC value from 0 to higher than the TPSC value. EX. Now BTSC value in 500.<br>7. Go to Algorithm Control and set the Set point value higher than the TPSC value, Ex. More than the 100 for Current scenario, now it is 300.</p> <p>8. Now user can see that the Set point value is 300, which is more than the TPSC value.</p> |  | U1 |  |  | FINDING | [6 empty] | 89037
35069 | FINDING | In Set point Algorithm, TPSC and BTSC value can be written till 38 digits, but the user can provide only 12 digits for set point in Algorithm Control | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-01-08 13:44 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-01-08 13:44 |  |  |  | 2016-01-08 13:44 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2015-11-25 03:33 |  | In Set point Algorithm, TPSC and BTSC value can be written till 38 digits, but the user can provide only 12 digits for set point in Algorithm Control |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p> <p>Net#36 EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | Works as designed.&nbsp; Value depicts significant digits for a floating point number. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Insert a new Control Sheet, Create a logic having a Set Point Algorithm.<br>2. Save the Control Sheet and Load the Controller Drops.<br>3. Open the Signal Diagram for Control Sheet created in step1.<br>4. Select the Set point Algorithm and Go to Properties Summary.<br>5. Verify that the TPSC current value is 100 and BTSC current value is 0. <br>6. Provide the 38 digit value to TPSC and BTSC and commit the changes.<br>7. Go to Algorithm Control and try to provide 38 digits to Set point but its accepting only 12 digits</p><p><br></p><p>Does exponent format work correctly?</p><p>RS 08/01/2015: Yes,&nbsp; exponent format is working fine.</p> |  | U1 |  |  | FINDING | [6 empty] | 90765
35070 | FINDING | The property sumary renders real algorithm record fields with exponential numbers incorrectly. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-01-08 13:43 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-01-08 13:43 |  |  |  | 2016-01-08 13:43 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2015-11-25 03:40 |  | Set point value is getting changed if BTSC value is changed to -ve and having more than 6 digits. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p> <p>Net#36 EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | Works as designed exponential format depicts actual significant digits. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1. Insert a new Control Sheet, Create a logic having a Set Point Algorithm.<br>2. Save the Control Sheet and Load the Controller Drops.<br>3. Open the Signal Diagram for Control Sheet created in step1.<br>4. Select the Set point Algorithm and Go to Properties Summary.<br>5. Verify that the TPSC current value is 100 and BTSC current value is 0. <br>6. Go to Algorithm Control and try to provide the Set point a value between TPSC and BTSC limit. For Ex setpint value is 56.<br>7. Go to Prosperties Summary and change the BTSC limit to -999999999 and commit the changes.<br>8. Set point value changed from previous value to some other value. Now value is 23.706. |  | U1 |  |  | FINDING | [6 empty] | 90764
35088 | FINDING | Alarm Viewer Window is crashing when Search string Tab is kept empty in Find Point . | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-12-21 20:50 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-12-21 20:50 | 64979 |  |  | 2015-12-21 20:50 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2015-11-25 21:44 |  | <p>Alarm Viewer Window is Crashing when -</p><p>Clicking on Find Point and Search string Tab is kept empty and click on Find Next. Refer Attachment (<strong>Alarm Window.JPG</strong> and the <strong>Event Viewer Log.Txt</strong>&nbsp;for the same).</p><p>While creating the same scenario in Ov 3.5.2, a popup comes with <strong>&quot;Enter Search String&quot;. </strong>Refer Attachment (<strong>3.5.2 alarm window.JPG</strong>).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U2 |  | &nbsp;Ws12 R2 &amp; W7 SP1(64 bit) 3.6.0 U1 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Go to ovation applications.</p><p>2. Click on Alarms.</p><p>3.&nbsp;Click on&nbsp;Find Point icon in Alarm Viewer window.</p><p>4. Keep the search string empty&nbsp;and click on Find Next.</p> |  | U1 |  |  | FINDING | [6 empty] | 90065
35090 | FINDING | GBNT:PtBrowser cannot search the points having description 50 characters. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 04:56 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 04:56 | 65014 |  |  | 2015-12-21 04:56 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-26 00:18 |  | <p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman"><font face="Segoe UI">As per the SRF1725 Functional Overview: </font></font></font><font size=3><font face="Times New Roman">The Ovation Software will be enhanced to support ED fields of 50 bytes, EU fields of 12 bytes, RS fields of 12 bytes, and ST fields of 12 bytes.<span style="">&nbsp; </span>This means the internal Ovation WESAPI will need to be enhanced to support the bigger ED, EU, RS, and ST fields, and also all of the Ovation programs that display and/or store the ED, EU, RS, and ST fields will need to be modified to be able to display/store the 50 byte ED field and the 12 byte EU, RS, and ST fields.</font></font></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman">Not only will the base Ovation Software need to be modified, but all Ovation add on products will need to support the larger ED, EU, RS, and ST fields.<span style="">&nbsp; </span>Most of these add on products will need to support running on older Ovation systems with 30 character ED fields and 6 character EU, RS, and ST fields, so new versions of these products will need to support Ovation Systems with both 30 and 50 byte ED fields and 6 and 12 byte EU, RS, and ST fields.</font></font></p><p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3></font></p><p><font face="Times New Roman" size=3>Since description field of GBNT:PtBrowser is accepting only 30 characters. So user cannot search the points having description 50 characters from GBNT:PtBrowser.</font></p> |  |  |  | Make sure user can enter 50 chars in ED entry field on pt filters tab of pt browser dialog | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | <p>size entry field to ED_LEN define in spd.h so that this app will not need to change next time we increase ED len. Also set ptname, alias, &nbsp;and characteristics entry fields on the pt filters tab to #defines in spd.h instead of allowing them to be hard-coded in the app...</p><p>LB-12/21/15: Verified in Ovation 3.6.0_U2 and observed that PtBrowser window,description field is accepting 50 characters. Hence this finding is closed by validation.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,WIN7</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | Allow 50 chrs in ED field on pt filters dialog/tab | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio&gt;go to graphics&gt;&nbsp;Create a diagram and open it.</p><p>2)Now Open the GBNT:PtBrowser window. Try to enter 50 characters on description field.</p> |  | U1 |  |  | FINDING | [6 empty] | 89991
35091 | FINDING | Graphics Viewer is displaying truncated character of a point description. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 05:05 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 05:05 | 6515766352 |  |  | 2016-03-15 05:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-26 00:55 |  | <p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman"><font face="Segoe UI">As per the SRF1725 Functional Overview: </font></font></font><font size=3><font face="Times New Roman">The Ovation Software will be enhanced to support ED fields of 50 bytes, EU fields of 12 bytes, RS fields of 12 bytes, and ST fields of 12 bytes.<span>&nbsp; </span>This means the internal Ovation WESAPI will need to be enhanced to support the bigger ED, EU, RS, and ST fields, and also all of the Ovation programs that display and/or store the ED, EU, RS, and ST fields will need to be modified to be able to display/store the 50 byte ED field and the 12 byte EU, RS, and ST fields.</font></font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>&nbsp;</font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman">Not only will the base Ovation Software need to be modified, but all Ovation add on products will need to support the larger ED, EU, RS, and ST fields.<span>&nbsp; </span>Most of these add on products will need to support running on older Ovation systems with 30 character ED fields and 6 character EU, RS, and ST fields, so new versions of these products will need to support Ovation Systems with both 30 and 50 byte ED fields and 6 and 12 byte EU, RS, and ST fields.</font></font></p><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3></font>&nbsp;</p><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>When I tried to monitor the description (50 character)&nbsp;of point ,only first 30 characters of description were displayed.</font></p> | Fixed a bug that caused only 1st 30 chars of a 50 c har ED field to display in QuickView and only 1st 6 chars of EU,RS, and ST fields to display. Garbage chars after that displayed in QuickView... |  |  | Test that all 50 chars of a 50-char ED field can be displayed at runtime using QuickView. Can test runtime graphics as well to be thorough, but problem was displaying the test graphic using QuickView... Also test that all 12 chars of a 12-char EU,RS, and ST fields display on a test graphic in QuickView and at runtime. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | <p>Call a new routine in GBNT (<font face=Consolas size=2><font face=Consolas size=2>SPD_get_recfld_datatype_and_size() ) to return size of ascii fields insteadof assuming size matched SHC data type define!</font></font></p><p><font face=Consolas size=2>AND</font></p><p><font face=Consolas size=2>in graphics, return the length of the&nbsp;input attribute field in SIM_SHC_get_ascii_field() via the input 'length' parram</font></p><p><font face=Consolas size=2>LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that exact 50 characters of ED,12 characters of EU,RS,ST are displaying on GBNT QuickView.Hence this finding is closed by validation.</font></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0u4 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,WIN7</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Fixed. Problem was in Quickview within GBNT (not in runtime graphics.exe).</p><p>LB-12/21/15: Verified on Ovation 3.6.0_U2 and observed the following things.</p><p>1)Extra characters are displaying, suppose a point has assigned 50 characters description it is displaying 52 characters on quick view.</p><p>2)characters are blinking sometimes showing + sign, sometimes showing full description.</p><p>Screenshot is also attached for your reference.</p><p><br></p><p>klj [02/25/16]. Also had to make a change to CSimSHC.cpp in graphics/quickview to fix this....</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio&gt;go to graphics&gt;&nbsp;Create a diagram and open it.</p><p>2)Select a process point&gt;go to properties&gt;Assign point name having 50 character description </p><p>3)Download the graphics and monitor the points ED field&nbsp;.</p> |  | U1 |  |  | FINDING | [6 empty] | 93348
35093 | FINDING | Some Test Cases of Test Record 3.6.0_CB_SVTP_rev_2.8_xx.doc needs corrections | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-15 01:36 | [11 empty] | USPITTFSService | 2016-04-15 01:36 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-26 03:07 |  | <p>Test Record 3.6.0_CB_SVTP_rev_2.8_CG.doc</p> <p>1. Section 5.1 Testcase5.1.1-i<br>&quot;Save As&quot; functionality should have additional description in the testcase as this functionality only creates a copy of existing Control Sheet in the same Control Task of same drop with same name and Sheet number. The description (Duplicate Control Function) should be added in the testcase since the same description is also available in Control Builder after user clicks Save As option in File menu.</p> <p>2. Section 5.6<br>Menu name is &quot;Tools&quot; in place of &quot;Toolbar Items&quot; as indicated in SVTP.</p> | <p>AA: 01/05/2016:&nbsp;Linda is working on the Control Builder manual for 3.6.0 release. Therefore, assigning this Finding to him.</p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/SVTP/STP | <p>AA: 01/05/2016:&nbsp;Linda is working on the Control Builder manual for 3.6.0 release. Therefore, assigning this Finding to him.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | SVTP/STP | In Validation | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>LA: 11/27/2015: Abhinav is working on the Control Builder manual for 3.6.0 release. Therefore, assigning this Finding to him.</p><p><br></p><p>AA: 01/05/2016:&nbsp;Linda is working on the Control Builder manual for 3.6.0 release. Therefore, assigning this Finding to him.</p><p>LC: 01/05/2016: Software Validation Test Plan (SVTP) findings and SDRs should be assigned to Nooch.</p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 95013
35094 | FINDING | The document tab remains open when the document is closed from the file menu option | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-02-22 05:23 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-02-22 05:23 | 65494 |  |  | 2016-02-22 05:23 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-26 03:16 |  | lf any Control Sheet (open in Control Builder) is closed from 'Close' option in File menu, the sheet is partially closed.<br>Following can be observed:<br>1. Main area showing the logic becomes blank, indicating that the sheet is closed.<br>2. Tab showing Control Sheet name (with path) is still open.<br>3. Property Editor menu for the item which was in selected condition before closing the sheet is still open.<br>4. Object Browser menu for the item which was in selected condition before closing the sheet is still open.<br>5. Control Builder crashes if we try to change the properties of item (as mentioned in point#3). |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0_U3 |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>As mentioned in Finding description</p> <p>Point# 1 and 2 are passing.</p> <p>Point3 3, 4 and 5 are failing. Issue mentioned in these points is still found.</p> <p><br></p> <p>Hence this finding&nbsp;has failed retest on Ov3.6.0_U2 build. (01/28/2016 Goyal, Ashish)</p> <p><br></p> <p>This should be corrected in U3.</p> <p>&nbsp;</p> <p>Verified that issue is fixed in Ov3.6.0_U3 build. Hence colsing the finding. (02/22/2016 Goyal, Ashish)</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 92530
35095 | FINDING | Print option has errors while printing Contol Sheets from Control Builder | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-31 00:41 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-31 00:41 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-26 03:19 |  | <p><u>Printing to USB Printer (HP LaserJet 1020):</u></p> <p>Print option from:<br>1. File menu --&gt; Print<br>2. File menu --&gt; Print Report <br>3. Tools --&gt; Operation --&gt; Print<br>outputs&nbsp;only blank sheets from physical printer. But if tried to print soft copies by selecting XPS document printer, files are generated successfully.</p> <p>(HP LaserJet 1020 is A4 page size printer).</p> <p>&nbsp;</p> <p><u>Printing to LAN Printer (HP Laserjet 5000):</u></p> <p>Scaling of document is not correct when printing on LAN printer.</p> <p>1. For A3 size page (11&quot;x17&quot;) printing, the print area extends on&nbsp;shorter edge of the page (11&quot; side) even if the print is given with 'Scale to fit page' option (under Resizing Options --&gt; Print Document On option).</p> <p>2. For A4 size page (8.5&quot;x11&quot;) printing, the print area extends on&nbsp;Longer edge of the page (11&quot; side) even if the print is given with 'Scale to fit page' option (under Resizing Options --&gt; Print Document On option).</p> <p>Hence only around 75% of the Control Sheet logic gets printed in both the cases</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software | <p>Can you re-test this with U2.&nbsp; When I test with the latest code, it seems to work&nbsp;(Cuts off a little)</p> <p>&nbsp;</p> <p>(Goyal, Ashish Apr 12, 2016)</p> <p>Verified in U4. Results are as follows:</p> <p>1. Able to print from USB printer (HP LaserJet 1020). No issues found in printing. Scaling is also perfect (complete control sheet gets printed with proper page margins).</p> <p>2. While printing from LAN Printer (HP Laserjet 5000), the issue mentioned in finding still persist. Improvement is that around 80-85% of the Control Sheet logic gets printed in both the cases.</p> <p>&nbsp;</p> <p>(Goyal, Ashish&nbsp;May 31, 2016)</p> <p>Tried with A4 network printer 'HP LaserJet P2055dn'. Prints cut off a little - around 1 to 2% on&nbsp;shorter i.e. 8&quot; side.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit)R |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 97988
35096 | FINDING | The algorithm anchor is not redrawn when Cycling the anchor thru available pins with the N or P key. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-01-27 23:17 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-01-27 23:17 | 65018 |  |  | 2016-01-27 23:17 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-26 03:22 |  | For a newly added algorithm, Algorithm Anchor does not cycle thru pins until the algorithm is placed in the control sheet.<br>As mentioned in SVTP (3.6.0_CB_SVTP_rev2.8_xxxx.doc, testcase 5.16.1-d), pressing the P or N keys will make the algorithm&nbsp; cycle thru the pins after which user has to click the area where the user wants to place the algorithm. But algorithm anchor is not visible until algorithm is placed in the control sheet.<br>Additionally, once algorithm is placed in the control sheet and algorithm anchor is visible, on pressing P or N key the algorithm anchor is not available and it becomes available only after deselecting and reselecting the algorithm. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U2 |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>Tested and found that issue is fixed&nbsp;on Ov3.6.0_U2 build. (01/28/2016 Goyal, Ashish)</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 91696
35097 | FINDING | Point Characterstic field accepting SINGLE numeric and SINGLE special character . | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-02-24 06:21 | [11 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-02-24 06:21 |  |  |  | 2016-02-24 06:21 |  |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | 2015-11-27 00:43 |  | <p>The point Characteristic field has following rules:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>1.&nbsp; The first character of Characteristic field must be &quot; &quot; , &quot;-&quot;, or A through Z.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>2. Characteristic field must consist of alphanumeric, ' ' ,'-' characters.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;Unlike the rule-1 if we enter single digit (0 through9) or a single special character say '%', the point is accepting the same and loading the point successfully.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Consequently if the point in alarm, the point will not appear in alarm window as the AY filed is invalid.&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Please note that entry only SINGLE digit or % creating a problem. If more that one character starting with first character as digit or '%' followed by other characters are entered , the point is accepting the value as per the rule 1 &amp; 2.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> |  |  |  | The affected area is restricted to the software which performs the validation check of the point Characteristics field.&nbsp; No specific test recommendations other than what would be considered to be obvious. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.6.0_U2 |  | OV 3.6.0 , Developer studio- point window. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  | <p>The check on valid characters for the Characteristics field had (mistakenly) only occurred if the length of the string is GREATER than 1.&nbsp; This will be corrected such that the validation of this field occurs regardless of the length of the string.</p><p>PJ 02/24: Checked and found in U3 build&nbsp;that the characteristic field is accepting the special &amp; alphanumeric characters as per the rule defined. Passed.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open an existing point or create a new point to open the point configuration window in developer studio.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;2. Click on 'Point' tab and enter any SINGLE digit (0-9)&nbsp;or '%' and click on Apply tab .&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Observation - The point is accepting the single digit or SINGLE '%'.&nbsp; This is unlike the rule-1 defined.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp; 3. Repete step-2 by entering digit or % followed by other acceptable character (Alphanumeric or '-'or &lt;space&gt;).&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Observation - An alert message message appear as per rule -1- This is ok.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>So on step-2 also , we should get the Alert message.</p> |  | U1 |  |  | FINDING | [6 empty] | 92679
35098 | FINDING | the control builder crashes when a new simple graphic or Control macro is created with a document already open. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:12 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:12 | 65494 |  |  | 2016-02-02 02:12 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-27 02:40 |  | <p>Addition of a simple graphic or control macro is crashing the control builder.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB-12/22/15: Verified on Ovation 3.6.0_U2 and observed that the control builder crashes when a new simple graphic or Control macro is created with a document already closed.</p><p>Steps to reproduce-</p><p>1)Open the developer studio&gt;select a controller drop &gt;create a control sheet and open it or open the existing control sheet.</p><p>2)Now close the control sheet opened on step1. go to file menu select&gt; New &gt;simple graphic or control macro option will crash the control builder.</p><p><br></p><p>LB 02/02/16- Verified on Ovation3.6.0_U3 and observed that the control builder&nbsp;is not crashing,&nbsp;when&nbsp;user creates a&nbsp;new simple graphic or Control macro with a document already open or&nbsp;closed.Hence this finding is closed by validation.</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio&gt;select a controller drop &gt;create a control sheet and open it or open the existing control sheet.</p><p>2)Now close the control sheet opened on step1. go to file menu select&gt; New &gt;simple graphic or control macro option will crash the control builder.</p><p>but when&nbsp;user open a control sheet and add another sheet as a simple graphic or control macro&nbsp;&nbsp;will not crash the control builder.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 91807
35101 | FINDING | Controller OCR1100 got failed with “Ovation SIS CHARMS” Driver Type | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-03-01 03:01 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-03-01 03:01 | 65791 |  |  | 2016-03-01 03:01 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2015-11-29 21:36 |  | <font face="Times New Roman" size=3> </font><p style="margin-bottom:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Controller OCR1100 Downloaded with “Ovation SIS CHARMS” Driver followed by Clear and reboot. </font></span></p><p style="margin-bottom:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Controller got failed due to Data Link error. Parameters are set to default i.e “Fail Controller on Error” is set to “FALSE”. </font></span></p><p style="margin-bottom:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>For reference error log is attached.</font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <p>Reduced amount of memory allocated for DPU.TotalMemory so that SISCHARMS driver&nbsp;can be loaded.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [5 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>Retested with U2, not fixed.</p><p>Validation could proceed testing with&nbsp; work around: <span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Performed manual changes in CONFIG.DPU as following</span></p><p>DPU.TotalMemory: 45000000; <span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.ControlMemory: 21000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.sharedMemSize: 21000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT0.sheetsetsize: 4000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT1.sheetsetsize: 4000000.</span></p><p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">Retested in U3, found not fixed. Amount of memory&nbsp;size <font color="#000000">allocated for DPU is not reduced.</font></span></p><p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">Following are the default DPU.CONFIG file size with U3.</span></p><p><font face="Times New Roman" size=3> <span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.TotalMemory</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">:</span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">69206016; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU. ControlMemory</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">: </span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">33554432;</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"> DPU.sharedMemSize</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">: </span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">33554432;&nbsp; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT0.sheetsetsize</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">:</span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">6291456; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT1.sheetsetsize</span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">:</span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">6291456.</span></span></font></p><p><font face="Times New Roman" size=3><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Controller is running with work around of manual change in DPU.Config file. Changes are following.</span></span></font></p><p><font face="Times New Roman" size=3><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.TotalMemory: 45000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.ControlMemory: 21000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.sharedMemSize: 21000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT0.sheetsetsize: 4000000; </span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;">DPU.CT1.sheetsetsize: 4000000.</span></span></span></font></p><p><font face="Times New Roman" size=3><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><br></span></span></span></font></p><p><font face="Times New Roman" size=3><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><strong><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></strong></span></font></p><font face="Times New Roman" size=3><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><strong><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"></span></strong></span><p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><font color="#000000">VP-02/29/15-Again retested in U3 with default parameters of CONFIG.DPU. </font></span><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><font color="#000000">Issue reported in finding (Failure of controller) not seen.&nbsp;&nbsp;</font></span></p><p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><font color="#000000"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">through hyper terminal session,&nbsp;observed &nbsp;error log while rebooting the&nbsp;controller.</span></font></span></p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><font color="#000000"><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the Shared Memory Configuration (6144000) ***</span></p><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the TotalMemory Configuration (19456000) ***</span></p><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the sheetsetsize Configuration (1536000) ***</span><font face="Times New Roman" size=3><br></font></p><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the sheetsetsize Configuration (1536000) ***</span></p><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the sheetsetsize Configuration (1536000) ***</span></p><p><font face="Times New Roman" size=3></font><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the sheetsetsize Configuration (1536000) ***</span></p><p><font face="Times New Roman" size=3></font><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the sheetsetsize Configuration (1536000) ***</span></p><p><font face="Times New Roman" size=3></font><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">*** Overriding the ControlMemory Configuration (8704000) ***</span></p></font><p>VP-03/01/16- Issue reported in finding (SIS Controller failure)&nbsp;not seen in U3, with default parameters of CONFIG.DPU.</p><p>Hence, finding is closed.</p><p><br></p></span><p><br></p><p><br></p><span style="color:rgb(31, 73, 125);font-family:Consolas;font-size:10pt;"><p><br></p><p><br></p><font color="#000000"><p><br></p><p><font face="Times New Roman" size=3><br></font></p><p><span style="color:rgb(228, 108, 10);font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p></font><p></p><p></p></span><p><br></p></font><p></p> | 11 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-1: Added I/O Driver Type “</font><b style=""><font size=3>Ovation SIS CHARMS</font></b><font size=3>” under Controller </font><b style=""><font size=3>dropxx- Configuration</font></b><font size=3>. </font><span style=""><font size=3>&nbsp;</font></span><font size=3>Parameters are set to default:</font><span style=""><font size=3>&nbsp; </font></span><font size=3>i) Timeout (msec): </font><b style=""><font size=3>10000</font></b><font size=3> ii) Fail Controller on Error: </font><b style=""><font size=3>False</font></b></span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-2: Added IO Device for </font><b style=""><font size=3>Ovation SIS CHARMS </font></b><font size=3>under</font><b style=""><font size=3> </font></b><font size=3>Controller</font><b style=""><font size=3> dropxx- IO device.</font></b></span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-3: Downloaded the Controller</font></span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-4: Clear the Controller. Controller comes up in failed mode</font></span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-5: Reboot the Controller. </font><span style=""><font size=3>&nbsp;</font></span><font size=3>Controller again comes up in Failed mode. Controller Error : I/O : Data Link Error : 0x19 011 : 0x2 : 0xe0005 : 0x0. </font></span></p><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 92834
35102 | FINDING | Properties window of OL button / Poke is seen to be distorted | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-02-23 21:16 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-02-23 21:16 | 65097 |  |  | 2016-02-23 21:16 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2015-11-30 02:23 |  | Graphics are made with multiple OL button /Poke . Initially properties <br>window appeared to be OK.<br>&nbsp;After opening the four / five the property window, the property window &nbsp;seems to be get distorted. | Bug occurs on POKE, OLBUTTON, PLOT, XYPLOT, and BMPIMAGE dialogs when user repeatedly selects an option that adds/removes widgets on the dialog (i.e. when user selects the 'dynamic rotation' box on the BMPIMAGE dialog or the 'shape_plot' box on the XYPLOT dialog) that causes widget positions to move off the dialog so they are unusable. This can occur from doing multiple &quot;Properties&quot; functions on pokes/buttons/plots/xyplots/bmpimages as well. The bug can occur when the user checks/unchecks a box that causes widgets to be added/removed on the dialog, or when the Properties function causes the widgets to be added/removed to display the current attributes of a selected item. This is new to VS&nbsp;2013 (release 3.6.0). |  |  | Brings up each of these 5 dialog boxes. You do not have to enter any data on the dialogs or create any graphics. Just repeatedly click on the options that change widgets. Move the dialogs on the screen and again repeatedly switch between options that change widgets. Widgets positions on dialogs should no longer change (become distorted) when you do this. On the BMPIMAGE dialog, repeatedly check/uncheck the 'dynamic rotation' box; on the&nbsp;OLBUTTON dialog, switch between the trigger and poke functionality buttons. Also switch between the various poke types when the poke functionality is selected; on the POKE dialog, switch between the various poke types; on the PLOT dialog, switch between the shape_plot and none plot types; on the XYPLOT dialog, check/uncheck the shapeplot box. Remember to move the dialogs around on the screen and perform the tests over again. Dialog widget positions should not become corrupted any longer. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | Something changes with the way this worked in VS 2013. Had to re-implement the code that handles this (class in Area.cpp). |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U2 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>Fixed bug. Bug occurred on POKE, OLBUTTON, PLOT, XYPLOT, and BMPIMAGE dialogs when user selects an option that adds/removes widgets on the dialog (i.e. when user selects the 'dynamic rotation' box on the BMPIMAGE dialog or the 'shape_plot' box on the XYPLOT dialog).</p><p><br></p><p>Verified in U2 and now it is ok</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Created a graphics with multiple pokes.<br>2. Right click on the first poke property window seems ok(Please seethe attached image :-OL_BTN_PROPERTIES.jpeg &amp; POKE_PROPERTIES.jpeg)<br>3. Go to second poke and select the properties.<br>4. After selecting the property window of few Pokes it is observed that Property window seems to be get distorted. (Please seethe attached image :-OL_BTN_PROPERTIES_DISTORTED.jpeg &amp; POKE_PROPERTIES_DISTORTED.jpeg) |  | U1 |  |  | FINDING | [6 empty] | 92667
35103 | FINDING | OSR may report Wireless HART device and Wireless HART Gateways details | Costlow, Kim EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:35 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:35 |  |  |  | 2017-02-16 15:35 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-11-30 05:00 |  | <p>OSR may report Wireless HART device and Wireless HART Gateways details.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | IC 2/16/17&gt; Entered SDR #38705 to track this, closed finding. | 5 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1)Open the developer studio go to systems&gt;Networks and configure Wireless HART device and Wireless HART Gateways details.</p><p>2)Generate the OSR report and verify the Wireless HART device and Wireless HART Gateways details</p> |  | U1 |  |  | FINDING | [6 empty] | 108976
35104 | FINDING | Unable to Edit Lock Property in Style Editor. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:03 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:03 |  |  |  | 2016-03-21 08:03 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2015-11-30 05:14 |  | <p>There is not way to change from 'Locked' to 'Unlocked' under Common Properties in the Style Editor. There is no pull down option for this feature available.</p> <p>Same observation is also found in older versions of Ovation (for example Ov351, Ov352)</p><p><br></p><p>Property is blank and does not create a pull down editor for (TRUE/FALSE) selection.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Net#36 VCH drop154 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | Attribute is not used.&nbsp; No plans to fix. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U1 |  |  | FINDING | [6 empty] | 93687
35111 | FINDING | Dev Studio stopped updating the config.vch file on the DBS | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-01 09:42 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-01 09:42 |  |  |  | 2015-12-01 09:42 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-11-30 15:39 |  | In the validation lab, on the Tim network, drop132 was configured as a VCH. 20 VCs were configured (including 2 redundant pairs) by Ramesh.&nbsp; It was noticed that after downloading/rebooting the VCH, that one of the VCs was not starting up.&nbsp; After looking at the config.vch for this VCH drop, it was noticed that one of the VC drops was not in the file.&nbsp; Using Studio on the DBS, the configuration of the VCs was modified repeatedly in an attempt to update the DBS&nbsp;config.vch file.&nbsp; It would not update, though it had been updated previously (the timestamp was from 45 minutes earlier and 19 of the VCs had been added to the file). We attempted deleting VCs, restarting Studio and rebooting the DBS, but still could not get the config.vch file to update.&nbsp; Please see Matt or Ramesh for any further clarification or questions. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lal, Ramesh External | [9 empty] | Implementation |  |  | Ovation 3.6.0 U1 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>More information required:&nbsp; Was drop132 (the VCH) downloaded?&nbsp; The generation of the config.vch file occurs during the download operation of the Virtual Controller Host itself.&nbsp; It is not updated during modifications of the configurations in the Ovation Developer Studio.<br>MP 12/1/15 - After downloading the VCH, the file was updated.&nbsp; The original problem of a drop not being in the file is recreated by :<br>In a redundant VC, swap the index numbers of both VCs.&nbsp; One of the VCs (appears to always be the partner) will be in the file, the other will not.<br></p><p>MES 12/1/15 - Please note that the issue with swapping index numbers should not focus on the generated configuration file.&nbsp; Opening the VCH in the Ovation Developer Studio will show that the both halves of the redundant VC may not have been re-assigned in the VCH.&nbsp; For example, perform a Where Used operation on the VCH (choose 4th selection -- references made by drop132 (the VCH)).</p><p>Also note that it appears that the description of this finding does not accurately&nbsp;represent the issue.&nbsp; The config.vch file is being generated on the DBS -- the validator mistakenly assumed that the file was generated/updated concurrent with the edits made in Ovation Developer Studio.&nbsp; This finding now boils down to a problem when a redundant VC is modified such that the index numbers of the&nbsp;two halves are swapped.</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U1 |  |  | FINDING | [6 empty] | 89114
35114 | FINDING | Point information-> Current point description field is not displaying 50 characters. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 05:02 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 05:02 | 65047 |  |  | 2015-12-21 05:02 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-01 03:45 |  | Point information Current point description field is not displaying 50 characters. Only&nbsp;42 characters&nbsp;are displaying remaining are displaying by dot. In older version ovation 3.5.1 exact 30 characters are displaying.&nbsp;&nbsp;As per the SRF1725 point description field can use description upto 50 characters. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0.U2 |  | Ovation 3.6.0_U1 |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>The user can view the full ED on the Point Tab; however, I will expand the size of the description&nbsp;field on the current value bar.&nbsp;</p><p>LB-12/21/15: Verified in Ovation 3.6.0_U2 and observed that Point information Current point description field is&nbsp; displaying 50 characters. Hence this finding is closed by validation.</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1) Create a point and write 50 characters on description field.</p><p>2)Load the drop.</p><p>3)Open the point on point information and verify the Current point description field.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 89992
35115 | FINDING | User defined alarm could not be acknowledged from Point Info or Alarm application | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:38 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:38 |  |  |  | 2025-03-19 07:38 |  |  |  | Kant, Krishna EMR SYSS PWS NOIDA | 2015-12-01 05:35 |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">User defined alarm for&nbsp;an Long Analog (LA)&nbsp;point&nbsp;could not be acknowledged from Point Info or Alarm application.</font></span> |  | No Action Required |  | <p>I tried to reproduce this error with U2 release, and could not.&nbsp; The UDA alarms were able to be acknowledged from Point Info.</p> | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Thakre, Dushyant AUTOSOL PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Ovation 3.6.0 setup with U1. Test was performed for OCR1100G01&nbsp;Controller</font></span> |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | No Action Required | 0 |  |  | Kant, Krishna EMR SYSS PWS NOIDA | Software Quality |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li> <div class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><font color="#000000"><font face=Calibri>Create an analog (LA)&nbsp;point with Low alarm limit user as -10 and high alarm limit user as 100 without defining any other high or low limit (as in attachment UDA.png).</font></font></font></div></li> <li> <div class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><font color="#000000"><font face=Calibri>Force the value of point to be 100 or more than that. HI UDA alarm will be generated.</font></font></font></div></li> <li> <div class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><font color="#000000"><font face=Calibri>Try to acknowledge the alarm from Point information application. Point is not acknowledged. </font></font></font></div></li> <li> <div class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><font color="#000000"><font face=Calibri>Try to acknowledge the alarm from Alarm application. Point is not acknowledged. </font></font></font></div></li> <li> <div class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font color="#000000" size=3 face=Calibri>The same is true for LO UDA alarm when point value is forced to be less than -10. </font></div></li></ol> | EPM Product Development | U1 |  |  | FINDING | [6 empty] | 229016
35117 | FINDING | Swapping the index numbers of a redundant pair of VCs causes one of the VCs not to be assigned. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-19 10:24 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-19 10:24 |  |  |  | 2016-01-19 10:24 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-01 09:54 |  | After configuring a redundant pair of VCs, using Studio to swap the index numbers of these VCs will cause the primary VC not to be assigned to a VCH. <br> |  |  |  | The affected area is in the software which updates VCH object(s) when the user modifies the assignment of a VC to a VCH (and its index).&nbsp; Rigorous testing of VC assignments to VCH is required to ensure that no other errors have been introduced with this fix.&nbsp;&nbsp; Verification (that the software is operating properly) should be made by inspection of VCH Where Used information as well as refreshed open operations of the VCH and inspection of the attributes associated with the assigned VCs. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lal, Ramesh External | [9 empty] | Implementation | 3.6.0_U2 |  | Ovation 3.6.0 U1<br> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>The software which implicitly updates references in a VCH based on changes made to a VC (specifically the VCH Index) will be modified.&nbsp; Swapping index numbers on a redundant VC is handled as two separate updates to the VCH.&nbsp; The second update (e.g., the partner's reassignment to the other index) cleans up the location where it used to be -- which is now being occupied by the primary half.&nbsp; The software will be updated to handle this very special case.</p><p><br></p><p>MP 1/19/16 - Retested successfully in U2</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Configure a redundant pair of VCs and assign to a single host machine. Verify both VCs appear in the VCH properties in Studio by clicking 'open' on the VCH. Swap the index numbers of the redundant VCs and hit apply.&nbsp; Open the VCH properties again in Studio by clicking 'open' on the VCH.&nbsp; Only the partner VC will be assigned to this VCH.<br> |  | U1 |  |  | FINDING | [6 empty] | 91363
35118 | FINDING | Developer Studio dosn't show error for missing configurations for Virtual Controllers | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Swartz, Mark EMR SYSS PWS PITT | 2016-03-17 12:20 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-03-17 12:20 |  |  |  | 2016-03-17 12:20 |  |  |  | Lal, Ramesh External | 2015-12-01 14:57 |  | <p>While configuring&nbsp; Virtual Controllers it was observed that Developer studio will not report any error if: </p><p>1.&nbsp;Virtual Controller Host field and Virtual Controller Index fields are&nbsp;left blank &nbsp;2. Virtual Controller Host field is left blank but&nbsp;Virtual Controller Index fields is defined.</p><p>In both the cases if VC was configured correctly and was running earlier, it will be still possible to download, reboot,&nbsp;clear and&nbsp;load the VC.</p><p>Please refer attached snapshot for VC Drop142 and Redundant VC Drop153/Drop154</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Virtual Controller Host Drop (WS 2012)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Lal, Ramesh External | Validation |  | <p>Is this new functionality specific to Ovation 3.6.0?&nbsp; The type of validation checking (or consistency checks) that this represents has never been part of any previous versions of Ovation.</p><p>12/01/2015:&nbsp;I don't think this is a new functionality. But it was never reported in earlier releases. However, it will be great if possibility of its implementation is looked into.</p><p>MES - 12/2/2015: This type of check could only be performed as part of a new Consistency Check, because we do not force the user to define their Virtual Controller Hosts before defining their Virtual Controllers (which&nbsp;would be too restrictive during the engineering of the system).</p><p><br></p><p>There are no plans to implement a new Consistency Check to support this validation in the Ovation 3.6.0 release.</p><p>&nbsp;</p> | 7 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>Configure Virtual Controller without defining Virtual Controller Host field and Virtual Controller Index fields and /or&nbsp;&nbsp;without defining&nbsp;Virtual Controller Host field&nbsp;but&nbsp;defining Virtual Controller Index fields</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 93498
35124 | FINDING | WRTap driver is not getting installed on Windows 2012R2 for VCH configuration | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 14:40 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 14:40 |  |  |  | 2016-06-07 14:40 |  |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | 2015-12-03 00:42 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>In case try to install WRTap driver from the WRTap installer, error related to installation comes and WRTap driver is not getting installed on Windows 2012R2 for Ovation 3.6 VCH creation. Please find attached windows event logs as “wrtapInstaller exe failed event log.txt” and &quot;Report.wer&quot; for details as why WRTap installer is not able to be installed.</font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Ovation 3.6.0 setup with U1</span> |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | IC 6/7/16&gt; this was resolved during 3.6.0 validation. See F#34955. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Product Development | U1 |  |  | FINDING | [6 empty] | 98355
35125 | FINDING | In case, if primary OHI driver is down, link speed is shown as 1Gbps | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Burgoon, Frank AUTOSOL PWS PITT | 2016-03-17 10:02 | [11 empty] | Burgoon, Frank AUTOSOL PWS PITT | 2016-03-17 10:02 |  |  |  | 2016-03-17 10:02 |  |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | 2015-12-03 00:57 |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">In case, if primary OHI driver is down, link speed is shown as 1Gbps</span> <div><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><br></span></div> <div><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Where do you see this 1Gbps displayed?</span></div> <div><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"></span>&nbsp;</div> <div><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;"><font color="#000000">Open Network connections from path “Control Panel\All Control Panel Items\Network Connections”, then right click on OHI1 (primary network adapter on which OHI is installed)&nbsp;and select “status” option. There you can see Speed in “General“ tab.</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;"><font color="#000000">Attached is the Screen shot (Status_With_Path.png) with complete path when network cable of OHI1 (primary network adapter on which OHI is installed)&nbsp;is disconnected for reference.</font> </span></p></span></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | Zaremsky, Mark External MZCI |  |  |  |  | Implementation |  |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Ovation 3.6.0 setup with U1</span> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | The questionable information is provided by the underlying network card driver. Emerson has no control over this. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>a.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Set the link speed as 100Mbps full duplex for two network adapters on which OHI has to be configured.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>b.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Configure OHI for these two network adapters.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>c.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Link speed is shown as 100Mbps</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>d.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Disable Primary OHI network adapter or remove network cable and Link speed starts shown as 1Gbps.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>e.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Enable Primary OHI network adapter or reconnect network cable and Link speed starts shown as 100Mbps.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>f.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3 face=Calibri>This behavior is not observed for secondary OHI network adapter.</font></p> | EPM Product Development | U1 |  |  | FINDING | [6 empty] | 93484
35141 | FINDING | SIS I/O CHARMS cannot be configured as CHARMS Hardware type cannot be populated in studio base on CHARM class | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-01-07 12:46 | [11 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-01-07 12:46 | 65018 |  |  | 2016-01-07 12:46 |  |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | 2015-12-04 05:38 |  | <p>SIS I/O CHARMS cannot be configured as CHARMS Hardware type cannot be populated in studio base on CHARM class (refer CHARMS-1.jpg).</p><p>&lt;Insert new&gt; SIS I/O CHARMS under CSLS level,&nbsp;On clicking &lt;ok&gt; gives error(refer CHARMS-2.jpg</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U1,Drop100,Server 2012 R2 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | SK: Tested in U2 and found to be Ok hence closed. | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1) Navigate to CSLS level under CHARMS controller.</p><p>2)&lt;Insert new&gt; SIS I/O CHARMS under CSLS level.</p><p>3) On clicking &lt;ok&gt; gives error(refer CHARMS-2.jpg.</p> |  | U1 |  |  | FINDING | [6 empty] | 90691
35153 | FINDING | Point Review application is crashing when user try to find point keeping the search string of find point empty. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 05:05 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-21 05:05 | 64979 |  |  | 2015-12-21 05:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-08 02:59 |  | Ovation Point Review application is crashing when user try to find point keeping the search string of find point empty. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software | Point information Current point description field is not displaying 50 characters |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U2 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,Win7</p> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Same issue as Finding 35088</p><p>&nbsp;</p><p>LB-12/21/15: Verified in Ovation 3.6.0_U2 and observed that Ovation Point Review application is not crashing when user try to find point keeping the search string of find point empty.Hence this finding is closed by validation.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the point review application.</p><p>2)Search some points then&nbsp;go to find point option under home tab.</p><p>3)leave&nbsp;&nbsp;the search string of find point empty and press find next button.</p><p>Screenshot is also attached for your reference</p> |  | U1 |  |  | FINDING | [6 empty] | 89993
35154 | FINDING | Firmware files for Logic solver & Sis net repeaters are not available. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:01 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:01 | 66672 |  |  | 2016-03-16 00:01 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2015-12-08 04:59 |  | <font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Logic Solver firmware &quot; SLSFirmware.zip&quot; file and SIS Net Repeater firmware &quot;SNRFirmware.zip&quot; file are not available in &quot;C:\Ovation\SIS\Firmware&quot;. Logic Solvers and Sis net repeater's firmware can not be upgraded with 3.6.0_U1. </span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PP:03/16/2016-Veryfied in Ov3.6.0_U4 of following path &quot;C:\Ovation\SIS\Firmware&quot; &amp; found three Zip files name as : </span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">1. OvSisSDSFirmware.zip</span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">2. SLSFirmware.zip</span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">3. SNRFirmware.zip</span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Hutchison, Steven EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [5 empty] | Implementation | U4 or U5 |  | <font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ov3.6.0_U1 in DBS drop100 (OS: Windows Server 2012R2)&nbsp;</span></p><font face="Times New Roman" size=3></font> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | IC 2/16/16 Val+Dev Mtg&gt; Val should test with existing FW for now. <br>Dev plans to&nbsp;release new FW containing one fix in U4. | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">1.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Go to the path C:\Ovation\SIS\Firmware.</span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"></span><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">2.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;</span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Only &quot;OvSisSDSFirmware.zip&quot; file is available.</span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"></span><font face="Times New Roman" size=3> </font></p> |  | U1 |  |  | FINDING | [6 empty] | 93407
35159 | FINDING | Quick access “Add Folder (plus sign)” and “Up (up arrow)” options are not available in Favourite folder menu bar. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-02-10 05:11 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-02-10 05:11 | 65491 |  |  | 2016-02-10 05:11 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2015-12-08 06:45 |  | <font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Quick access “Add Folder (plus sign)” and “Up (up arrow)” options are not available in Favorite folder menu bar however user can add the favorite folder from right click menu option.</span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PP: 02/10/2016-Verified in Ov3.6.0_U3 &amp; found the <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Quick access “Add Folder (plus sign)” and “Up (up arrow)” options are working fine.</span></span></p><p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Hence the finding closed.</span></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U1 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpFirst style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">1.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Open control builder </span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">2.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Go to View option &amp; click on Favorites Folder option.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">3.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Then asking for Local &amp; Shared options.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">4.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Select Local option.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpLast style="margin:0cm 0cm 10pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">5.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">The “Add Folder (plus sign)” and “Up (up arrow)” options are not available.</span></p><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 92076
35169 | FINDING | Newly created points show bad quality | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2015-12-09 10:34 | [11 empty] | Lal, Ramesh External | 2015-12-09 10:34 |  |  |  | 2015-12-09 10:34 |  |  |  | Lal, Ramesh External | 2015-12-08 14:32 |  | <p>Created LA, LD DA,DD points in one of the Controllers. After drop load when these points are viewed in Point Info they show bad quality. This happens even when they are configured with initial values. It is when they are scan off, forced with some value and scan on again that they will show good quality.</p><p>&nbsp;</p><p>12/09/2015: Finding closed based on Dev's comment.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation Controllers (OCR400/OCR1100)</p> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Create LA,LD,DA,DD points in a controllers</p><p>2. Drop load the controller</p><p>3. View the points in Point Info</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 89533
35170 | FINDING | External Ovation Network driver is not working correctly | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2024-01-11 09:12 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2024-01-11 09:12 |  |  |  | 2024-01-11 09:12 |  |  |  | Lal, Ramesh External | 2015-12-08 15:03 |  | <p>Multi-networking &nbsp;is established between Ov 3.6.0 and 3.5.1 system. Local point D35-LA-01 in controller Drop35/85 on 3.6.0 is mapped with remote point D16-LA-A-1 of controller Drop16/66 on 3.5.1 through I/O access path <a href="mailto:D16-LA-A-1.UNIT0@SIS">D16-LA-A-1.UNIT0@SIS</a>. It is observed that point D35-LA-01 is in bad quality and its value is not changing&nbsp;as per the value&nbsp;of remote point&nbsp;&nbsp;D16-LA-A-1. </p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0, Controller OCR1100</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Establish&nbsp; multi-networking between 3.6.0 (local network)&nbsp;and 3.5.1 (remote network)</p><p>2.&nbsp; In controller (on local network) define External Ovation Network driver.</p><p>3. Map a point in the local network with a point in remote network using Hardware tab &gt; IO access path</p><p>4. Verify that value of the local point changes based on the value of remote point and its Quality is good.</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 212606
35176 | FINDING | ISB Registered modules are not display in ISB despatcher GUI and theses modules are connected to the Ov3.6.0 database. | Anselmo, Christine AUTOSOL PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Anselmo, Christine AUTOSOL PWS MNL | 2016-04-22 03:47 | [11 empty] | Anselmo, Christine AUTOSOL PWS MNL | 2016-04-22 03:47 | [7 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2015-12-09 03:11 |  | <span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">ISB Registered modules are not display in ISB GUI and gives an &quot;syntax error&quot;. These modules are connected to the Ov3.6.0 database .Please see the attached snapshot for your reference.</span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Anselmo, Christine AUTOSOL PWS MNL | [8 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;"><font face=Calibri size=3>Ovation 3.6.0_U1+ ISB 2.5.1</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;"><font face=Calibri size=3>OS: Ws-2008-R2 and Win7+64 Bit&nbsp;</font></span></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | [Workaround] If it is confirmed that the description in &quot;Steps to Reproduce&quot; field is consistent then user just needs to wait until all modules started before accessing the Registered Modules page again (see workaround.png) | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Is this how to reproduce the error ? </p><p>1. Put all modules to a stop</p><p>2. Then Start the Modules</p><p>3. While Transaction Kernel is running, access the Registered Modules page</p><p>4.&nbsp;Error is replicated as shown in attached syntax_error.png</p> |  | U1 |  |  | FINDING | [6 empty] | 95422
35179 | FINDING | Editor unable to resolve SDS in database. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:10 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:10 | 65864 |  |  | 2016-03-16 00:10 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2015-12-09 03:54 |  | <font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&quot;SIS Logic Solver not found in database&quot; error occurred while inserting &amp; opening new sheets in control builder of any control module in a 1508.</span></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Please find attached snap shot for reference.</span></p><font face="Times New Roman" size=3> </font><p class=MsoNormal style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;</span></p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3>PP:02/10/2016-As per e-mailed by Nooch , we have replaced the old files with new files into C:\Ovation\CtrlBldr\dbExtension in Ov3.6.0_U3.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3>After that launched the developer studio &amp; Opened the control sheet from SDS01-LS01-CM01 &amp; found the sheet get opened without any error.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3>Since this issue will be fixed in U4.</font></p><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3>So , we are waiting for Ov3.6.0_U4.</font></p><p style="margin:0cm 0cm 0pt;"><font face=Calibri size=3><br></font></p><font face=Calibri size=3><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PP:03/16/2016-Veryfied in Ov3.6.0_U4&nbsp;of (DBS &amp; EWS drops) and&nbsp;did not found&nbsp;Error&nbsp;&nbsp;<span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&quot;SIS Logic Solver not found in database&quot;&nbsp; while inserting &amp; opening new sheets in control builder of any control module in a 1508 (</span>SIS logic solver). </span></span></p><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Hence Finding is closed.</span></span></p></font><p style="margin:0cm 0cm 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Raciborski, Mikolaj AUTOSOL PSS WRSW | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <p class=MsoNormal style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ov3.6.0_U1 in DBS drop100 (OS: Windows Server 2012R2)&nbsp;</span></p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpFirst style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">1.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Go to SIS Controller drop-&gt;SDS01&gt; SLS01 in developer studio.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">2.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Tried to&nbsp;Insert new control sheet in Control Module 1.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">3.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Give sheet name &amp; sheet number of new control sheet .</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpMiddle style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">4.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Click on O.K. button.</span></p><font face="Times New Roman" size=3> </font><p class=MsoListParagraphCxSpLast style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">5.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">In <span style="">&nbsp;</span>error list of control builder, error <span style="">&nbsp;</span>&quot;SIS Logic Solver not found in database&quot; appeared.</span></p><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 93409
35183 | FINDING | AMS DM 13.0 can not be installed on WS12-R2 machine. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 14:19 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 14:19 |  |  |  | 2016-06-07 14:19 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2015-12-09 05:53 |  | <p>When AMS 13.0 DM was tried to&nbsp;install on&nbsp;WS12-R2 operating system, it gave&nbsp;compatible error.</p><p>However when it is tried to install using &quot;NOOSCHECK&quot; command than it does not gave compatible error but installation failed&nbsp;</p><p>with&nbsp;Microsoft dot net 3.5 SP1 error.&nbsp;&nbsp;&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Wood, Thomas T AUTOSOL PWS PITT | Phan, Quang EMR ENT TECH AUS | [7 empty] | Implementation |  |  | AMS 13.0 DM with WS12-R2 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>IC 6/7/16&gt;</p><p>Work-around from 2/24/16 MS email: </p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;line-height:18pt;"><b><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Steps to “Enable .NET Framework 3.5 by using the Add Roles and Features Wizard”</span></b></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;line-height:18pt;"><b><span style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Requirements</span></b></p><p><font face="Times New Roman" size=3> <br></font></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Windows&nbsp;Server 2012 R2 </span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Installation media</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Administrator user rights. The current user must be a member of the local Administrators group to add or remove Windows features.</span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;line-height:18pt;"><b><span style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Steps</span></b></p><p><font face="Times New Roman" size=3> <br></font></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:12pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">In Server Manager, click <b>Manage</b> and then select <b>Add Roles and Features</b> to start the Add Roles and Features Wizard.</span></p></li><li style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:12pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select installation type</b> screen, select <b>Role-based or feature-based installation</b>.</span></p></li><li style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:12pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Select the target server.</span></p></li><li style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:12pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select features</b> screen, check the box next to <b>.Net Framework 3.5 Features</b>.</span></p><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Confirm installation selections</b> screen, a warning will be displayed asking <b>Do you need to specify an alternate source path?</b>. <br>If the target computer does not have access to Windows Update, click the <b>Specify an alternate source path</b> link to specify the path to the <b>\sources\sxs</b> folder on the installation media and then click <b>OK</b>. <br>After you have specified the alternate source, or if the target computer has access to Windows Update, click the <b>X</b> next to the warning, and then click <b>Install.</b></span></p></li></ol><p><font face="Times New Roman" size=3> <br></font></p> | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1.&nbsp; Insert AMS 13.0 DM DVD in WS12-R2 machine.</p><p>2.&nbsp; Navigate the DVD drive &amp; click on AMSDeviceManager_Setup.exe</p><p>3. Click Next on &quot;Welcome to AMS Suite&quot; page</p><p>4.&nbsp; OS Compatible error appeared (please refer attached snapshot&nbsp;CompatibleError_jpg&nbsp;)</p><p>5.&nbsp;Opened the command prompt G :\AMSDeviceManager_Setup.exe\NOOSCHECK ( G is DVD drive)</p><p>6. 3. Click &quot;Next&quot; on &quot;Welcome to AMS Suite&quot; page</p><p>7. Click &quot;OK&quot; to AMS Suite : Intelligent Device Manager Setup page.</p><p>8. Accept the License agreement &amp; click Next.</p><p>9.&nbsp; Click &quot;Yes&quot; to continue</p><p>10 Select Server Plus station </p><p>11 Click Next on Choose Destination Location page</p><p>12. AMS installation continue but in few seconds in gave Microsoft.NET Framework V3.5 SP1 error</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; (please refer attached snapshot Microsoft.NET_Error.jpg&nbsp;)</p> |  | Build 228 |  |  | FINDING | [6 empty] | 98353
35194 | FINDING | Profibus module fails to communicate after performing Firmware Download | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 7 | Lal, Ramesh External | 2016-04-16 05:40 | [11 empty] | Lal, Ramesh External | 2016-04-16 05:40 | 66158 66839 |  |  | 2016-04-16 05:40 |  |  |  | Lal, Ramesh External | 2015-12-09 11:02 |  | <p>Profibus modules are configured in Controller Drop39/Drop89. Wago devices are connected and process points are updating. An attempt was made to perform Firmware Download through Controller Diagnostics. The download was successful. The module was re-seated. Now any further attempt to Download Firmware or reboot from Controller Diagnostics gives communication error. This renders the module unusable.</p><p>It may be noted that there may be similar problem&nbsp;with DeviceNet module as well. It was not attempted because it will corrupt the module.&nbsp;</p> |  |  |  | Reformat controller flash and retest Profibus, DeviceNet, &amp; Fieldbus. | 0 |  |  |  |  | 0 |  |  | <p>Fixed bus module kernel missing symbols.</p><p><br></p><p>Removed &quot;vxworks.sym and restart.scr&quot; from the prototypical module boot directory.&nbsp;&nbsp;Reformat Controller Flash &amp; Retest.</p><p><br></p><p>3/21/2016:RL - Retested in 3.6.0_U4 by clearing the flash (deleted flash contents). restart.scr &amp; vxWorks.sym files are still present asking for download. Please refer the attached snapshots.</p><p><br></p><p><br></p><p>3/21/2016:GS - Updated the files for OCR400. &nbsp;OCR1100 should already have been updated in changeset 66158 (3.6.0_U4).</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | Ovation 3.6.0, Controller:OCR1100, Profibus Module |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>2/10/16: Retested in 3.6.0_U3.&nbsp;When Firmware download is attempted,&nbsp;SUCCESS message is displayed for all the files. But after rebooting the module&nbsp;files restart.scr &amp; vxWorks.sym show that they still need&nbsp; download. A second Download will also give similar result. Thus, these two files never get downloaded. Please refer attached snapshot.</p><p>4/16/16: Retested in 3.6.0_U6 and found O.K. Finding closed.<br></p> | 15 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Configure Profibus module in Developer Studio and mount the module in I/O slot</p><p>2. Open Controller Diagnostics and navigate to the target module</p><p>3. Perform Firmware Download and reseat the module</p><p>4. Try to Reboot/firmware Download again from Controller Diagnostics</p><p>It will show communication error.</p> |  | 3.6.0_U3 |  |  | FINDING | [6 empty] | 95091
35196 | FINDING | Virtual controllers respond to simulator commands even if not configured for simulation | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-19 16:30 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-19 16:30 | 66955 |  |  | 2016-04-19 16:30 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-09 13:32 |  | <p>Virtual controllers are acting on simulator commands (including freeze) even if not in simulation mode. There is no Ovation simulator driver configured and bit 4 (zero based)&nbsp;of the FF field of the DU record is not set to indicate simulation mode.&nbsp; But they are still acting on simulator commands. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | Verified that commands are not going to VCs that are not configured with an Ovation simulator driver. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Raciborski, Mikolaj AUTOSOL PSS WRSW | [9 empty] | Implementation | U5 |  | Ovation 3.6.0 U1 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Send simulator commands to Virtual controllers not configured for simulation. |  | U1 |  |  | FINDING | [6 empty] | 95246
35197 | FINDING | Controller Diagnostics doesn't show Profibus/DeviceNet ports/devices which are configured | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Lal, Ramesh External | 2016-05-15 22:49 | [11 empty] | Lal, Ramesh External | 2016-05-15 22:49 | 67652 |  |  | 2016-05-15 22:49 |  |  |  | Lal, Ramesh External | 2015-12-09 14:38 |  | <p>Profibus Modules and Wago devices are configured in Controller Drop39/Drop89 and working fine. Controller Diagnostics shows the Profibus modules but it doesn't show ports (P01,P02) and devices configured underneath. Similar is the case with DeviceNet modules. Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software | <p>3/21/2016:RL - Retested in 3.6.0_U4 in GEC in Controller Drop24/Drop74 and did not observe this problem. Hence finding is closed.</p><p>3/23/2016:RL- On further investigation, it was found that Drop24/drop74&nbsp;are OCR400 controllers wherein the finding is&nbsp;fixed. But&nbsp;the problem still persists in OCR1100 controllers. Hence this finding&nbsp; is being reopened.&nbsp;</p><p>4/26/2016:SRS - The OCR1100's&nbsp;Ethernet driver for VxWorks 6.9 was not properly fragmenting&nbsp;large UDP packets (data payload over ~1472 bytes). The module devices response that diagnostic server transmits exceeds this size (currently ~3KB). Mark Zaremsky modified the Ethernet driver to address this issue.</p><p>5/16/16: RL - Retested in 3.6.0_U7 and found O.K. Hence, finding is closed.</p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | [9 empty] | Implementation | U7 |  | Ovation 3.6.0_U1, Controllers: OCR1100, Profibus, DeviceNet modules |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | The ports and devices&nbsp;are now properly displayed in the Controller Diagnostics&nbsp;I/O tab. | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure Profibus/DeviceNet modules in Developer Studio</p><p>2. Configure Wago devices in port&nbsp; P01/P02 using Sycon tool</p><p>3. Load the controllers</p><p>4. Verify if ports and devices are seen in the Controller Diagnostics</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 96857
35204 | FINDING | Point menu>signal diagram option may also available for drop points. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:05 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:05 |  |  |  | 2016-03-21 08:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-10 04:34 |  | Like LA,LD,LP points user may reach to signal diagram from&nbsp;point menu signal diagram option. Suppose user has created two points LA,LD and used these points on control sheets. After loading the controller user can open these points on&nbsp;point information &nbsp;window. User can also check the status of these points on signal diagram by using the point menu signal diagram option. Similar thing may also work for drop points,this will help the user for algorithms like&nbsp;Drop status because it&nbsp;uses drop points. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,Win07</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | DU Points are not widely (Almost NEVER)&nbsp;used in control, and do not conform to normal data point processing. | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1)Create a control sheet.</p><p>2)add drop status algorithm and a assign drop point.</p><p>3)load the control sheet.</p><p>4)open the drop point assigned on drop status algorithm in Point information window.</p><p>5)Right click on point information window and verify the signal diagram option on point menu.</p><p>Screenshot is also attached for your reference.</p> |  | U1 |  |  | FINDING | [6 empty] | 93688
35211 | FINDING | Q-Line Analog points going to bad quality | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:38 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:38 |  |  |  | 2025-03-19 07:38 |  |  |  | Wood, Thomas T AUTOSOL PWS PITT | 2015-12-10 12:06 |  | As the value of output points assigned to remote Q-Line cards&nbsp;change value&nbsp;the&nbsp;point periodically changes from good to bad quality.&nbsp; |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U1 |  |  | FINDING | [6 empty] | 229017
35213 | FINDING | Backup Virtual Controller goes off and on highway if Primary Virtual Controller is stopped | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2016-04-21 01:43 | [11 empty] | Lal, Ramesh External | 2016-04-21 01:43 | 66878 |  |  | 2016-04-21 01:43 |  |  |  | Lal, Ramesh External | 2015-12-10 14:18 |  | <p>In redundant Virtual Controller pair&nbsp;the Primary Virtual Controller is in control and Secondary Virtual Controller is in backup. If Primary VC is stopped using 'Ovation Virtual Controller Manager' GUI, the backup VC will assume control but it keeps on&nbsp;going off the highway and coming back again repeatedly.</p> |  |  |  |  | 0 |  |  |  | 4/21/16: Retested in 3.6.0_U6. If Primary VC is stopped using 'Ovation Virtual Controller Manager' GUI, the backup VC will assume control and will not go off /on ovation highway. Hence finding is closed. | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U5 |  | Ovation 3.6.0, Redundant Virtual Controller |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure Redundant Virtual Controllers.</p><p>2. Put Primary VC in control and Secondary VC in backup.</p><p>3. Open 'Ovation Virtual Controller Manager' GUI</p><p>4. Stop Primary VC</p><p>Secondary VC will go off the highway and come back again repeatedly</p> |  | 3.6.0_U1 |  |  | FINDING | [6 empty] | 95347
35214 | FINDING | External Ovation Networks points are not operational in virtual controllers | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-04 15:01 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-04 15:01 | 65754 |  |  | 2016-02-04 15:01 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-10 14:34 |  | A VC configured with External Ovation network is not reading values from the external point. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | <p>Merged files from dev to integration, but we are using the &quot;dev&quot; files either way.&nbsp; Merging to integration just in case something is somehow using these files:</p><p><a href="https://uspit-tfs-v.emrsn.org/tfs/Products/Embedded/_versionControl/changeset/65754">https://uspit-tfs-v.emrsn.org/tfs/Products/Embedded/_versionControl/changeset/65754</a></p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U3 |  | Ovation 3.6.0 U1 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Configure a VC with external Ovation network. Add point to read external point. see that value is not transferred to the local point. |  | U1 |  |  | FINDING | [6 empty] | 91925
35215 | FINDING | Simulated points using external network points for simulation point not working | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-04 15:00 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-04 15:00 | 65754 |  |  | 2016-02-04 15:00 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-10 14:37 |  | Use of external network points as simulation points are not transferring proper value to local point. Use of a local point as simulation point is operational.<br>Same is true for I/O immediate points (i.e. slc in algorithms)<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | <p>Merged files from dev to integration, but we are using the &quot;dev&quot; files either way.&nbsp; Merging to integration just in case something is somehow using these files:</p><p><a href="https://uspit-tfs-v.emrsn.org/tfs/Products/Embedded/_versionControl/changeset/65754">https://uspit-tfs-v.emrsn.org/tfs/Products/Embedded/_versionControl/changeset/65754</a></p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U3 |  | Ovation 3.6.0 U1 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Use and external Ovation point as a simulation point in a local hardware point. see that it does not transfer the proper value. |  | U1 |  |  | FINDING | [6 empty] | 91924
35219 | FINDING | Maximize and Close Button are disabled in OSR GUI Window | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-17 00:46 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-17 00:46 | 6763267634 |  |  | 2016-05-17 00:46 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2015-12-11 03:54 |  | <p>In the GUI of OSR, maximize and Close Button are disabled. </p> <p>Though there have been workaround for these by using the drag option of the opened window, one can maximize and by using 'Cancel' or 'Alt+F4' one can close the window.</p> <p>Please see the attached screenshot OSR_Maximize_Close_Button2.jpg</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | 2016-05-02 RStaab: I've re-enabled the close button but not the maximize button. The main window does not really handle being resized very well currently. Hiding the maximize button would also hide the minimize button which is undesirable. The hope is to update the entire GUI and resizing/maximizing will be taken into consideration then. |  | 35 | FINDING |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U7 |  | <p>Ovation 3.6.0_U1</p> <p>OS-Windows server 2012.</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the OSR Utility.</p> <p>2. Try to close or maximize the window.</p> |  | U1 |  |  | FINDING | [6 empty] | 97019
35221 | FINDING | The Add License feature is disabled in EWS which is configured as VCH | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Spillane, Donal AUTOSOL PWS PITT | 2015-12-11 08:19 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2015-12-11 08:19 |  |  |  | 2015-12-11 08:19 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2015-12-11 05:07 |  | <p>The Add License feature is disabled in EWS which is configured as VCH.</p><p><br></p><p>Network licenses can only be added on the license server which in the case of Ovation is the DataBase Server.</p><p>In this case it appears that the VCH is not a license server and therefore the Add License... option should be disabled.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | OV3.6.0; VCH ; W7 64bit; |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Step1&gt; Open Dev. Studio</p><p>Step2&gt; Navigate to the Ovation Licensing</p><p>Step3&gt; Open Licensing and click on Add License . This is disabled only on VCH drop.</p> |  | U1 |  |  | FINDING | [6 empty] | 89672
35222 | FINDING | Historical Review application is crashing when user try to find point keeping the search string of find point empty. | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-28 22:22 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-28 22:22 |  |  |  | 2015-12-28 22:22 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-11 05:15 |  | Historical Review application is crashing when user try to find point keeping the search string of find point empty. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Historical Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,Win7</p> |  | Ovation for Windows | Ovation | Operator Station/Historical Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>fixed. Retest in U2.</p><p>&nbsp;</p><p>LB-12/29/15: Verified on Ovation 3.6.0_U2 and observed that Ovation Historical Review application is not crashing when user try to find point keeping the search string of find point empty. Hence this finding is closed by validation.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the Historical Review.</p><p>2)Select the find point option.</p><p>3)leave&nbsp;&nbsp;the search string of find point empty and press find next button.</p><p>Screenshot is also attached for your reference</p> |  | U1 |  |  | FINDING | [6 empty] | 90203
35223 | FINDING | Ovation Developer Search operation UI is not forcing character to upper case. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-03-29 23:11 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-03-29 23:11 |  |  |  | 2016-03-29 23:11 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2015-12-11 05:32 |  | <p>The Ovation Developer Search operation UI is not forcing character to upper case, if the CAPS LOCK is off.</p><p>For more details, please refer to Enchancement request SDR# 20168.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>Windows 7-64 Bit + Ov3.6.0, Windows Server 2012 R2-64 Bit + Ov3.6.0, Windows Server 2008 R2-64 Bit+ Ov3.6.0</p><p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>Please provide appropriate screen shots, as it is unclear how the above steps are being performed.</p><p>This issue is already resolved now so finding closed.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Ovation Developer studio&nbsp; search UI.</p><p>2.Type any point which exists in the database by keeping the CAPS LOCK off.</p><p>3.You can see the characters are typed in lower case.</p><p><br></p> |  | U1 |  |  | FINDING | [6 empty] | 94010
35224 | FINDING | Historical review is truncating last character of EU field. | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-15 04:21 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-15 04:21 | 66331 |  |  | 2016-04-15 04:21 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2015-12-11 06:16 |  | <p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman"><font face="Segoe UI">As per the SRF1725 Functional Overview: </font></font></font><font size=3><font face="Times New Roman">The Ovation Software will be enhanced to support ED fields of 50 bytes, EU fields of 12 bytes, RS fields of 12 bytes, and ST fields of 12 bytes.<span>&nbsp; </span>This means the internal Ovation WESAPI will need to be enhanced to support the bigger ED, EU, RS, and ST fields, and also all of the Ovation programs that display and/or store the ED, EU, RS, and ST fields will need to be modified to be able to display/store the 50 byte ED field and the 12 byte EU, RS, and ST fields.</font></font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>&nbsp;</font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman">Not only will the base Ovation Software need to be modified, but all Ovation add on products will need to support the larger ED, EU, RS, and ST fields.<span>&nbsp; </span>Most of these add on products will need to support running on older Ovation systems with 30 character ED fields and 6 character EU, RS, and ST fields, so new versions of these products will need to support Ovation Systems with both 30 and 50 byte ED fields and 6 and 12 byte EU, RS, and ST fields.</font></font></p><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3></font>&nbsp;</p><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>When I tried to monitor the&nbsp;EU Field&nbsp;(12 character)&nbsp;of point ,only first&nbsp;11 characters were displayed on historical review.</font></p><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;">&nbsp;</p> |  |  |  |  | 0 |  |  |  | <p>LB-04/15/16-Verified on Ovation3.6.0_U6 and observed historical review is displaying 50 characters&nbsp;for ED field and 12 characters of EU,RS,ST field under point and alarm tab . Hence this finding is&nbsp;closed by validation.</p><p></p> | 0 |  | Ovation for Windows/Operator Station/Historical Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Contento, James AUTOSOL PWS PITT | [9 empty] | Implementation | U5 |  | <p>Ovation 3.6.0_U1</p><p>OS-WS12,WIN7</p> |  | Ovation for Windows | Ovation | Operator Station/Historical Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB-12/23/15:Verified on ovation 3.6.0_U2 and observed that Historical review is not truncating last character of EU field, exact 12 characters are displaying under Historical review point Tab.</p><p>But under Historical review&nbsp;alarm Tab only six characters of EU field are displaying last six characters got truncated.</p><p>Screenshot is also attached for your reference.</p><p>SM-2/24/2016. Tested in U3, it works except set/reset alarm review. Please retest everything in 3.6.0U4.&nbsp;</p><p>LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that last four characters of RS,ST field got truncated on historical review alarm tab. Hence this finding is&nbsp;failed by validation.</p><p>Screenshot is also attached for your reference.<br></p> | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Open the historical review and verify the EU field of point containing 12 characters.</p><p>Screenshot is also attached for your reference.</p> |  | U4 |  |  | FINDING | [6 empty] | 95024
35229 | FINDING | graphic buider crashes when macro having text string tagout parameter greater than 51 is added. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-30 22:19 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-30 22:19 | 65310 |  |  | 2015-12-30 22:19 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-13 22:25 |  | <p>when I try to add a macro having text string tagout parameter $Tn (with n&gt;51) to a graphic builder diagram the graphic builder crashes.</p><p>As per documentation graphic builder allows upto 50 text string tagout parameters($Tn) to be defined in a macro. But when I tried to&nbsp;define more than 51 text string tagout parameters in a macro,&nbsp;Graphic builder is allowing me to save the same with an error message saying that range of text string tagout parameter is between 0-50. When I call this macro in a graphic builder diagram graphic builder crashes.</p> | Fixed a bug that could cause GBNT to crash if a graphic contained $T pointers with indices &gt; 50 in a graphic. Only $t1-$T50 are supported in graphics, but GBNT was not checking to make sure user did not use $T60, $T99, $T100, etc. |  |  | Test the applicable commands listed in the Resolution section to verify that valid instances of $T pointers can be used and invalid instances cannot be added via the dialog or the source editor. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | Check that only $T1..$T50 are allowed where $T pointers are supported in a graphic. Left code that would flag an error for $T pointer usage in olbutton and olchoice labels (not applicable) commented out in case any existing graphics do this so users would not get new compile errors that weren't hurting anything... |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U2 |  | <p>Net#26&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>&nbsp;controller drop28/78 (OCR1100)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;EWS drop195 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <p>GBNT now checks that only valid $T pointers ($T1..$T50) are used in a graphic where applicable{TEXT/MULTITEXT/DECORATIVE_TEXT labels and conditional labels,</p><p>BUTTON labels and conditional labels and poke type 7/23 program arguments,METER add-on text/mulittext,MACRO text parameters to MACRO command, poke list arguments to RUN_PROGRAMS and FUNCTION_KEY commands).&nbsp; Checks are done from applicable dialogs (e.g. GBNT:Button dialog) and the compile routines. Should no longer be able to save a graphic containing an invalid $T pointer. The commands that do not support $T pointers but accept text strings are not required to perform this checking...</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. create a new macro and define a text string tagout parameter $Tn where n&gt;51.</p><p>2. create a new graphic builder diagram and open the GBNT Macro dialogue box.</p><p>3. browse the&nbsp; macro created in the 1st step having the text string&nbsp; tagout parameter using the browse tab in the GBNT macro dialogue box.</p><p>4.&nbsp; Select the macro created in the 1st step.</p><p>5. Graphic Builder will crash. </p> |  | U1 |  |  | FINDING | [6 empty] | 90314
35239 | FINDING | Flash used in Controller Diagnostics show free flash space rather than used | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Thakre, Dushyant AUTOSOL PWS NOIDA | 2016-02-24 00:37 | [11 empty] | Thakre, Dushyant AUTOSOL PWS NOIDA | 2016-02-24 00:37 | 65476 |  |  | 2016-02-24 00:37 |  |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | 2015-12-15 01:56 |  | <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">“Flash used” in Controller Diagnostics show free flash space rather than used. For e.g., after Controller clear and reboot operation, Controller diagnostics shows used Flash as 61 MBs where after Load of Controller, it reduces to 35 MBs.</span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"></span>&nbsp;</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">DT(24/02/2016):</span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">tested in U3 and checked Field is updated as Flash Free. </span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 35 | FINDING |  |  | FINDING | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | [5 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | Software Quality |  | Changed the label on Controller Diagnostics to indicate &quot;Flash Free&quot;. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri><b><u>Steps to reproduce:</u></b></font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="COLOR:black;"><span style=""><font size=3 face=Calibri>1.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Perform Clear and Reboot operation of Controller and wait for controller to come up, check Controller Diagnostics (Screenshot: &nbsp;Flash used before load.jpg) </font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="COLOR:black;"><span style=""><font size=3 face=Calibri>2.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri><font size=3>Load Controller and then check again Controller Diagnostics. ( Screenshot: &nbsp;Flash used After load.jpg)</font><font size=3><span style="COLOR:#1f497d;">.</span></font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="COLOR:black;"><span style=""><font size=3 face=Calibri>3.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3 face=Calibri>Check Controller Diagnostics and compare both the results.</font><span style="COLOR:#1f497d;"></span></p> | EPM Product Development | U1 |  |  | FINDING | [6 empty] | 92673
35240 | FINDING | CPU Load under Process Information Tab in Controller Diagnostics should have sorting option. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 14:31 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 14:31 |  |  |  | 2016-03-30 14:31 |  |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | 2015-12-15 02:00 |  | <font size=3 face=Calibri> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri>In Controller Diagnostics Process Information Tab shows Task Name, CPU Load and State. If sorting of CPU Load is possible then it will be easy for check task with incremental/decrementing CPU usages.</font></p></font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 35 | FINDING |  |  | FINDING | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | [5 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>Ovation 3.6.0 setup with U1. Test was performed for OCR1100 Controller G01.</font></p> |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | In Validation | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | Software Quality |  | Tasks are shown in order of priority. &nbsp; This is a reasonable idea, but is not going to included in the base 3.6.0 release due to time constraints. | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [6 empty] | EPM Product Development | U1 |  |  | FINDING | [6 empty] | 94099
35264 | FINDING | Correct time is not displayed for controller points in Alarm window. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-01-08 08:28 | [11 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-01-08 08:28 |  |  |  | 2016-01-08 08:28 |  |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | 2015-12-16 11:04 |  | <font face=Calibri size=3><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"> </span></font><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">On Ov3.6.0 network, Live Alarms of controller point were showing date/time as 1970.Although DU points were showing correct date/time.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">When we download DBS drop of respective network no files related to NTP is getting downloaded.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">On investigation it’s found that NTP server setting under W32 time is empty on DBS (refer attached snapshot from both 3.6.0 network).</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">In Ov3.6.0 networks, NTP server defined is Standard Time server and IP used is gateway IP of that network:</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For Net#26 :192.168.27.9 </span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For Net#36:192.168.37.9</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">At network level Controller networking setting is also present.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Downloaded the Controllers and checked the entry of NTP server &nbsp;is the same in:<br> /ata0/etc/config.ntp </span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Restarted Controller but still&nbsp;Date displayed in Alarm window is 1970.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U1, Drop100 (Server2012 R2),drop24/74(OCR1100 G02) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  | <p>msb - 12/29 - In Ov-3.6.0_U2 all Controllers in Pgh show current time upon reboot.</p> <p>&nbsp; Shailendra - Please recheck Controolers time in GEC.</p><p>SK: In Ov3.6.0_U2 alarms for controller point is correct, hence closed.</p> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">1)Open Alarm window</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2)Controller point shows date/time as 1970 although DU point shows correct time.</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3)Checked NTP server configuration under /ata0/etc/config.ntp&nbsp; of controller and it is same as configured in studio.</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">4)Restarted controller but still Alarm window shows 1970.</span></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><p><font face="Times New Roman" size=3> <br></font></p> |  | U1 |  |  | FINDING | [6 empty] | 90749
35267 | FINDING | Starting of Virtual Controllers with VCoordManger seems to be delayed relayed to VC index. | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-19 17:21 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-19 17:21 | 66958 |  |  | 2016-04-19 17:21 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2015-12-16 14:45 |  | Using the VcoordManager to start a virtual controller appears to delay the start of the VC relative to the index number. For example, starting VC index 1 is fairly immediate (3 seconds), but starting VC index 18&nbsp;takes nearly a minute.&nbsp; The VCoordmanager actually times out waiting for the VC start and it looks like it didn't work, though it eventually does change to the proper state in the manager.<br>See attached file.<br> |  |  |  |  | 0 |  |  |  | Verified higher indexed VCs were not delayed in startup. | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U5 |  | 3.6.0 U1 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | IC 1/13/16&gt; updated Planned Release = U3 as was in RR. RR should not be used/created for Findings since Findings are a release record themselves. | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use to Vcoordmanager to stop a VC with a high index number. After it is stopped, start the VC and notice the time necessary for it to start. |  | U1 |  |  | FINDING | [6 empty] | 95263
35273 | FINDING | Windows 2012 R2 server (DB Server + Domain Controller) crashed with error “attempted execute of noexecute memory”. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-22 16:09 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-22 16:09 |  |  |  | 2016-03-22 16:09 |  |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | 2015-12-17 22:32 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Windows 2012 R2 server was crashing with error “attempted execute of noexecute memory” and The memory dump shows that the problem is related to the ohi.sys driver.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>This server is configured with OHI and working as Domain Controller/ DB Server.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>&nbsp;</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>We have observed this crash about 5-6 times or more in a day.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><span style="COLOR:#1f497d;">&nbsp;</span></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><u>Hardware Machine details:</u></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Dell R730(Intel(R) Xeon(R) CPU E5-2620 v3 @2.40Ghz 2.40GHz), 16GB RAM</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>This is Ovation prescribed rack mounted server and is used for Ovation 3.6 U1 with Windows 2012R2. Drawing no on crossroads for this server is 5X00727.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><u>NIC cards<span style="COLOR:#1f497d;">:-</span></u> </font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Broadcom NetXtreme Gigabit Ethernet, &nbsp;</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Driver Version: 16.4.0.2 (for OHI configuration refer attached screenshot NIC details.jpg)</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Part no. FM487 (PRINTED WIRING ASSY, PLANAR (MOTHERBOARD), 12G, RNDC, BROADCOM CORPORATION, QP, 1G, COPPER)</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><b><span style="COLOR:#1f497d;">&nbsp;</span></b></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><b><span style="COLOR:#1f497d;">&nbsp;</span></b></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><b>Attachments:</b></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>servercrash.zip folder contains following files:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>1.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Screenshot of error “ServerCrash.jpg”</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>2.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Mini dump “121615-21781-01.dmp” in Kernel_fc_9c722e5c5347379d1e5e84fbd97f4e11ef538f_00000000_cab_17c990ed </font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>3.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Windows error report “Report.wer” in Kernel_fc_9c722e5c5347379d1e5e84fbd97f4e11ef538f_00000000_cab_17c990ed </font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>4.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>System data “WER-168921-0.sysdata.xml” in Kernel_fc_9c722e5c5347379d1e5e84fbd97f4e11ef538f_00000000_cab_17c990ed</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>5.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Meta data “WER90DE.tmp.WERInternalMetadata.xml” in Kernel_fc_9c722e5c5347379d1e5e84fbd97f4e11ef538f_00000000_cab_17c990ed</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3><span><span><font face=Calibri>6.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri>Windows Events “BugCheck.txt”, “Eventlog.txt” and “Kernel-power.txt”</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><b>Remote Login Details: </b></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>The test setup can be accessed from internet explorer/Google Chrome using below credentials.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><b><span style="COLOR:#1f497d;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></b>iDRAC IP:-10.132.153.71</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; UserID&nbsp; :-root</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Password:-Ovation30</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri></font>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri><strong>DT[18-02-2016]:</strong></font></p><font size=3 face=Calibri> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>Installed Ovation 3.6.0 U3 on server 2012R2 and tried with Enabling/Disabling network cards which are configured for OHI.</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>Following observations are seen: </font></span></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;LINE-HEIGHT:normal;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:black;"><span style="">1.<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:black;">While Disable/Enable secondary NIC, server crashed once.</span></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;LINE-HEIGHT:normal;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:black;"><span style="">2.<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:black;">While Disable/Enable primary NIC, disable worked but enable was not happening and for enabling needed to restart the server but on restarting the server, observed server crash during boot up. On again performing restart, server booted up normally. Same scenario was tried 3-4 times and same is observed all the times. Crash dump (.dmp) file for the crash is attached.</span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>Attachments</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Server2012_crash.zip</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>Remote Login Details:-</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:black;"><font face=Calibri>As mentioned above</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"></font>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 35 | FINDING |  |  | FINDING | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | [5 empty] | Implementation |  |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Ovation 3.6.0 setup with U1. Test was performed for OCR1100 Controller G01</span> |  | Ovation for Windows | Ovation | Operator Station/General | Software | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | Software Quality |  | IC 3/22/16 &gt; per Dev, <font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);">It is known &amp; expected&nbsp;that Disabling/Enabling the</span><span style="color:rgb(31, 73, 125);"> NICs from the context menu will cause drastic results. <br>Findings is closed as WIW (No Plans to Fix). </span></font></font><font face="Times New Roman" size=3> </font> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3> From Network Connections window, where all available Network Cards are visible, tried disable/enable of NIC from context menu.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Please refer to the screenshot ”Disabling_OHI.png” .</font></span></p><font face="Times New Roman" size=3> </font> | EPM Product Development | U3 |  |  | FINDING | [6 empty] | 93802
35275 | FINDING | In Ovation 3.6.0, SIS Diagnostics tool is not working | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-03-16 04:42 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-03-16 04:42 |  |  |  | 2016-03-16 04:42 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2015-12-18 02:40 |  | <p>In Ovation 3.6.0, SIS Diagnostics tool is not working.</p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [6 empty] | Implementation | U4 |  | <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Windows 7-64 Bit + Ov3.6.0, Windows Server 2012 R2-64 Bit + Ov3.6.0, Windows Server 2008 R2-64 Bit+ Ov3.6.0</span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p><strong>RS 03/17/2016:</strong> Verified SIS Diagnostics tool&nbsp;in Win2012 R2, Win2008 R2 and Win 7 64 Bit for Ovation 3.6.0 U4 and now it is working. </p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Windows START icon than go to All Programs\Ovation\Ovation Utilities.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on SIS Diagnostics </p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">SIS Diagnostics application gets crashed.</p></li></ol><font face="Times New Roman" size=3> </font> |  | U1 |  |  | FINDING | [6 empty] | 93418
35277 | FINDING | RSR_SVTP_rev1.1.doc test case 5.1.x.c should be clarified | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-03-23 15:20 | [11 empty] | USPITTFSService | 2016-03-23 15:20 | [7 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2015-12-18 08:59 |  | RSR_SVTP_rev1.1.doc test case 5.1.x.c (where x = 1, 2, 3, 4,5, 6&nbsp;) should be modified to be <br><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">If the&nbsp;Studio description does not match the text in the RSR user manual, notify the&nbsp;Tech Writer.</span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Add-Ons | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U1 |  |  | FINDING | [6 empty] | 93867
35291 | FINDING | OCR1100 Controller is going to “failed mode” during load operation as Compact flash is going out of space during load | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-05-26 23:07 | [11 empty] | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-05-26 23:07 | 65584 |  |  | 2016-05-26 23:07 |  |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | 2015-12-22 06:18 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>OCR1100 Controller is going to “failed mode” during load operation with following error messages:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : OPP Subsystem Error : OPP System Error - Notice : 0x10 : 0xfffffffe : 0x8000a7aa : 0x0</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : OPP couldn't get local memory for 0x8000a7aa</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : Subsystem Group 1 Error : Generic Fatal Error : 0x2 : 0x1 : 0x3 : 0x0</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>REDUND_PROC MSG : Switching to Failed mode</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Init_SHC : ERROR in &lt;adm_db.c:ADMDB_sync_static_data_always&gt;</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Init_SHC : TEXT: &quot;Unable to update static.dat file&quot;</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : Coordinator Subsystem Error : Coordinator Point Edit Error : 0x3 : 0x18 : 0x1 : 0x1</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : OPP Subsystem Error : OPP Point Edit Error : 0x11 : 0x0 : 0x6 : 0x0</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Controller Error : OPP lost communications with point edit during a load operation</font></font></i></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>&nbsp;</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>On further investigation it was found that Compact flash is going out of space during load operation.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>After download, reboot and clear operation (on formatted flash), approx. 28 MBs were free out of 119 MBs of usable space (Flash capacity is 128 MBs).</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>During load Controller is going into failed mode with 0 MB space available on Compact flash disk.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>It is suspected that following two files are consuming more space:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Dpuctl file in data folder is of 32MBs</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>static.dat.tmp file is of 17 MBs. </font></font></p><font color="#000000"><span style="FONT-FAMILY:Wingdings;COLOR:#1f497d;"><span><font size=3> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Wingdings;COLOR:black;"><span>Ø<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp; </span></span></span><span style="COLOR:black;"><font face=Calibri>DPUCTL was approx. 5 MB in Ovation 3.6 U1 while it is 32 MB in Ovation 3.6 U2.</font></span></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Wingdings;COLOR:black;"><span>Ø<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp; </span></span></span><span style="COLOR:black;"><font face=Calibri>We never observed static.dat.tmp in past (as it’s a new feature), we didn’t have this in Ovation 3.6 U1.</font></span></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"></font></span></span></font>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>&nbsp;</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>For reference attached is the screen shot of Space sniffer application ran on Compact flash data (Space_sniffer_flash_drop4_Simplex_OCR1100.JPG) when Controller was failed.</font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri></font>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><strong>DJ [18-02-2016]:</strong></font></font></p><font size=3 face=Calibri> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><span style="FONT-SIZE:12pt;COLOR:black;">Checked on Noida Validation setup and found following:</span><span style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;COLOR:black;"></span></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt 39pt;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>1.</font></span><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>Setup was updated with Ovation3.6.0 U3 build with OCR1100 G02 Controllers,</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt 39pt;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>2.</font></span><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>Controller drops are loaded with 2875 points (365 Control Sheets) with no errors or failures</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt 39pt;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>3.</font></span><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;"><font face=Calibri>36.03 MBytes (Out of 122 MBytes of usable memory) are free in case of primary Controller and 37.65 MBytes (Out of 123 MBytes of usable memory)</font></span><span style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;COLOR:black;"></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"></font><font size=3 face=Calibri>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"></font>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt;"><font face=Calibri><b><span style="FONT-SIZE:12pt;">DJ [23-02-2016]:</span></b><span style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"></span></font></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt;"><font face=Calibri><span style="FONT-SIZE:12pt;COLOR:black;">On 23-02-2016, checked on Noida Software Development setup (</span><span style="FONT-SIZE:12pt;COLOR:black;">updated with Ovation3.6.0 U3) </span><span style="FONT-SIZE:12pt;COLOR:black;">on OCR1100 G01 Controller configured with 32000 points and found issue is still coming</span><span style="FONT-SIZE:12pt;"> while on 18-02-2016, c</span><span style="FONT-SIZE:12pt;COLOR:black;">hecked on Noida Validation setup (</span><span style="FONT-SIZE:12pt;COLOR:black;">updated with Ovation3.6.0 U3) </span><span style="FONT-SIZE:12pt;COLOR:black;">on OCR1100 G02 Controller configured with 2875 points and found it was loading without any failure.</span></font></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt;"><span style="FONT-SIZE:12pt;"><font face=Calibri>Following steps were performed in case of <span style="COLOR:black;">Noida Software Development setup</span>:</font></span></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt 42pt;TEXT-INDENT:-0.25in;"><font face=Calibri><span style="FONT-SIZE:12pt;COLOR:black;">1.</span><span style="FONT-SIZE:7pt;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;">Setup was updated with Ovation3.6.0 U3 build with OCR1100 G01 Controllers,</span><span style="FONT-SIZE:12pt;"></span></font></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt 42pt;TEXT-INDENT:-0.25in;"><font face=Calibri><span style="FONT-SIZE:12pt;COLOR:black;">2.</span><span style="FONT-SIZE:7pt;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;">Controller drop is configured for 32000 points and created 31990 digital points,</span><span style="FONT-SIZE:12pt;"></span></font></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt 42pt;TEXT-INDENT:-0.25in;"><font face=Calibri><span style="FONT-SIZE:12pt;COLOR:black;">3.</span><span style="FONT-SIZE:7pt;COLOR:black;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="FONT-SIZE:12pt;COLOR:black;">On loading Controller again facing issue that </span><span style="FONT-SIZE:12pt;">Compact flash is going out of space during load operation and OCR1100 Controller is going into “failed mode”.</span></font></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt 42pt;TEXT-INDENT:-0.25in;"><span style="FONT-SIZE:12pt;"><font face=Calibri>4.<span style="">&nbsp;&nbsp;&nbsp; </span>Found in Controller Diagnostics application that flash free is zero.</font></span></p> <p class=MsoNormal style="MARGIN:0in 3pt 0pt;"><span style="FONT-SIZE:12pt;"><font face=Calibri>For reference attached is the screen shot of Space sniffer application ran on Compact flash data (Space_sniffer_flash_drop4_Simplex_OCR1100_32k_points_23feb2016.JPG) when Controller was failed.</font></span><span style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"></p> |  |  |  | <p>1. Start with a blank (1Gb) flash card.&nbsp; </p><p>2. Boot controller</p><p>3. Download controller.</p><p>4. Reboot controller.</p><p>5. Load controller with up to 32000 points.</p><p>6. Reboot controller.</p><p>7.&nbsp; Observer no failure related to compact flash running out of space.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | [5 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | <div>Ovation 3.6.0 ocr1100 controllers now require a 1Gb flash card.<br></div> <div>&nbsp;</div> <div>[DJ-27/5/2016]: Checked on Ovation 3.6.0 U9 build and found that issue is not coming now.<br></div> <div><br></div> | 13 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [6 empty] | EPM Product Development | U3 |  |  | FINDING | [6 empty] | 97884
35298 | FINDING | Event messages are not generated in signal diagram -> event viewer when keys are fired through ovation keyboard | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-02-05 08:06 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-02-05 08:06 |  |  |  | 2016-02-05 08:06 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-23 02:58 |  | when control sheet having keyboard algorithm is loaded in signal diagram viewer and ovation keyboard is used to control the keyboard algorithm event messages are not getting generated when keys on ovation keyboard(like&nbsp;auto,manual etc) &nbsp;are pressed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  | <p>Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>controller drop37/77 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <p>Where are you look for event messages?</p><p><br></p><p>The signal diagram event log show message local to the current signal diagram context.&nbsp; The graphic process the ovation keyboard events and will generate an operator event, which is visible in historical review.&nbsp; </p><p><br></p><p>The signal diagram does not support the ovation keyboard.</p><p><br></p><p>I was looking for event messages of Ovation keyboard in signal Diagram event log. Event messages of ovation keyboard&nbsp;are getting generated&nbsp;in historical review.</p><p><br></p><p>Can we document that &quot;Event messages of Ovation keyboard can only be seen as events in&nbsp; historical review only and not in signal diagram event log&quot;. If you agree I would like to route this finding to documentation. This would bring clarity in testing and verifying the event logs.&nbsp;</p><p><br></p><p>No action is necessary.&nbsp; It meets reasonable expectations.&nbsp; The expectation that this event log would contain all historical review information has not been expressed in the last 8 years of deployment.</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Create a control sheet with keyboard algorithm and load the sheet.</p><p>2. Create a graphic diagram with various keyboard algorithm output parameters. Then Download the drop.</p><p>3. Configure the ovation keyboard to the drop on EWS.</p><p>4. Open the control sheet having keyboard algorithm in signal diagram .</p><p>5. Open the online graphics for keyboard as created in step 2.</p><p>6. Now press various keys on ovation Keyboard. Event messages will not be generated. However, the event messages are seen if Keys are fired from signal diagram itself.<br></p><p>&nbsp;</p> |  | U2 |  |  | FINDING | [6 empty] | 91938
35299 | FINDING | Keyboard Algortihm, Key 7 and key 8 for membrane key board does not function as required. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Spillane, Donal AUTOSOL PWS PITT | 2016-01-08 07:07 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2016-01-08 07:07 |  |  |  | 2016-01-08 07:07 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2015-12-23 03:05 |  | When P7 key of ovation keyboard is pressed Pk7 output of keyboard algorithm should go high but instead Pk8 output of keyboard algorithm goes high. When&nbsp; P8 key of ovation keyboard is pressed no response is seen on keyboard algorithm as seen in signal diagram. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  | <p>Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>controller drop37/77 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <p>Please attach the source for the&nbsp;graphic created in step 2.</p><p>Can you please supply the source for the main diagram.</p><p><br></p><p>In the main diagram you have FUNC_KEY 7 assigned to Pk8.&nbsp;&nbsp; &nbsp;FUNC_KEY 7 ON 1 124 0 1 8&nbsp;&nbsp;&nbsp; this should read FUNC_KEY 7 ON 1 124 0 1 7&nbsp;&nbsp; and if you want Pk8 you need FUNC_KEY&nbsp;8 ON 1 124 0 1 8.<br></p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a control sheet with keyboard algorithm and load the sheet.</p><p>2. Create a graphic diagram with various keyboard algorithm output parameters.&nbsp; Download the EWS.</p><p>3. Configure the ovation keyboard on EWS .</p><p>4. Open the control sheet having keyboard algorithm in signal diagram .</p><p>5. Open the online graphics created in step 2.</p><p>6. Now press P7 key of ovation keyboard Pk8 output of keyboard algorithm goes high.</p><p>7.Now press P8 key of ovation keyboard no response is observed.<br></p><p>&nbsp;</p> |  | U2 |  |  | FINDING | [6 empty] | 90734
35313 | FINDING | On rebooting, OCR1100 Controller is booting up in “failed mode” due to “Could not sync with ssv_task” and “Invalid Redundancy State detected” errors | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-02-24 05:22 | [11 empty] | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-02-24 05:22 | 65394 |  |  | 2016-02-24 05:22 |  |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | 2015-12-28 22:48 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>After updating system to Ovation 3.6 U2 build, OCR1100 Controller is booting up in “failed mode”:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>IOIC Driver: isr info: dev idx: 0: unsolicited response:</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>IOIC Driver: main firmware ready.</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Init_SHC : Initializing SHC 0</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Init_SHC : Final SHC init status 0001</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Init_SHC : Starting SHC daemon - SHC_HWY</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Drop Started : OCR1100 G01</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>Copy to Backup : Error initializing watchdog interface</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>REDUND_PROC ERROR : Could not sync with ssv_task</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>REDUND_PROC ERROR : Invalid Redundancy State detected</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>REDUND_PROC MSG : Switching to Failed mode</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font size=3 face=Calibri>Update Backup : Update Backup Exiting</font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;">&nbsp;</p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;"><strong>DJ [24-02-2016]:</strong></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.75in;TEXT-INDENT:-0.25in;">Checked for the issue on&nbsp;Ovation3.6.0 U3,&nbsp;with OCR1100G01 and found that these messages are not observed now.</p> |  |  |  | <p>Controller should now boot up and not report this error(s).</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | Increased the Timeout for the SSV &amp; SHC synchronization (because it takes longer with increased point count of 64000)&nbsp; Also made it a non-fatal error so we can finish booting up properly.&nbsp; |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | [5 empty] | Implementation | 3.6.0_U3 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Ovation 3.6.0 setup with U2. Test was performed for OCR1100 Controller G01.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>Controller is configured with 6112 slow broadcast frequency points and 122 Control Sheets.</font></p> |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | Increased the time to wait for SSV sync. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Product Development | U2 |  |  | FINDING | [6 empty] | 92676
35316 | FINDING | hostinfo.1 file always has 24 bit mask for N2 and N3, even if 23 bit mask is defined in Controller Networking | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2016-02-08 22:54 | [11 empty] | USPITTFSService | 2016-02-08 22:54 | [7 empty] | Jindal, Deepak EMR SYSS PWS NOIDA | 2015-12-29 22:10 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>hostinfo.1 file always has 24 bit mask for N2 and N3, even if 23 bit mask is defined in Controller Networking and Controller is downloaded with changes.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>DB Server OHI NIC is also configured with 23 bit mask.</font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | [5 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>Ovation 3.6.0 setup with U2. Test was performed for OCR1100 Controller G01.</font></p> |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | <p>The attribute referenced in this finding (&quot;Controller Net Mask&quot; in the Controller Networking object) drives the value in the netmasks file, not the hostinfo.1 file.</p> <p>The network interface N2 is the standard Ovation network interface.&nbsp; </p> <p>This finding references N3.&nbsp; More information required: Does this OCR1100 have its Ovation Highway Connection attribute configured for Dual?&nbsp; If so, N3 is the Backup NIC Interface.</p> <p>So if this OCR1100 is configured for Dual connect, then the hostinfo.1 file is correct.&nbsp; </p> <p>By design, the subnet masks for the Ovation Network interfaces are hidden from the user,&nbsp;hard-coded as 255.255.255.0, and written to the hostinfo.1 file.&nbsp; </p> <p>As stated above, the modifications performed in Steps to Reproduce will result in modifications to the netmasks file(s) (e.g., netmasks.drop1 and netmasks.drop51).</p> <p>&nbsp;</p> <p><strong><u>DJ [11-01-2016]:</u></strong></p> <p>As per the attached document &quot;Ovation IP Address Guidelines.pdf&quot; whose first page&nbsp;says &quot;<span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">Emerson suggests each DCS LAN be allocated two consecutive class C address blocks (512 IP addresses) using the sub-net mask 255.255.254.0 (/23)&quot;.</span></p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=2 face="Segoe UI">If Controller is hard coded with 24 bit sub-net mask, then it seems we will never have Controller on 23 bit&nbsp;sub-net mask. It can cause problems while communicating with remote network devices.</font></span></p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=2 face="Segoe UI"><br></font></span></p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=2 face="Segoe UI">Please note that for the Ovation interface (e.g., N2), the controller does not reference the hostinfo.1 file.&nbsp; Instead it references the two files hostinfo and netmasks.&nbsp;&nbsp; As stated above, the attribute referenced as &quot;Controller Net Mask&quot; in the Controller Network object drives the value in the netmasks file.&nbsp; To verify whether or not the netmask is properly configured for the Ovation network interface, the hostinfo.1 should not be referenced.&nbsp; To be absolutely sure, configure the netmask in the Ovation Developer Studio, Download and Reboot the controller, then login to the controller and perform an ifconfig command on the controller itself.</font></span></p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=2 face="Segoe UI"></font></span>&nbsp;</p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><strong><u><font size=2 face="Segoe UI">DJ [09-02-2016]:</font></u></strong></span></p> <p><span style="FONT-SIZE:14pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=2 face="Segoe UI">As mentioned by Mark, Hostinfo.1 file doesn't refere to netmasks file, so we are assigning this finding to Controller group. Purpose of assigning is to have same subnet mask at all references in Controller.</font></span></p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Following steps were performed:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>1.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Open Controller networking under network configuration.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>2.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Add 23-bit mask (255.255.254.0) in “Controller Net Mask” option and apply the settings.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>3.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Download the Controller</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>4.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3 face=Calibri>Check hostinfo.1 file at location “C:\OvPtSvr\Ovation\NET4\UNIT0\DROP2-DROP52\Config”. It still shows 24-bit net mask (255.255.255.0) &nbsp;</font></p> | EPM Product Development | U2 |  |  | FINDING | [6 empty] | 92035
35317 | FINDING | Failure in adding default gateway is observed on Controller Console during Controller boot up | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Thakre, Dushyant AUTOSOL PWS NOIDA | 2016-05-26 23:11 | [11 empty] | Thakre, Dushyant AUTOSOL PWS NOIDA | 2016-05-26 23:11 | 65488 |  |  | 2016-05-26 23:11 |  |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | 2015-12-30 06:13 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Failure in adding default gateway is observed on Controller Console during Controller boot up.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>When Controller boots up, it gives error as below:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span style=""><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>192.168.9.9</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span style=""><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><i><font face=Calibri><font size=3>is an invalid gateway.</font></font></i></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.25in;TEXT-INDENT:-0.25in;"><span style="FONT-FAMILY:Symbol;"><span style=""><font size=3>·</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri><i>FAILURE - &quot;routec add default 192.168.9.9</i></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Due to this problem, we are not able to sync Controller with NTP server configured in other Ovation network, connected via multi-network switch.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>This problem is not coming in Ovation3.5.1.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3>Just for more information if we try running <b>routec “add default 192.168.9.9”</b></font><font size=3> command manually from console, it works ok and Controller is able to sync to NTP Server. </font></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | routine was only separating strings from tabs and spaces, not carriage returns or&nbsp;newlines. |  | 35 | FINDING |  |  | FINDING | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Kijanka, Pawel EMR SYSS RS WRSW | Zochowski, Piotr EMR SYSS RS WRSW | [5 empty] | Implementation | 3.6.0_U3 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>Ovation 3.6.0 setup with U2. Test was performed for OCR1100 Controller G01.</font></p> |  | Ovation for Windows | Ovation | Controller/General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Thakre, Dushyant AUTOSOL PWS NOIDA | Software Quality |  | <p>Fixed parsing of the &quot;etc\routes&quot; configuration file.</p> <p>&nbsp;</p> <p>DT(27/05/2016):</p> <p>Verified with U9 Build by Booting up controller and checked Bootup sequence,&nbsp;now default gatway information is&nbsp;available<span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;"><font color="#000000"> &quot;routec add default 192.168.11.9&quot;” message during Controller boot up which indicates issue is resolved.</font></span></p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Following steps were performed:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>1.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Open Controller networking under network configuration.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>2.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Add 23-bit mask (255.255.254.0) in “Controller Net Mask” option, define “Primary and Partner Default Router IP Address” and apply the settings.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>3.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Download the Controller.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><span style=""><span style=""><font size=3 face=Calibri>4.</font><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3 face=Calibri>Connect Controller Console and check boot-up messages (during reboot).</font></p> | EPM Product Development | U2 |  |  | FINDING | [6 empty] | 97885
35318 | FINDING | An OCR configured with MHM either fails upon boot or doesn't boot | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2016-02-03 14:23 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-02-03 14:23 | 65394 |  |  | 2016-02-03 14:23 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2015-12-30 09:16 |  | OCR1100 Controller 2/52 (Emily) is configured with MHM.&nbsp; One of the partners either boots up and becomes Failed or does not boot.&nbsp; In the case where the OCR does not boot, one or more hard reboots may be required for the OCR to boot up and enter Failed Mode).&nbsp; Drop Clears from Studio and CF clears have been performed multiple times with no change in behavior.<br><br>Error Log messages are attached.<br><br>Update:&nbsp; This is not MHM-specific.&nbsp; Other controllers are exhibiting this behavior.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | See Finding 35313 | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U2 |  |  | FINDING | [6 empty] | 91863
35321 | FINDING | Add note to DIR : System Viewer was not designed to support multiple networks | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:17 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:17 |  |  |  | 2016-06-08 08:17 |  |  |  | Capani, Innocenzo AUTOSOL PWS PITT | 2015-12-30 15:31 |  | SDR 34426 notes: System viewer does not show other networks.<br><br>Dev responded: <p>the System Viewer was not designed to support multiple networks.</p><p>This should be noted in the DIR (3.6.0 and older). </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U2 |  |  | FINDING | [6 empty] | 98392
35340 | FINDING | Ovation Control Builder application crashes when clicked on Advanced Edit option of few SIS Algorithms | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:36 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:36 | 66657 |  |  | 2016-04-13 23:36 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-04 23:31 |  | <p>Ovation Control Builder application crashes when clicked on Advanced Edit option of few&nbsp;SIS&nbsp;Algorithms like LSCEM, LSSEQ, LSSTD.</p> <p>Please find attached screenshot of the error when application crashes and the Events generated in the Event Viewer as <em>Event Viewer and CB Error Screenshots.zip</em>.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT |  |  |  |  | Implementation | U4 |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>IC 3/17/17 &gt; Priyanka: please retest with U4.</p> <p>PA 4/17/16 &gt; Retested with U4 and working fine. Now the Control Builder doesn't crash when clicked on Advanced Edit of the algorithms mentioned in the Finding.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the Ovation Control Builder (Drop --&gt; I/O Device 5 Ovation SIS CHARMs --&gt; LSN --&gt; SIS CHARM Logic Solvers --&gt; SIS Control Modules)</p> <p>2. Insert a new SIS Control Sheet.</p> <p>3. Insert any of the above mentioned SIS algorithms (LSCEM, LSSEQ or LSSTD) in the SIS Control Sheet created in step#2.</p> <p>4. Right Click on the Algorithm and click on Advanced Edit.</p> <p>5. Control Builder crashes as soon as we click on Advanced Edit.</p> |  | U2 |  |  | FINDING | [6 empty] | 94867
35342 | FINDING | Control builder>window>close all windows feature is not working properly. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:16 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:16 | 65494 |  |  | 2016-02-02 02:16 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-05 05:17 |  | Control builder, close all window feature is closing all the existing open sheets window but property editor and object browser window&nbsp;is holding the data of last control sheet. After using the refresh option data&nbsp;got eliminated from the&nbsp;property editor and object browser window. In ovation earlier releases like ovation3.5.1,3.5.0 close all window feature is closing all the&nbsp;existing open sheets window&nbsp;as well as no data is&nbsp;retained on&nbsp;property editor and object browser window which is true&nbsp;because all sheets got closed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB 02/02/16- Verified on Ovation3.6.0_U3 and observed that after closing all the sheets using close all window feature data is not retained on property editor and&nbsp; object browser&nbsp; window.&nbsp;Hence this finding is closed by validation.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the control sheets. and select any algorithm.</p><p>2)go to window menu option and select close all windows option.</p><p>3)Verify that all the existing open sheets window&nbsp;got closed and no data is retained on&nbsp;property editor and object browser window.</p><p>Screenshot is also attached for your reference.</p> |  | U2 |  |  | FINDING | [6 empty] | 91808
35360 | FINDING | Unable to download firmware to DEC module | Boehmer, Robert W AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-03 14:52 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-03 14:52 |  |  |  | 2016-02-03 14:52 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-05 16:18 |  | Unable to download the firmware to the DEC module.&nbsp; The directory Embedded\Controller\ocr1100\module\DEC does not exist on the DBS. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software | <p>The directory was being named &quot;dvr&quot;.&nbsp; This was because we wanted to name the .romfs file &quot;dvr.romfs&quot; so its mount point would be &quot;/dvr&quot;.&nbsp; Having a mount point of &quot;/dvr&quot; allowed the module's default configuration files to be located in the same path as they were located in the legacy TCSA product.&nbsp; The code has been modified so the default configuration files are located in &quot;/dec/etc&quot;.&nbsp; The romfs file is renamed to &quot;dec.romfs&quot; and the dbs directory will be named &quot;dec&quot; as expected.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U3 |  | Ovation 3.6.0 U2 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>The DEC directory was being handled incorrectly.&nbsp; This will be addressed in U3.</p><p><br></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Attempt to download firmware from controller diagnostics to a DEC module.&nbsp; Also view that the mentioned directory does not exist on the dbs. |  | U2 |  |  | FINDING | [6 empty] | 91867
35361 | FINDING | Description of TPSC and BTSC parameters in SIS Secure Write Confirmation Window for few SIS algorithms is not self explanatory | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-01-20 06:24 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-01-20 06:24 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-06 01:03 |  | <p>Description of TPSC and BTSC parameters in SIS Secure Write Confirmation Window for few SIS algorithms (LSMID, LSAVTR, LSALM)&nbsp;is not self explanatory.</p> <p>The description of both TPSC and BTSC comes as IN_SCALE which is not clear for the user if it is for TPSC or BTSC. While for the other parameters the description is as according to the manual.</p> <p>Please see the attached screenshots of Ovation SIS Secure Write Confirmation window and the attached screenshot of the description of TPSC and BTSC fields as from OW352_R1101 Reference manual in <em>Finding35361.zip</em></p><p>SHS 1/11/2016&gt; Same has &nbsp;been observed for SCDML parameter (Decimal place) in LSALM algorithm, instead of SCDML the description appears as IN_SCALE.</p> |  |  |  | <br><br> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <p>This is the feedback message from the CSLS.&nbsp; It has always worked this way.&nbsp; </p><p><br></p><p>I don't think it needs fixed.&nbsp; But I will leave that up to the responsible developer.</p><p><br></p><p>The algorithm parameter resolution names are ambiguous.<br>the template have following translation:<br>TPSC&nbsp; &quot;IN_SCALE:EU100&quot;<br>BTSC&nbsp; &quot;IN_SCALE:EU0 &quot;<br>i also expecting the same issue for as it have the same construction.<br>SCU&nbsp;&nbsp; &quot;IN_SCALE:UNITS&quot;<br>SCDML &quot;IN_SCALE:DECPT&quot;</p><p><br></p><p><br></p><p><br></p> |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"></span>&nbsp;</p> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open a Control Sheet having LSAVTR/LSMID/LSALM algorithm, in Signal Diagram.</p> <p>2. Right Click on the algorithm and click on Advanced Tuning.</p> <p>3. Try to commit a new value for TPSC or BTSC Tuning parameter and click on Commit.</p> <p>4. Ovation SIS Write confirmation window appears.</p> |  | U2 |  |  | FINDING | [6 empty] | 91402
35362 | FINDING | OvPtSvr.exe stops occasionally on Ov360 Database machine. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Jain, Yukta AUTOSOL PWS NOIDA | 2016-03-29 16:16 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2016-03-29 16:16 |  |  |  | 2016-03-29 16:16 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2016-01-06 03:29 |  | <p class=MsoNormal>It is observed 4 -5 times that OvPtSvr.exe stops occasionally on Ov360 database machine Drop100.&nbsp;</p><p class=MsoNormal>This is an anomaly situation where root cause could not be found. Please see the attached snapshots of event viewer and reliability monitor.</p><p class=MsoNormal><br></p><p class=MsoNormal>Drop100 is freshly loaded NET36 DBS machine.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p class=MsoNormal>Ovation Version: 3.6.0_U2</p> <p class=MsoNormal>Machine type: DBS only</p> <p class=MsoNormal>OS type: WS2012 R2</p> <p class=MsoNormal>Hardware: Power Edge R730</p> |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Please provide examples of user actions which cause this event to occur.&nbsp; Cross-referencing the time OvPtSvr.exe stops/crashes with Engineering Tools audit logs and Ovation Error Logs may be helpful.<div><br></div><div>YJ:&nbsp;<span style="line-height:18px;">Anomaly situation. under monitoring.</span></div><div><span style="line-height:18px;"><br></span></div><div><span style="line-height:18px;">YJ (03/29): Not able to recreate.&nbsp;</span>&nbsp;<span style="line-height:18px;">Anomaly situation.</span></div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U2 |  |  | FINDING | [6 empty] | 93993
35367 | FINDING | Find point name feature could not highlight the algorithm of selected point. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:45 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:45 | 66666 |  |  | 2016-03-15 00:45 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-07 04:43 |  | <p>Find point name feature is only&nbsp;highlighting the algorithm of&nbsp;&nbsp;first selected point however no other algorithms are highlighted&nbsp; by selecting the remaining points in &quot; Find point name feature window&quot;.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that find point name feature is highlighting the algorithm of selected point. Hence this finding is&nbsp;closed by validation. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Create a control sheet and make some logic using algorithm like PID,SETPOINT,MASTATION,LEAD LAG.</p><p>2)click on find point name feature, now a window will appear, do not put any thing on point name entry field, click on find button, this&nbsp; populates all the points of control sheet on a window.</p><p>3)Now click or select any point, this highlight the corresponding algorithm on the sheet. <br>4) Further click or select another point , corresponding&nbsp; algorithms are not seems to be highlighted on sheet. However every time&nbsp; user has to&nbsp; close the&nbsp;&nbsp; &quot; Find point name feature window&quot;&nbsp; in case further any algorithm to be highlighted by selecting the point.</p><p>Screenshot is also attached for your reference<br></p><p><br></p> |  | U2 |  |  | FINDING | [6 empty] | 93331
35368 | FINDING | All tuning values in Properties Summary Window of Advanced Tuning in Signal Diagram get reset to 0 for LSAVTR and LSDVTR Algorithm, after CSLS and Controller load operation. | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:02 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:02 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-07 05:49 |  | <p>All tuning values in Properties Summary Window of Advanced Tuning in Signal Diagram get reset to 0 for LSAVTR and LSDVTR Algorithm, after CSLS and Controller load operation. (Load operation performed after making some changes in the&nbsp;algorithm parameters&nbsp;to generate CRC changes)</p> <p>Please see the attached screenshots of Properties summary window and the Control Sheet used in <em>Finding35368.zip</em></p> <p>PA 01/19//2016: The same behaviour has been observed for other SIS Algorithms too for which Advanced Tuning option is there.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the Ovation Control Builder (Drop --&gt; I/O Device 5 Ovation SIS CHARMs --&gt; LSN --&gt; SIS CHARM Logic Solvers --&gt; SIS Control Modules)</p> <p>2. Insert a new SIS Control Sheet.</p> <p>3. Insert LSAVTR or LSDVTR Algorithm and make a simple logic with nonsecure parameters and output points.</p> <p>4. Load the CSLS and the Controller.</p> <p>5. Open the above created Control Sheet in Signal Diagram.</p> <p>6. Now make some changes in the Control Sheet&nbsp;through the Control Builder&nbsp;so as to create some CRC changes for the Control Module (We changed DTYPE and SOPT parameter).</p> <p>7.&nbsp;Again load the CSLS and the Controller.</p> <p>8. Now refresh the Signal Diagram where the same Control Sheet created in step#2 is already opened.</p> <p>9. Right click on the Algorithm (LSAVTR/LSDVTR)&nbsp;and click on Advanced Tuning.</p> <p>10. All the tuning parameters&nbsp;are reset to 0 in the Properties Summary window.</p> <p>11. Now the user has to close the Signal diagram and again open it to see the normal Properties Summary window of Advanced Tuning populated with correct values.</p> <p><em><u>Note:</u></em></p> <p><em>a.&nbsp;It was also observed that sometimes (6 out of 10 times), the same behaviour was there for other Control Sheets in different Control Module of same CSLS having an LSAVTR or LSDVTR algorithm, even when changes were made in just one Control Sheet.</em></p> <p><em>b. It happens only when Signal Diagram&nbsp;application remains&nbsp;open&nbsp;at the time of CSLS and the Controller load.</em></p> |  | U2 |  |  | FINDING | [6 empty] | 95736
35384 | FINDING | pack16 Algorithm is retaining its output value when few of the input bit locations are left non-connected. | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 | [7 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-01-07 21:31 |  | Pack16 Algorithm is observed to retain its output value when few of the input bits kept non-connected. When Bit locations on pack16 algorithm are left as spare (no input is connected) then output bit corresponding to that spare bit should be zero. But instead the output retains its previous value corresponding to that bit.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | <p>3.6.0_U2_Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>controller drop37/77 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a control sheet having Pack16 Algorithm. Assign input points to few of the inputs of algorithm.</p><p>2. load the sheet and open it in the signal diagram.</p><p>3. make all the input points high and observe the output of Pack16 Algorithm.</p><p>4. Now open the same sheet in the control builder; delete any or all of the input points assigned to the Pack16 algorithm and load the sheet.</p><p>5. Open the same sheet in signal diagram. The pack16 algorithm is observed to retain its previous output status. </p> |  | U2 |  |  | FINDING | [6 empty] | 118595
35390 | FINDING | Ovation License Manager window is crashing if wrong License code is entered. | Spillane, Donal AUTOSOL PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Spillane, Donal AUTOSOL PWS PITT | 2016-01-18 16:10 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2016-01-18 16:10 | 65733 | [6 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-01-08 03:04 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Drop:- Drop100(DBS)</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation:- Ov 3.6.0</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Os:- Win 2012 R2</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>It is observed that Ovation License manager window is crashing if the wrong Code is entered into the Ovation license manager window.</font></p><font face="Times New Roman" size=3> </font> |  |  |  | Retest as before. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U3 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | Fix to check for invalid license codes entered. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>1:- Open the License Manager Window at Drop100.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>2:- Go to Add License.. tab.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>3:- Enter License code. (e.g.:- 1234 absd) and press Enter.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>4:- Ovation License Manager Window is crashing.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><span style=""><font size=3>&nbsp;</font></span><font size=3>For more details please find the “Application Error.txt” and “DotNet runtime error.txt” </font><span style=""><font size=3>&nbsp;</font></span><font size=3>from the attachment.</font></font></p><font face="Times New Roman" size=3> </font> |  | 3.6.0_U2 |  |  | FINDING | [6 empty] | 91325
35391 | FINDING | All the output points of the algorithms present in a Control Module go to BAD quality for significant time after CSLS load followed by Controller load. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-03-01 04:50 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-03-01 04:50 |  |  |  | 2017-03-01 04:50 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-08 05:39 |  | <p>All the output points of the algorithms present in a Control Module go to BAD quality for significant time after CSLS load followed by Controller load. This happens when the load operation is performed after making some CRC changes in the Control Module. Algorithms of all the Control Modules whose CRC changes, have their output points first in POOR quality for&nbsp;59 sec&nbsp;while when Controller starts loading sheets, then point enter into BAD Quality for 23 sec.</p> <p>When the IO Driver timeout period was increased from default 10000 msec&nbsp;to 40000/60000/100000 msec, time period for which POOR and BAD quality was observed, decreased by just 5-10 msec.</p> <p>Controller Console logs show following messages during Controller load operation:</p> <p><em>FRI JAN 08 10:16:54 2016 : &lt;132&gt; SIS Alg : SID: 0x80008a50: Control Module revis<br>ion mismatch: CSLS 3, CM 10<br>FRI JAN 08 10:16:54 2016 : &lt;132&gt; SIS Alg : Throttling error messages</em><br></p> <p>Please find attached the following items:</p> <p>a. Controller printErrorBuffer logs.</p> <p>b. CSLS load script</p> <p>c. Generated SIFs</p> <p>d. Trend logs</p> <p>e. Ovation Error logs</p> <p><em><font face="Segoe UI Semibold">Note: We are using OCR1100Ctlr.Out file as given by Greg for resolution of Finding#35313 in our Controller Drop.</font></em></p> |  |  |  | Resolved in U9<br> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | [6 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Make some changes in a Control Sheet so as to create CRC changes in the Control Module. (We added one non-secure parameter in CM#2 and as there were Control Sheets in other Control Modules having Nonsecure parameters, CRC of all following Control Modules changed)</p> <p>2. Open the output point of the algorithms in Trend application.</p> <p>3. Load the CSLS and the Controller.</p> <p>4. Observe the point quality as POOR when CSLS load is in progress and point quality becoming BAD as soon as the Controller starts loading Control Sheets.</p> |  | U2 |  |  | FINDING | [6 empty] | 109487
35417 | FINDING | Control builder is crashing, if user selects the edit algorithm operation . | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-09 13:38 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-09 13:38 |  |  |  | 2016-03-09 13:38 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-11 06:14 |  | <p>** DUPLICATE OF 34800 **</p><p><br></p><p>Control builder is crashing,&nbsp;if user selects &nbsp;the edit algorithm operation on DBS drop. On EWS drop, some times the algorithm editor window opens and sometimes it crashes.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Is this a duplicate of 34800?</p><p>LB 01/27/16-Yes, it is a duplicate of 34800.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer Studio, Select a controller drop, Open a control sheet.</p><p>2)Go to edit menu option and select algorithms. After doing this Control builder crashes.</p><p>Screenshot is also attached for your reference.<br></p> |  | U2 |  |  | FINDING | [6 empty] | 93152
35426 | FINDING | SIS Events are not appearing in Historical Review application | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:56 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:56 |  |  |  | 2016-04-13 23:39 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-12 07:29 |  | <p>SIS Events are not appearing in Historical Review application.</p> <p><em>Note:</em></p> <p>a. We have verified from the OPH team and OPH is working fine from their end.</p> <p>b. The Controllers on which SIS Charms is configured are downloaded with new <em>OCR1100Ctlr.out</em> file which contains the changes for <strong>Finding#35313</strong>.</p> <p>c. OvSisEvents service is running on both scanner machines.</p> <p>d. Performed following steps to gather sisev logs:</p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;" dir=ltr><span><span>1.<span style="FONT:7pt 'Times New Roman';"><font size=2 face="Segoe UI">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span></span></span>Go to C:\Ovation\OvSisEventService.</p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;" dir=ltr><span><span>2.<span style="FONT:7pt 'Times New Roman';"><font size=2 face="Segoe UI">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span></span></span>Open OvSisEvents.Service.exe CONFIG File and uncomment the line inside “<i>system.diagnostics</i>” title which is responsible for generation of sisev.log file on Scanner machine.</p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;" dir=ltr><span><span>3.<span style="FONT:7pt 'Times New Roman';"><font size=2 face="Segoe UI">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span></span></span>Gather fresh SIS Events log by restarting OvSisEventsService.exe.</p> <p>e. Please find attached gathered sisev.log file.</p> <p>&nbsp;PA 1/13/2016&gt; After observing an error message &quot;Exception: Could not find file 'C:\Ovation\OvSisEventService\Messages.xml'&quot; in sisev.log file , we manually copied 'Messages.xml' at the location mentioned in the error message. After this&nbsp;step,&nbsp;SIS Events have started appearing in Historical Review application. Please see the attached updated sisev.log file as <em>sisev_Updated_13thJanuary.zip</em>. After making these changes now the above mentioned error message has also not come. But SIS Events are not appearing as exxpected for which <strong>Finding#35436</strong> is raised.</p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;" dir=ltr>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Raciborski, Mikolaj AUTOSOL PSS WRSW | Silvaggio, Gregory W EMR SYSS PWS PITT | [5 empty] | Implementation | U4 |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Historian&nbsp;Drop180&nbsp;(OS: Windows Server 2012 R2)</span></p></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | PA 4/14/16:&nbsp;Retested in U4 and Found fixed | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Historical Review application.</p> <p>2. Go to SIS tab.</p> <p>3. Select the required Historian and click on Start.</p> |  | U2 |  |  | FINDING | [6 empty] | 94877
35434 | FINDING | GBNT: "Macro Notes & parameter Info" window,default value field becomes uneditable, if user passes 66 characters on description/label field of any parameter | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:43 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:43 | 65720(dev), 65721(integration) |  |  | 2016-02-02 02:43 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-13 03:09 |  | <p>GBNT: &quot;Macro Notes&nbsp;&amp; parameter Info window&quot;, <strong>default value field</strong>&nbsp; becomes <strong>uneditable</strong>, if user passes&nbsp;66 characters or more then 66 characters&nbsp;on <strong>description/label field</strong> of any parameter. </p><p>As per the help file user can enter &nbsp;up to 80 characters on <strong>description/label field </strong>of any parameter.</p> | <p>If user enters a very large (&gt; 66 chars) macor param description on the GBNT:MacroNotes&amp;ParameterInfo dialog, the Description\Label column resizes to fit the longest description/label, which forces the DefaultValue column out of view and the user must scroll to see/edit it. After doing this, there was a bug that caused the user not to be able to click on any defaultValue column entry to edit it. that bug has been fixed.</p><p><br></p><p>work-around: use the TAB key to tab to the entry fields which you want to edit. That will allow you to edit any of the DefautlValue fields in this scenario until you get a release with this fix.</p> |  |  | <p>Enter 1 or more macro param descriptions on the GBNT:MacroNotes&amp;ParameterInfo dialog that is the max length supported [80 chars]. Press the Apply button to save/store the param description (or click on another param value or another row). Note that the columns are resized to show the longest param description when you do any of the latter. The default value column will now be out of view and you will have to scroll to it to see/edit those fields. Scroll to view/edit the default value fields. Verify that you can click to select any of the default value fields. Verify that you can edit any of these fields. Verify that you can still tab between fields.</p> | 0 |  |  |  |  | 0 |  |  | Forgot to add the horz scroll start to the current mouse click position to determine which column user was attempting to select... |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>Ovation3.6.0_U2</p><p>OS-WS12, WIN 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>GBNT:Macro Notes &amp; Parameter Info dialog: If a macro param description string is entered that is large enough to force the default value column out of view [must be scrolled to] , which takes about 66 chars, then the user could not click on the default value entry fields to select them to edit them. That was the bug that was fixed. The user could still successfully tab to these entry fields in order to edit/change them however - so the entry fields were not&nbsp;completely unusable after entering 66 chars...&nbsp; Bug fixed.</p><p><br></p><p>LB 02/02/16- Verified on Ovation3.6.0_U3 and observed the following things-</p><p>1)User can edit the default value field&nbsp;after entering 66&nbsp;character on description label field. </p><p>2)User is able to click to select any of the default value field and edit them.Tabs are present&nbsp;between the fields.</p><p>3)Horizontal scroll bar is added.</p><p>Hence this finding is closed by validation.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the&nbsp;developers studio and make a GBNT macro. </p><p>2) Open the created macro. </p><p>2) Now open the &quot;macro notes/parameter info&quot; window.&nbsp;Enter&nbsp;66 or more than 66 characters on description/label field of any parameter&nbsp;then try to edit default value field of any parameter&nbsp;.</p><p>&nbsp;&nbsp;&nbsp; The default value field become uneditable. </p><p><br></p> |  | U2 |  |  | FINDING | [6 empty] | 91810
35435 | FINDING | Ovation GBNT Application is crashing,if user exceeds the character limit on GBNT: "Macro Notes & parameter Info" window,default value field | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:55 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:55 | 65724(dev), 65725(integration) |  |  | 2016-02-02 02:55 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-13 04:00 |  | Ovation GBNT Application is crashing, if user <strong>exceeds</strong> the characters limit&nbsp; on GBNT: &quot;Macro Notes &amp; parameter Info&quot; window,<strong>default value field</strong>. | GBNT would crash if user entered more than 200 chars in the DefaultValue field of the GBNT:MacroNotes&amp;ParameterInfo dialog. |  |  | enter over 200 chars in the defaultValue field on the MacroNotes&amp;ParameterInfo dialog and make sure GBNT handles this case and reports an error and does not crash. | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>Ovation3.6.0_U2</p><p>OS-WS12, WIN 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Fixed. Had to exceed 200 char internal buffer size to get this error.</p><p><br></p><p>FYI. Validation. Please do not concentrate your testing of 3.6.0 GBNT on entering ridiculously large strings on the dialogs. This application has been in the field for nearly&nbsp;30&nbsp;years and this is NOT what users do - hence no one has ever reported such a finding/bug.&nbsp; </p><p><br></p><p>LB 02/02/16- Verified on Ovation3.6.0_U3 and observed that, GBNT Application is not crashing, if user exceeds the character limit on &quot;macro notes/parameter info&quot; window default value field. Instead of crash a warning messages is displayed &quot;Pt name exceeds 40 character limit for a fully qualified name&quot;. Hence this finding is closed by validation.</p><p><br></p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the&nbsp;developers studio and make a GBNT macro. </p><p>2) Open the created macro. </p><p>2) Now open the &quot;macro notes/parameter info&quot; window.&nbsp;Enter&nbsp;some characters on &nbsp;description/label field of any parameter&nbsp;then&nbsp;enter and <strong>exceed</strong> the&nbsp;characters limit on <strong>default value field </strong>of same parameter&nbsp;and press the apply button.</p><p>&nbsp;&nbsp;&nbsp;After pressing the apply button GBNT application crashes. Screenshot is also attached for your reference.</p> |  | U2 |  |  | FINDING | [6 empty] | 91811
35436 | FINDING | Unable to Decode messages appear in SIS Events for operations performed on CSLS | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:56 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:56 |  |  |  | 2016-04-13 23:37 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-13 04:59 |  | <p>Unable to Decode messages appear in SIS Events for operations performed on CSLS. </p> <p>We tried performing load operation of the CSLS followed by Controller Drop load, Reboot operation, Lock and Unlock operation. For all the mentioned operations, SIS Events appeared as <br>01/13/2016 15:33:57&nbsp;DROP30&nbsp;&lt;OtherSisEvent: CSLS06_D30: CSLS06_D30&gt;:&nbsp;[INTERNAL ERROR: Unable to decode (82)]<br>01/13/2016 15:28:15&nbsp;DROP30&nbsp;&lt;LsEvent: CSLS03_D30: CSLS03_D30&gt;:&nbsp;[INTERNAL ERROR: Unable to decode (423)]<br>01/13/2016 15:18:00&nbsp;DROP30&nbsp;&lt;LsEvent: CSLS03_D30: CSLS03_D30&gt;:&nbsp;[INTERNAL ERROR: Unable to decode (422)]</p> <p>Please see attached Historical Review Data file attached for the list of all SIS Events corresponding to specific operation.</p> <p>&nbsp;</p> <p>Observed following messages in <em>sisev.log</em> file:</p> <p>OvSisEvents.Service.exe Warning: 0 : LS_EVENTS: messageId 422 not found<br>OvSisEvents.Service.exe Warning: 0 : LS_EVENTS: messageId 423 not found</p> <p>OvSisEvents.Service.exe Warning: 0 : LS_EVENTS: messageId 82 not found</p> <p>Please see attached sisev.log file attached for the list of all messages.</p> <p>Please find attached Ovation Error log for reference.</p> <p><em>Note</em>: The Controllers on which SIS Charms is configured are downloaded with new <em>OCR1100Ctlr.out</em> file which contains the changes for <strong>Finding#35313</strong></p> |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | Raciborski, Mikolaj AUTOSOL PSS WRSW | [5 empty] | Implementation | U4 |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Historian&nbsp;Drop180&nbsp;(OS: Windows Server 2012 R2)</span></p></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | PA 4/14/16: Retested in U4 and found fixed | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Load the CSLS and the Controller Drop.</p> <p>2. Reboot the CSLS.</p> <p>3. Lock the CSLS.</p> <p>4. Unlock the CSLS.</p> |  | U2 |  |  | FINDING | [6 empty] | 94878
35446 | FINDING | SPO1.7.3: Windows Firewall is blocking mysqld.exe while installating SPO1.7.3 on W7, 64 bit system | Anselmo, Christine AUTOSOL PWS MNL | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Anselmo, Christine AUTOSOL PWS MNL | 2016-04-22 03:48 | [11 empty] | Anselmo, Christine AUTOSOL PWS MNL | 2016-04-22 03:48 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-01-14 04:18 |  | It has been observed that while installing SPO1.7.3 software on Windows7, 64bit (Drop157) system, windows firewall blocks mysqld.exe, however this issue has not been observed on Windows Server 2008R2 Operating system. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Drop157 (W7, 64 Bit), OV360 (NET36), SPO.1.7.3 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | This is expected. Just allow access of mysqld.exe when asked. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Insert SPO1.7.3 released Installation media on Drop157.<br>2. Run setup.exe<br>3. During installation&nbsp; process setup asked to allow access for mysqld.exe in windows firewall. Please check the attached snapshot.<br>PS: After allowing access to this exe setup completes successfully. |  | U2 |  |  | FINDING | [6 empty] | 95423
35447 | FINDING | SPO1.7.3 installation set up could not install ‘.NET Framework 3.5’ feature on WS2012 Engineering Work Station machine. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-05-25 15:00 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-05-25 15:00 |  |  |  | 2016-05-25 14:59 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-01-14 04:21 |  | <p>While installation of Smart Process Optimizer 1.7.3 on OV3.6.0 machine Drop128 (Windows Server_2012), a pop-up window was observed stating that windows feature ‘.NET Framework3.5’ could not be installed. Snapshot ‘SPO_.NET_error.jpg’ is attached for reference.<br>After closing this pop-up and finishing the installation process followed by drop reboot, it is observed that ‘Smart Process Optimizer’ Service is not available at Control Panel -&gt; Administrative Tools -&gt; Services.</p><p><br></p><p>IC 5/25/16&gt; closed finding, track as SDR #36614, documented installation steps in SOP 1.7.3 DIR (#12-12). Changed to CAT 3 since workaround exists. <br><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Drop128 (WS2012), OV360 (NET36), SPO.1.7.3 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | <p><font face="Times New Roman" size=3> On WS2012 machine before the installation of&nbsp; SPO1.7.3, <strong>.NET Framework 3.5 </strong>needs to be installed.</font></p><p><font face="Times New Roman" size=3><br></font></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=3><strong>Steps to “Enable .NET Framework 3.5 by using the Add Roles and Features Wizard”</strong></font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><b><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><a title="Click to collapse. Double-click to collapse all."><font color="#0000ff" size=3>Requirements</font></a></span></b></p><ul><li><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;">Windows&nbsp;Server 2012 R2</span></li><li><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;">Installation media</span></span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;">Administrator user rights. The current user must be a member of the local Administrators group to add or remove Windows features.</span><font face="Times New Roman" size=3> </font></span><font face="Times New Roman" size=3><br></font></li></ul><p style="margin:0in 0in 0pt;"><b><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><a title="Click to collapse. Double-click to collapse all."><font color="#0000ff" size=3>Steps</font></a></span></b></p><p style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;1.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">In Server Manager, click <b>Manage</b> and then select <b>Add Roles and Features</b> to start the Add Roles and Features Wizard. </span></span></font></p><font face="Times New Roman" size=3><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><p style="margin:0in 0in 12pt 0.5in;color:rgb(0, 0, 0);text-indent:-0.25in;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">2.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:12pt;"><font face=Calibri>On the <b style="">Before you begin</b> screen, click next.</font></span></p><p style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"> </p><p style="margin:0in 0in 12pt 0.5in;color:rgb(0, 0, 0);text-indent:-0.25in;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">3.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select installation type</b> screen, select <b>Role-based or feature-based installation</b>. Click next.</span></p><p style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"> </p><p style="margin:0in 0in 12pt 0.5in;color:rgb(0, 0, 0);text-indent:-0.25in;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">4.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:12pt;"><font face=Calibri>On <b style="">Select destination Server</b> screen, s</font></span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">elect the target server. Click next.</span></p><p style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"> </p><p style="margin:0in 0in 12pt 0.5in;color:rgb(0, 0, 0);text-indent:-0.25in;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">5.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:12pt;"><font face=Calibri>On <b style="">Select server roles</b> screen, click next.</font></span></p><p style="margin:0in 0in 12pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"> </p><p style="margin:0in 0in 12pt 0.5in;color:rgb(0, 0, 0);text-indent:-0.25in;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">6.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">On the <b>Select features</b> screen, check the box next to <b>.Net Framework 3.5 Features</b>. Click next</span></p></span></font><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">On the <b>Confirm installation selections</b> screen, a warning will be displayed asking <b>Do you need to specify an alternate source path?</b><span style="color:rgb(31, 73, 125);"> </span>If the target computer does not have access to Windows Update, click the <b>Specify an alternate source path</b> link to specify the path to the <b>\sources\sxs</b> folder on the installation media and then click <b>OK</b>. After you have specified the alternate source, or if the target computer has access to Windows Update, click the <b>X</b> next to the warning, and then click <b>Install</b>.</span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><br></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">After the .NET Framework installation is completed successfully, install SPO.1.7.3 as per the manual.</span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"><br></span></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.Install Smart Process Optimizer 1.7.3 from released CD. </p><p>2.Poceed as per the instructions in the manual.&nbsp;&nbsp; </p><p>3.During installation, pop-up will appear&nbsp; stating that windows feature ‘.NET Framework3.5’ could not be installed. Snapshot ‘SPO_.NET_error.jpg’ is attached for reference.</p> |  | U2 |  |  | FINDING | [6 empty] | 97753
35465 | FINDING | GBNT Application is crashing if user exceeds the character limit of process point. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:23 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-02 02:23 | 65703 (integration) 65702(dev) |  |  | 2016-02-02 02:23 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-15 03:29 |  | GBNT Application is crashing if user exceeds the character limit of process point. | GBNT crashed (or hung when I tested this Finding) when I entered more than 132 chars into ptname/recfld entry field on ProcessPoint dialog.&nbsp; Now GBNT will not crash and will display an appropriate error dialog... |  |  | Enter WAY, WAY, WAY too&nbsp;many chars in ptname/recfld entry field (132+) to see this error. Now you can enter as many as you feel the need to when testing and you will get an error dialog and no crash.... | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | Internal buffer used to store ptname/recfld entry fld data read from dialog was sized to 132 chars, and validator overflowed that limit.... |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Fixed. Had to entered 132+ chars into ptname/recfld entry fld on ProcessPoint dialog&nbsp;to get this error. Any number of chars less than that produced an error stating that max # chars in ptname exceeded and no GBNT crash!</p><p><br></p><p>LB 02/02/16- Verified on Ovation3.6.0_U3 and observed that, GBNT Application is not crashing, if user exceeds the character limit of process point. Instead of crash a warning messages is displayed &quot;Pt name exceeds 40 character limit for a fully qualified name&quot;.Hence this finding is closed by validation.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developers studio.</p><p>2)Insert a new diagram, after this add a process point.</p><p>3)On the pt Name/Rec fld enter and exceed the character limit and press the apply button.</p><p>After doing this GBNT application crashes.<br></p> |  | U2 |  |  | FINDING | [6 empty] | 91809
35466 | FINDING | GBNT:Macro notes &Parameter Info window is accepting incorrect data format for some parameters and highlighting the correct data format instead of incorrect data format in some cases. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-15 03:27 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-15 03:27 | 65761(dev), 65763(integration) |  |  | 2016-02-15 03:27 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-15 03:36 |  | GBNT: Macro notes &amp;Parameter Info window is accepting&nbsp; incorrect data format for some parameters and highlighting the correct data format instead of incorrect data format in some cases.When a user enters the wrong data formats under the default value field of GBNT: Macro notes &amp; Parameter Info window.Warning messages pops up and that particular row get highlighted with red color. For eg:- $CONST1 parameter. Suppose user make a macro consists of 3 point,2 text and one constants. Now open the GBNT: Macro notes &amp; Parameter Info window enter some data under description/label field and default value field. Now open the generic text editor and change the value of $CONST1 say 1.1AS which is not a supported data format for $CONST1 .Now save the generic text editor and open the GBNT: Macro notes &amp; Parameter Info window and verify that same data appears here. Now press apply button a warning message pops up because wrong data format is entered for $CONST1 and its default value row get highlighted with red color. Now press the cancel button and save the macro and again open the GBNT: Macro notes &amp; Parameter Info window and verify that $CONST1 default value row is highlighted with red color or not? As per my&nbsp; observation instead of highlighting the&nbsp; $CONST1 default value row some other row get highlighted with red color. Screenshot is also attached for your reference. |  |  |  | Should not be able to put an incorrect macro default value in the DEF_MACRO_PARAMS command via integrated or generic text editor any longer. Compile routine should catch these errors (just like the dialog). Check that. Also check if you can duplicate the issue of getting the GBNT:MacroNotes&amp;ParameterInfo dialog to highlight the wrong default value in red when an error does occur. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | Changed compile routine for the DEF_MACRO_PARAMS command to check for the same errors as the GBNT:MacroNotes&amp;ParameterInfo dialog checks for. The compile routine is called from the integrated source editor, the generic text editor, on batch compiles, and on opening an existing&nbsp;graphic in GBNT. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Real issue here is that the compile routine for the DEF_MACRO_PARAMS command (from integrated source editor, generic text editor, or loading a graphic into GBNT) does not do the same error-checking that the GBNT:MacroNotes&amp;ParameterInfo dialog does. This finding wouldn't occur had the generic text editor not compiled the changes to the DEF_MACRO_PARAMS command successfully! Therefore, the compile routine for the DEF_MACRO_PARAMS command was changed to check for the same errors as the dialog does (which it should have been doing all along btw). I could not duplicate the issue with the wrong param being highlighted in red. See if you can still duplicate that after you get this fix please. I saw the screen capture, so I believe you got it to happen, just saying that I could not get it to happen no matter what I did while testing this ....</p><p><br></p><p>LB 02/15/16-Verified on ovation 3.6.0_U3 and observed that user is not able to put an incorrect macro default value in the DEF_MACRO_PARAMS command via integrated or generic text editor. Compile routine is catching these errors. Since user is not able to enter and save the wrong values,&nbsp;so GBNT:MacroNotes&amp;ParameterInfo dialog&nbsp;cannot &nbsp;highlight the wrong default value in red when an error does occur. Hence this finding is closed by validation.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the developers studio.</p><p>2)Insert a new macro consist of of 3 point,2 text and one constants,.</p><p>3)Open the GBNT:Macro notes &amp; Parameter Info window enter some data under description/label field and default value field.<br>4)Now open the generic text editor and change the value of $CONST1 say 1.1AS which is not a supported data format for $CONST1.</p><p>5)Save the generic text editor and open the GBNT:Macro notes &amp; Parameter Info window and&nbsp;verify that same data change appears for $CONST1.&nbsp;<br>6)Now press apply button a warning message pop up because wrong data format is entered for $CONST1 and its default value row get highlighted with red color&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>7)Now press the cancel button and save the macro and again open the GBNT:Macro notes &amp; Parameter Info window and verify that $CONST1 default value row is highlighted with red color or not?.</p><p>8)As per my&nbsp; observation instead of highlighting the&nbsp; $CONST1 default value row some other row get highlighted with red color.Screenshot is also attached for your reference<br></p> |  | U2 |  |  | FINDING | [6 empty] | 92259
35484 | FINDING | Bumpless failover is not occuring in redundant virtual controllers | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-25 15:27 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-25 15:27 | 67657 |  |  | 2016-05-25 15:27 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-01-15 10:42 |  | <p>Bumpless failover is not occurring in redundant virtual controllers.&nbsp; A ramping value is being trended, and on failover, the value consistently reverts to 0. </p><p>see attached trend.</p> |  |  |  |  | 0 |  |  |  | The bumpless failover appears to be fixed.&nbsp; A new finding will be written against the redundant VC in general. | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U7 |  | 3.6.0 U2 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | Updated the ddb driver so that a controller in backup mode will update internal memory from the ddb data on the windows host. | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Trend a changing value and reboot the 'in control' virtual controller of a redundant pair. |  | U2 |  |  | FINDING | [6 empty] | 97758
35488 | FINDING | Trend Application is crashing if user exceeds the character limit on point name entry field. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:58 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:58 | 65792 |  |  | 2016-03-15 00:58 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-18 03:04 |  | Trend Application is crashing if user exceeds the character limit on point name entry field . If user exceeds the character limit than application&nbsp;may generate some error messages/warning messages&nbsp;instead of crash. |  |  |  | Retest. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U4 |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Added code to restrict maximum length that can be entered.</p><p><br></p><p>LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that trend application is restricting the character&nbsp;length on point name entry field&nbsp;and application is not crashing.Hence this finding is&nbsp;closed by validation.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the trend application.</p><p>2)Select the <strong>Trend</strong> tab.</p><p>3)Click on <strong>add</strong> option.</p><p>4)On the <strong>Point Name</strong> field enter 470 or more characters and press the OK button.</p><p>After doing this Trend application crashes.</p><p>Screenshot is also attached for your reference.</p> |  | U2 |  |  | FINDING | [6 empty] | 93333
35507 | FINDING | Unable to load CSLS if SECPARAM Algorithm is connected to POUT pin of LSAVTR algorithm | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-13 08:39 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-13 08:39 |  |  |  | 2016-05-13 08:38 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-20 23:16 |  | <p>Unable to load CSLS if&nbsp;SECPARAM Algorithm&nbsp;is connected to POUT pin of LSAVTR algorithm.&nbsp;<span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">If secure parameter is connected to POUT pin of LSAVTR algorithm no error appears in Control Builder, but an error&nbsp;window appears after CSLS CRC load confirmation window.&nbsp;</span> </p> <div><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">But if Secure parameter is replaced with an external point then load is successful and no error appears.&nbsp;</span></div> |  |  |  |  | 0 |  |  |  | In U7 | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p><br></p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="FONT-WEIGHT:bold;">Steps:</span> <div> <ol> <li>Add LSAVTR Algorithm and connect required input and output.(No error in control builder)</li> <li>Load CSLS. Load successful.</li> <li>Add a POUT pin and connect it to a Secure Parameter.(No error in control builder)</li> <li>Load CSLS. Load unsuccessful. Error&nbsp;window appears as&nbsp;&quot;RT status received on controller Script Processing; rt null item&quot; </li> <li>Replace the Secure parameter with an external point.(No error in control builder)</li> <li>Load CSLS. Load successful.</li></ol> <div>(Please refer attached screenshot <span style="FONT-STYLE:italic;">Pout_SP.jpg </span>for reference)</div></div> <div><span style="FONT-WEIGHT:bold;"></span>&nbsp;</div> <div><span style="FONT-WEIGHT:bold;">Observation:</span></div> <p>CSLS should load when POUT is connected to secure parameter.</p> |  | U2 |  |  | FINDING | [6 empty] | 96820
35512 | FINDING | Rt Index out of range error comes during CSLS load when the user uses more than one Secure Parameter at an output point | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:11 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:11 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-22 00:33 |  | <p>Rt Index out of range error comes during CSLS load when the user uses more than one Secure Parameter at an output point. If the error is expected because of incorrect usage of Secure Parameter then a proper message should be displayed after CSLS load Failure or while saving the sheet in the Control Builder. </p> <p>&quot;RT Status Received on Controller Script Processing: rt index out of range&quot; error doesn't provide the user much idea of the cause of the failure, especially in case if the user loads multiple sheets together.</p> <p><em>Note:</em> </p> <p>a. According to OW352_R1101 Ovation Q-Line and Specialty Algorithms Reference Manual, the SECPARAM algorithm is used as a connector.</p> <p>b. If we connect&nbsp;multiple external page connectors to the output point of the SIS Algorithm, then the CSLS load is successful.</p> <p>Please find attached following items in the <em>Finding35512.zip</em> file:</p> <p>a. CSLS load script.</p> <p>b. Screenshot of the error after CSLS load failure.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | Error is a result of multiple declaration of the same secure parameter. This either can be permitted by control builder either script generation should skip duplicate.<br> |  | 35 | FINDING |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on&nbsp;Historian&nbsp;Drop180&nbsp;(OS: Windows Server 2012 R2)</span></p></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Make a simple logic having an LSDVTR algorithm in Ovation Control Builder.</p> <p>2. Connect two Secure Parameters at the output.</p> <p>3. Save the SIS Control Sheet.</p> <p>4. Load the CSLS.</p> <p>5. The load operation fails with the following error &quot;RT Status Received on Controller Script Processing: rt index out of range&quot;.</p> |  | U2 |  |  | FINDING | [6 empty] | 95738
35534 | FINDING | GBNT generates warning "Unresolved Points" when referencing Ovation 3.2.0 points from Ovation3.6.0 and vice versa. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:13 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:13 |  |  |  | 2016-06-08 08:13 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-01-26 15:14 |  | <p>When referencing Ovation 3.2.0 points in a Ovation 3.6.0 graphics builder , it generates warning window stating &quot;Unresolved Points&quot; while compiling even though the values are updated in Online graphics and other ovation applications. </p><p>Same is the scenario when referencing Ovation 3.6.0 points in a Ovation 3.2.0 graphics.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0</p><p>Ovation 3.2.0</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | This is an Oracle issue. The 3.2.0 and 3.6.0 versions of Oracle are not compatible. GB makes Oracle calls to get the point sids, No plans to change GB to work around this issue. GBn just generates a warning- it still produces a valid output file and the runtime graphics get the sids at runtime correctly for those that were unresolved.&nbsp;So the &nbsp;graphics will still function correctly at runtime. Chances are customers will not have both Ovation 3.2.0 systems and Ovation 3.6.0 systems - so this shouldn't be an issue in the real world.... | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1) Create a new Graphic diagram.<br>2) Add a process point.<br>3) Enter Pt Name &gt; Any existing Ovation 320 point (fully qualified)<br>4) Add a process point.<br>5) Enter Pt Name &gt; Any existing Ovation 350 point (fully qualified)<br>6) Add a process point.<br>7) Enter Pt Name &gt; Any existing Ovation 360 point (fully qualified)<br>8) Save</p><p>Observation : A warning window appears stating &quot;Unresolved Points&quot; stating reference to Ovation 3.2.0 Points. The reason displayed mentions &quot;Network Connection Unavailable&quot;.</p><p>9) Download the graphics to a drop. <br>10) Open the graphic diagram.</p><p>Observation:&nbsp; Warning window appears stating &quot;Unresolved Points&quot; but the values are updated for all points.<br>The same points can be reviewed in Point Review window.</p><p>Please find the screenshots attached.<br></p> |  | U2 |  |  | FINDING | [6 empty] | 98391
35536 | FINDING | GBNT:Integrated Source Editor,Append and Insert mode edit options are not working. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-28 06:03 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-28 06:03 |  |  |  | 2016-01-28 06:03 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-01-27 03:54 |  | <p>GBNT: Integrated Source Editor, <strong>Append</strong> and <strong>Insert</strong> mode edit options are not working. Insert mode is used&nbsp;to&nbsp;enter the character&nbsp;in the selected command at the cursor position while Append mode to&nbsp;enter the character&nbsp;in the selected. command at the end of line</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>I can't duplicate this. Works fine for me. Is the command selected (source highlighted in reverse video) for edit before you enter insert/append mode? What character(s) are you trying to insert/append? What locale are you using? Please attach the exact source command you are trying to&nbsp;insert/append&nbsp;and answer these questions.</p><p><br></p><p>LB-01/28/16-I have verified again and observed that this is working as per the design. Previously I Opened the <strong>integrated source editor</strong> of any diagram or macro then&nbsp;selected the edit option <strong>cmd for edit</strong> option to edit the source. After this Selected the&nbsp;<strong>Insert</strong> <strong>mode or append mode option </strong>and then changed the cursor position and try to append or insert the character, that's why it was not working.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the <strong>integrated source editor</strong> of any diagram or macro.</p><p>2)Go to edit option and select <strong>cmd for edit</strong> option to edit the source.</p><p>3)Select <strong>Insert</strong> <strong>mode</strong> and try&nbsp;to&nbsp;enter the character&nbsp;in the selected command at the cursor position.</p><p>4)In the same way Select&nbsp;<strong>Append</strong> <strong>mode</strong> and try&nbsp;to&nbsp;enter the character&nbsp;in the selected command at the end of line.</p><p><br></p> |  | U2 |  |  | FINDING | [6 empty] | 91700
35552 | FINDING | Alarm Shelve / Unshelve option generates incorrect message in Alarm and Point Review application. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-03-16 10:32 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-03-16 10:32 | 66178 |  |  | 2016-03-16 10:32 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-01-27 15:33 |  | <p>Alarm Shelve / Unshelve option in Alarm/Limit ribbon tab&nbsp;of Ovation Alarms and Ovation Point Review&nbsp;application generates incorrect message. The message generated is 'Alarm Shelve: ON' and 'Alarm Shelve: OFF' when Alarm is Shelved or Unshelved .</p><p>The message generated from other Ovation applications is 'Alarm Shelve' and 'Alarm Unshelve'.</p><p>Please find the screenshot attached for reference.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0_U4 |  | <p>Ovation 3.6.0</p><p>Windows 7 64 Bit</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | Tested in U4. Found the issue to be fixed. Hence closing this finding. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1) Open Ovation Alarms / Point Review application.</p><p>For Point Review run a review for points .</p><p>2) Select a point (In Alarm Condition)&nbsp;.</p><p>3) Navigate to Alarm/Limit tab.</p><p>4) Click on 'Alarm&nbsp;Shelve' option.</p><p>5) Enter reason and duration.</p><p>6) Press 'Ok'.</p><p>After the point is Shelved.</p><p>7)&nbsp;Again select a point.</p><p>8)&nbsp;Click on 'Alarm&nbsp;Unshelve' option.</p><p>9) Press 'Ok'.</p><p>After the point is Unshelved.</p><p>10) Open 'Historical Review' application.</p><p>11) Navigate to Operator Event tab.</p><p>12) Navigate to filter tab and select 'Alarm Shelved' and&nbsp;'Alarm Unshelved' subtype.</p><p>13) Run query .</p><p><br></p><p>Observation:</p><p>The message displayed is 'Alarm Shelve: ON' and 'Alarm Shelve: OFF' . Please see the screenshot attached for reference.<br></p> |  | U2 |  |  | FINDING | [6 empty] | 93446
35568 | FINDING | CSLS load script is not updated with Debounce 'Glitch' and 'Average' Configuration for LSDI SIS I/O CHARMs attributes | Daly, Joshua D EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-19 03:31 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-19 03:31 |  |  |  | 2016-04-19 03:31 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-29 05:21 |  | <p>CSLS load script is not updated with Debounce 'Glitch' and 'Average' Configuration for LSDI SIS I/O CHARMs attributes. </p> <p>Please find attached screenshot of the Attributes tab of LS DI SIS I/O Charms in&nbsp;Ovation Developer Studio and CSLS load Scripts when Debounce option is&nbsp; set to i) 'None'&nbsp;&nbsp;ii) 'Glitch' and iii)&nbsp;'Average' in <em>Finding35568.zip</em> file.</p> <p><em>Note:</em></p> <p>a. When the Debounce Option is changed from None to Delay then CSLS load script is updated with the configuration as</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p>OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=T } }</p></blockquote> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 35 | FINDING |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">CSLS Used: </span><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">D30_</span><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">CSLS03</span></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>Updated the charms template to retrieve the value correctly from the database server. This should be included in the next build</p> <p>&nbsp;</p> <p>PA 04/19/2016: Working correctly in Ovation3.6.0_U6 Build. Now the parameters are getting updated as</p> <p>None --&gt; OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=0 } }</p> <p>Delay --&gt; OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=1 } }</p> <p>Glitch --&gt; OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=2 } }</p> <p>Average --&gt; OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=3 } }</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure LS DI 24VDC Low-side CHARM&nbsp;or LS DI NAMUR CHARM.</p> <p>2. Load the CSLS and the Controller with default attributes.</p> <p>3. Change the Debounce Option from None to Glitch in the Attributes tab.</p> <p>4. Load the CSLS and the Controller.</p> <p>5. Compare the load script before step#3 and after step#4.</p> <p>&nbsp;&nbsp;&nbsp;The configuration field for Debounce Option remains set at V=F, without any changes.</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p>OV { TG='DEBOUNCE_OPTS' FLD { TG=CV V=F } } </p></blockquote> <p dir=ltr>7. Similar behaviour is observed when Debounce option is set to 'Average'.</p> |  | U2 |  |  | FINDING | [6 empty] | 95205
35578 | FINDING | Delay, Glitch and Average attribute for SIS I/O LSDI CHARMs does not work | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kijkowski, Tadeusz AUTOSOL PSS WRSW | 2016-09-08 08:42 | [11 empty] | Kijkowski, Tadeusz AUTOSOL PSS WRSW | 2016-09-08 08:42 |  |  |  | 2016-09-08 08:42 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-01-31 22:31 |  | <p>Delay, Glitch and Average attribute for SIS I/O LSDI CHARMs&nbsp;does not work. CSLS load script gets updated with the selected configuration but functionality is not working.<br>Please find attached <em>Finding35578.zip</em> which contains:</p> <p>a)&nbsp;CSLS load scripts generated before and after&nbsp;the Debounce option is selected as 'Delay', 'Glitch' and 'Average'&nbsp;the CSLS is loaded.</p> <p>b) Screenshot of the Attributes tab of LS DI SIS I/O Charms in&nbsp;Ovation Developer Studio </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | Debounce Options work fine, but contrary to Developer Studio labels and our documentation, Debounce Timer parameter units are milliseconds and not seconds. |  | 35 | FINDING |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Ov3.6.0_U2 on DBS drop100 (OS: Windows Server 2012 R2) <br>CSLS Used: D30_CSLS03 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>Tracked by SDR number 34143</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure LS DI 24VDC Low-side CHARM or LS DI NAMUR CHARM.<br>2. Load the CSLS and the Controller with default attributes.<br>3. Change the Debounce Option from None to Delay/Glitch/Average one by one&nbsp;in the Attributes tab.</p> <p>4. Set the Debounce Time to 30 sec.</p> <p>5. CSLS gets loaded with CRC changes.<br>6. Now observe the values coming from LS DI SIS I/O CHARMs in Trend application.<br>7. Next change the values of LS DI Dry Contact by making and breaking the contact.<br>8. Change in the values get reflected in the Trend without any Delay.<br></p> |  | U2 |  |  | FINDING | [6 empty] | 102378
35587 | FINDING | Sending a simulator partial save command to a VC while running may cause it to fall briefly off the highway | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-01 14:57 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-01 14:57 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-01 14:56 |  | Performing a partial snapshot of a VC in run mode (not frozen) may caused it to briefly go off the highway.&nbsp; The partial snapshots are used for the backtrack feature which is meant to save at specific intervals while the simulator and controller are running. Please see attached file and note that at 15:41:18, the trended value froze at 30 for 3 seconds. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0 U3</p> |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Perform partial simulator saves while the VCs are not frozen.&nbsp; Observe the system status graphic to watch for VC going off highway. |  | U3 |  |  | FINDING | [6 empty] | 91799
35588 | FINDING | RVP test procedure 3.6.0_RVP_SVTP_rev1.0 needs improvement | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 07:33 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 07:33 | [7 empty] | Lal, Ramesh External | 2016-02-01 20:22 |  | <p>Following Test cases of SVTP 3.6.0_RVP_SVTP_rev1.0 should be rewritten as below:</p><p>5.1.2 a) With the valve position at 25%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 25% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; b). Should be deleted.</p><p>5.1.3 b) With the valve position at 50%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 50% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c). Should be deleted.</p><p>5.1.4 b) With the valve position at 75%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 75% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c). Should be deleted.</p><p>5.1.5 b) With the valve position at 95%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 95% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c). Should be deleted.</p><p>5.1.6 b) With the valve position at 20%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 20% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c). Should be deleted.</p><p>5.1.7 b) With the valve position at 5%, remove the RVP module. Valve position will drop to 0%. Re-insert the module. Verify the valve position regains to 5% as the module starts up and enters<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;normal mode.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c). Should be deleted.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U2 |  |  | FINDING | [6 empty] | 91829
35590 | FINDING | Reasons field accepts more than 80 characters in request confirmation window while Alarm Shelve or Alarm check OFF operation. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-08 23:58 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-08 23:58 | 66353 |  |  | 2016-04-08 23:58 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-02-02 04:31 |  | <p>In Alarm Application or PI application </p><p>While Alarm Shelve or Alarm check&nbsp;OFF operation,&nbsp;request confirmation window appeared. Request confirmation window contain <strong>Reason</strong> filed,&nbsp;here user can enter&nbsp;N number of characters (verified more than 100)&nbsp;in <strong>Reason</strong> field without any&nbsp;warning &nbsp;.</p><p>More than 80 characters should not be&nbsp;allowed to enter in&nbsp;Reason field. For reference screenshot&nbsp; reason.jpg is attached.</p><p><br></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  | <p>Ov 3.6.0 + EWS.</p><p>Alarm application OR Point Information </p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Verified in U4 found fixed. Hence finding is closed. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>In Alarm Application or PI application- Perform &nbsp;Alarm Shelve or Alarm check&nbsp;OFF operation for a point.</p><p>Confirm <strong>Alarm check OFF request</strong> window appear while alarm check remove operation/ <strong>Confirm Alarm shelve request </strong>window appeared while Alarm shelve operation.&nbsp;</p><p>This window ask for reason, here user can enter N number of character more than 100 and can be applied without any warning.&nbsp;</p><p>Note: In Point information (Alarm check remove/Shelve comment)&nbsp;&nbsp;<strong>RE </strong>field working fine. Though user applied more than 100 characters in reason field,&nbsp;<strong>RE </strong>field&nbsp;show upto 80 character( show 1st 80 characters of applied reason).&nbsp;&nbsp;&nbsp;&nbsp;</p><p><strong>Confirm Alarm shelve request </strong>window appeared while Alarm shelve operation.&nbsp;</p> |  | U2 |  |  | FINDING | [6 empty] | 94660
35595 | FINDING | RVP test procedure 3.6.0_RVP_SVTP_rev1.0 needs improvement | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 12:16 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 12:16 | [7 empty] | Lal, Ramesh External | 2016-02-02 10:41 |  | <p>Following test cases of 3.6.0_RVP_SVTP_rev1.0 should be re-written as given below:</p><p>5.3.3 b) With the valve position at 50%, remove the RVP module. The valve position will drop to 0% as there is no drive signal to servo coil. Reinsert the module, verify that&nbsp;&nbsp;module starts up and&nbsp;&nbsp;&nbsp;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;enters Local-Manual mode. </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c) Verify that the valve position at 50% can&nbsp; be controlled by SLIM. &nbsp;</p><p>5.3.4 b) With the valve position at 5%, remove the RVP module. The valve position will drop to 0% as there is no drive signal to servo coil. Reinsert the module, verify that&nbsp;&nbsp;module starts up and&nbsp;&nbsp;&nbsp;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;enters Local-Manual mode. </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c) Verify that the valve position at 5%&nbsp;can&nbsp; be controlled by SLIM.</p><p>5.3.5 b) With the valve position at 95%, remove the RVP module. The valve position will drop to 0% as there is no drive signal to servo coil. Reinsert the module, verify that&nbsp;&nbsp;module starts up and&nbsp;&nbsp;&nbsp;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;enters Local-Manual mode. </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c) Verify that the valve position at 95% can&nbsp; be controlled by SLIM.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U0 |  |  | FINDING | [6 empty] | 91837
35596 | FINDING | RVP Test procedure 3.6.0_RVP_SVTP_rev1.0 needs improvement | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 12:16 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 12:16 | [7 empty] | Lal, Ramesh External | 2016-02-02 10:49 |  | <p>Following test cases should be removed from 3.6.0_RVP_SVTP_rev1.0:</p><p>5.3.6 : Seating Using SLIM: When controller is failed or switched off to pave the way for SLIM to take control of the valve position, all tuning parameters in Tuning graphics are timed out. Therefore,<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp; Seat Limit , target position etc can not be set in order to test 'Seating Using SLIM'. Hence, this test case should be removed.</p><p>5.3.7 : Backseating Using SLIM: When controller is failed or switched off to pave the way for SLIM to take control of the valve position, all tuning parameters in Tuning graphics are timed out. <br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Therefore,&nbsp; backSeatLimit , target position etc can not be set in order to test Backseating Using SLIM:. Hence, this test case should be removed.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U0 |  |  | FINDING | [6 empty] | 91836
35598 | FINDING | RVP test procedure 3.6.0_RVP_SVTP_rev1.0 needs changes | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 16:22 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-02 16:22 | [7 empty] | Lal, Ramesh External | 2016-02-02 16:05 |  | <p>Test cases 5.7.1.1 g),&nbsp;&nbsp;5.7.2.1 g),&nbsp;5.7.3.1 g), 5.7.4.1 g), 5.7.5.1 g), 5.7.6.1 g), 5.7.7.1 g),&nbsp;5.7.8.1 g),&nbsp; 5.7.9.1 g),&nbsp; 5.7.10.1 g): 125 Milliseconds should be changed to 120 Milliseconds</p><p>Test cases 5.7.1.3 d),&nbsp;&nbsp;5.7.2.3 d),&nbsp;&nbsp;5.7.3.3 d),&nbsp;&nbsp;5.7.4.3 d), 5.7.5.3 d), 5.7.6.3 d), 5.7.7.3 d), 5.7.8.3 d),&nbsp;5.7.9.3 d),&nbsp; 5.7.10.3 d): Reserved should be replaced with DC voltage input LVDT&nbsp;&nbsp;</p><p>Test cases 5.7.1.5 d),&nbsp;&nbsp;5.7.2.5d),&nbsp;&nbsp;5.7.3.5 d),&nbsp;&nbsp;5.7.4.5 d), 5.7.5.5 d), 5.7.6.3 d), 5.7.7.5 d), 5.7.8.5 d),&nbsp;5.7.9.5 d),&nbsp; 5.7.10.5 d):&nbsp;'Not used' should be added as an option&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U3 |  |  | FINDING | [6 empty] | 91844
35599 | FINDING | Virtual controllers do not operate well on Server 2012 R2 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-06-07 14:30 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-06-07 14:30 |  |  |  | 2016-06-07 14:30 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-02 16:24 |  | This finding is in addition to finding 34955 (wrtap can not be installed on 2012 R2).&nbsp;&nbsp;&nbsp; Even when a wrtap driver can be installed on 2012 R2, different issues have been seen.&nbsp; Machines have been seen to lock up with the VCs running, but runs fine without the VCs.&nbsp; Another machine will only allow the host machine or the VCs to be visible on the network, not both, even though bridged properly. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Use 2012 R2 as VCH running multiple VCs |  | U3 |  |  | FINDING | [6 empty] | 98354
35600 | FINDING | RVP test procedure 3.6.0_RVP_SVTP_rev1.0 needs changes | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-03 10:35 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-03 10:35 | [7 empty] | Lal, Ramesh External | 2016-02-02 18:56 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><br></p><span lang=EN-US style="color:red;"><p style="margin:0cm 0cm 0pt;"><br></p><font face=Times size=3><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman"> <br></font></p><p style="margin:0cm 0cm 0pt;"><br></p><span lang=EN-US style="color:windowtext;"><p style="margin:0cm 0cm 0pt;"><font face="Times New Roman"> </font><span lang=EN-US style="color:windowtext;font-size:14pt;">Following tuning parameters are not shown in tuning graphics , hence may be removed from test case 5.8.4 of 3.6.0_RVP_SVTP_rev1.0.<br></span><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:14pt;">&nbsp;&nbsp;&nbsp; slimBusAddr, manualRate, bfpM, bfpB, calRateFast, calRateSlow, maxDelta, min2dry</span></p></span><p style="margin:0cm 0cm 0pt;"><br></p></font><p style="margin:0cm 0cm 0pt;"><br></p><p style="margin:0cm 0cm 0pt;"><br></p></span><p style="margin:0cm 0cm 0pt;"><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U0 |  |  | FINDING | [6 empty] | 91857
35610 | FINDING | SRF2227: BIT3 of 2W status word (Point Value from I/O scan) of digital hardware output points is not updating as per actual value | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Durbin, Michael EMR SYSS PWS PITT | 2016-03-30 15:07 | [11 empty] | Durbin, Michael EMR SYSS PWS PITT | 2016-03-30 15:07 |  |  |  | 2016-03-30 15:07 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-02-04 04:07 |  | As per SRF#2227, In the case of points tied to physical hardware, this bit ( BIT3 of 2W status word ) represents the value that is currently being read from the I/O module. While testing this functionality, it has been observed that value at BIT3 of 2W status word (Point value from I/O Scan) of Digital Hardware Output points (LD &amp; DD point records) never updates as per the actual value of the point while Scan is ON.&nbsp; However, same functionality of Digital Hardware Input Points is working fine. Please check the attached snapshots. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab, Ov3.6.0, Net26, DBS220, Drop24/74 (OCR400) |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>SRF2227 only applies to input points.</p><p><br></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Configured digital hardware output points of LD and DD point record type from configuration studio. <br>2. Made a control logic to continuously update the value of these digital hardware output&nbsp;points.<br>3. Value at BIT3 of 2W status word of these digital hardware output points never updates as per the actual&nbsp;changing value of point, while scan is ON.<br>4. Configured some digital hardware input points also with the same procedure and value at BIT3 of 2W status word of these Digital hardware input points is updating continuously as per the actual&nbsp;value of point, while scan is ON. |  | U3 |  |  | FINDING | [6 empty] | 94111
35611 | FINDING | SRF2227: BIT3 of 2W status word (Point Value from I/O scan) of Digital Data Link points is not updating as per the actual value. | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Durbin, Michael EMR SYSS PWS PITT | 2016-03-30 15:08 | [11 empty] | Durbin, Michael EMR SYSS PWS PITT | 2016-03-30 15:08 |  |  |  | 2016-03-30 15:08 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-02-04 04:14 |  | As per SRF#2227, In the case of a data-link point, this is the value (value at&nbsp; BIT3 of 2W status word) that is currently being received from the end device. While testing this functionality, it has been observed that value at <strong>BIT3 of 2W status word</strong> (Point value from I/O Scan) of <strong>Digital data-link points (LD &amp; DD point records),</strong> never updates as per the actual value of the point While Scan is ON. Please check the attached snapshots. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab, Ov3.6.0, Net26, DBS220, Drop24/74 (OCR400), SCADA2.5.0 |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>This is not a Point Information Issue.&nbsp; Point Information simply displays the value of 2W.&nbsp; This is a controller issue specifically with respect to the data links.</p><p><br></p><p>ST(02/10/2016): Configured some&nbsp;data link digital&nbsp;input and output points using ELC1.3 (Controller Drop 24/74, OCR400)&nbsp;of MODBUS protocol. Value at BIT3 of 2W status word of&nbsp;digital data link input&nbsp;points (configured using ELC1.3)&nbsp;is updating as per the actual value of point, but same is not working for digital data link output points. However data link points configured using SCADA2.5.0 is still behaving as described in Description tab of this finding.</p><p><br></p><p><br></p><p>SRF2227 only applies to input points.</p><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <br>1. Configured digital hardware data-link points of LD and DD point record type from configuration studio using SCADA configuration tool for some Modbus addresses.<br>2. loaded the configuration as required.<br>3. Simulated values to these points from Modbus slave device, and value of the points getting updated according to the actual value at Modbus address of the end device.<br>4. But value at BIT3 of 2W status word of these data link points never updates as per the actual value of point while scan is ON. |  | U3 |  |  | FINDING | [6 empty] | 94112
35614 | FINDING | XML files are not copied to module for hardware addresses that include letters. | Brown, Rick P EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2016-04-06 08:21 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-04-06 08:21 |  |  |  | 2016-04-06 08:21 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-02-04 09:32 |  | SCB-04/06/2016:&nbsp; Does not occur in OVA351.&nbsp; Closing. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Saxena, Pratishtha EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 94492
35615 | FINDING | Qt plug-in platform missing which prevents online help from appearing. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:18 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:18 |  |  |  | 2016-04-26 15:18 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-02-04 09:49 |  | LC 02/04/2016:&nbsp; Tried to access online help for the Control Builder, algorithms, and Controller Diagnostics.&nbsp; Help does not appear. Instead, I got the message, &quot;This application failed to start because it could not find or load the Qt platform plugin windows.&quot; This is in the 3.6.0 U3 build. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Documentation |  | Help now appears but displays incorrect topic&nbsp; (Findings 36262,36263) | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 build |  |  | FINDING | [6 empty] | 95744
35616 | FINDING | Online help does not appear for System Registration utility | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-05-25 06:50 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-05-25 06:50 | 64758 |  |  | 2016-05-25 06:50 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-02-04 09:51 |  | LC 02/04/2016: Tried to access online help for SRU application, and it did not appear. This is in the 3.6.0 U3 build. Engineer has been advised. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | <p>2016-04-19 RStaab: Help topic IDs got out of sync. This has been corrected and the help file should now open correctly.</p><p>TN:05/25/16-Confiremed the issue is fixed. Veriffied &amp; tested in both DBS drops of NET26 &amp; Net36.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | N, Thamaraiselvi AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Documentation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 build |  |  | FINDING | [6 empty] | 97701
35619 | FINDING | Alarm Application is unable to display points configured in units other than Unit0 for local network. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-26 14:05 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-26 14:05 | 66178 |  |  | 2016-04-26 14:05 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-02-05 09:28 |  | <p>Alarm Application does not display points configured in Unit1 in alarm window. The application also does not allow to filter out alarms in Unit1.</p><p>Please find the remote login details below.</p><p><br></p><p>Remote Login Details for Drop125:</p><p>IP address : 172.16.136.125<br>Domain: Val1Dc8<br>User name: Administrator<br>Password: Ovation1</p> |  |  |  |  | 0 |  |  |  | TK 26-April-2016 :&nbsp;Alarm Application displays the points&nbsp;configured in Unit1. The issue is fixed,hence closing this finding. | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  | Ovation 360 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1) Configure alarm points in Unit 1. </p><p>2) Open Alarm application.</p><p>3) Navigate to Filter tab &gt; Network/Unit .</p><p>4) Select Local Network (eg. Emily ).</p><p>5) Click on '+'.</p><p>Observation:&nbsp; Only Unit0 is displayed. Blank is displayed in place of Unit1.&nbsp;Alarms for points configured in Unit0 are displayed.</p><p><br></p><p>Please find the screenshot attached.</p> |  | U3 |  |  | FINDING | [6 empty] | 95719
35630 | FINDING | Alarm guidance window is showing wrong ovation version. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:50 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:50 | 66221 |  |  | 2016-03-15 00:50 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-09 03:29 |  | The Ovation version displaying on alarm guidance window about Tab is 3.5.2 instead of 3.6.0. |  |  |  | <p>This affects the Alarm Guidance and the Alert Details Windows.&nbsp; They both had the wrong version number.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  | <p>Ovation 3.6.0_U3</p><p>OS WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that alarm guidance window is displaying the Ovation&nbsp;version as 3.6.0. Hence this finding is&nbsp;closed by validation. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the alarm guidance window and verify its version.</p><p>Screenshot is also attached for your reference.</p> |  | U3 |  |  | FINDING | [6 empty] | 93332
35635 | FINDING | archivelog.bat fails in 3.6.0. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-20 13:19 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-20 13:19 | 3.6.0_U4 |  |  | 2016-05-20 13:19 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-02-09 15:54 |  | <p>As directed in SBR manual for Database Servers, the archivelog.bat file fails.&nbsp; See attachment. </p><p><br></p><p>MP 5/16/16 - archivelog.bat continues to fail, but with different failure.&nbsp; See attachment archivelog2.png</p> |  |  |  | The affected area is in the FindOraHome.vbs script's reference to the Oracle registry items.&nbsp; No specific test recommendations other than what would be considered to be obvious. | 0 |  |  |  | The original problem with findOraHome.vbs has been verified to be fixed.&nbsp; This finding will be closed.&nbsp; A new finding will be written against SBR 2.0 in regard to the new issue.&nbsp; SBR installs a version of archivelog.bat. | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0_U4 |  | <p>Ovation 3.6.0 U3</p> |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | One of the scripts used by the archivelog.bat file is FindOraHome.vbs.&nbsp; This script contains incorrect references to Oracle 12c registry entries.&nbsp; The FindOraHome.vbs script will be corrected. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Run c:\ovation\ovationbase\archivelog.bat |  | U3 |  |  | FINDING | [6 empty] | 97379
35636 | FINDING | Ov3.6.0: Graphics Application does not open - WesDialog.dll missing | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-16 12:38 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-16 12:38 |  |  |  | 2016-02-16 12:38 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-09 16:07 |  | <p>In Ov-3.6.0_U3 Operator Stations, on clients (W7, Ws12R2) of Lumension AV , it observed on some drops that after a scheduled daily Scan is run, <span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Ovation Graphics application does not open &amp; displays error:</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">&nbsp;&nbsp;&nbsp; graphics.exe - System Error</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; The program can't start because WesDialogs.dll is missing from your computer</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Attempts to reproduce, by scheduling scans, may or may not succeed to delete the file.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">It is observed on one drop that the file was deleted during a manual reboot, 2 hours after the scan.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">A popup error during startup with a related message was observed, but&nbsp;disappeared too fast to record it.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">No trace of the error message was found in any of the Event viewer or Ovation Error logs.</font>&nbsp;</span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">The Ovation errors &amp; scan logs do not list the deletion or flag the file.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Lumension claims that the deletion is not related to the AV, though it only happens on LAV Clients.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Other LAV clients on older Ovation levels, and the same clients prior to loading Ov-3.6.0_U3, did not show this problem.</font></span></p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> <p><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">Systems &amp; Clients are under observation for recurring events.</font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Foose, David A AUTOSOL PWS PITT | Kristopher Cummings | Joshi, Parmesh EMR SYSS PWS NOIDA | Spillane, Donal AUTOSOL PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | Saxena, Pratishtha EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | msb - 2/16/2016 - Closed Finding: converted to SDR 35692 against LAV.8.2 | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri><font color="#000000">Steps of observations:</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="FONT-SIZE:12pt;"><font color="#000000" face=Calibri>&nbsp;</font></span></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font color="#000000"><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>1.</font></span><span lang=EN-IN style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>Schedule the recurring scan from LAV server (LEMSS 8.2 or LAV 8.2) and observe the workstations .</font></span></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font color="#000000"><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>2.</font></span><span lang=EN-IN style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>The dll file mentioned in the attachment is deleted from C:\Ovation\OvationBase after scanning.</font></span></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font color="#000000"><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>3.</font></span><span lang=EN-IN style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>The LAV client window is not showing any message related to Virus/Quarantine in the dll file.</font></span></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font color="#000000"><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>4.</font></span><span lang=EN-IN style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span lang=EN-IN style="FONT-SIZE:12pt;"><font face=Calibri>After copying back the dll file to location&nbsp; C:\Ovation\OvationBase, the Ovation Graphics application opening.</font></span></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="FONT-SIZE:12pt;"><font color="#000000" face=Calibri>&nbsp;</font></span></p> |  | U3 |  |  | FINDING | [6 empty] | 92339
35638 | FINDING | Point information Apply point name feature is not working when user paste a copied point on point name field. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-24 07:54 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-24 07:54 |  |  |  | 2016-02-24 07:54 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-10 05:21 |  | Point information <strong>Apply point name</strong> feature&nbsp; is not working when user paste a copied point on <strong>point name</strong> field under home tab. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U3 |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | No plans to fix | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Copy a point first.</p><p>2)Open the point information application.</p><p>3)Paste the copied point on point name option under home tab.</p><p>4)Now try to click on Apply point name button.</p><p>Apply point name button is grayed out. But if user manually enters the point name then this feature is working fine. Screenshot is also attached for your reference.</p> |  | U3 |  |  | FINDING | [6 empty] | 92681
35656 | FINDING | Parameter modifications done in MHM configurations require a clear and load of the controller to come into effect while calculating measurement values | Brown, Rick P EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Rick P EMR SYSS PWS PITT | 2016-07-23 11:45 | [11 empty] | Brown, Rick P EMR SYSS PWS PITT | 2016-07-23 11:45 | Patch 68/20Apr16 |  |  | 2016-07-23 11:45 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-02-10 15:24 |  | <p>In Ov 3.6.0, MHM module, Thrust measurement values are calculated correctly as per the given sensitivity S1. </p><p>But if we modify the sensitivity value to S2&nbsp;in the configuration tool and load the controller, the calculated results displayed&nbsp;are the value as per the last sensitivity S1&nbsp;and does not take into account the modified sensitivity S2.</p><p><br></p><p>The measurement values are calculated correctly with S2 only after we perform a clear and load on that controller.</p><p><br></p><p>ELG: There is a missing step to change the configuration on the channel by sending a new XML file. Assigned to Bob to him to reroute.</p> | Modified the EP driver. |  |  | Rerun the same tests. | 0 |  |  |  | MHM is not a part of the initial 3.6 release.&nbsp; It will be in a feature pack.&nbsp; Note that this works in 3.5.1 from which the feature pack will be derived. | 0 |  | Ovation for Windows/Controller/MHM/Software | <p>Wrote a standard function to determine when a configuration file is associated with a particular module.&nbsp; This is now used when determining if the&nbsp; load caused a change, and by the download thread.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Ov 3.6.0, Drop125 ( DBS Emily network), Controller drop2/52, MHM module in Branch 2, Slot1. |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>Assigned back to&nbsp;Rick Brown based on:</p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">We repeated a modification of the sensitivity this morning.&nbsp; </span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">The Ovation Developer Studio updated the XML file on the server.&nbsp; The incremental load put the modified XML file on the controller (new timestamp on controller).&nbsp; We then logged in to the module and saw that the XML file was not updated there.&nbsp; The incremental load of the controller did not push the XML file to the module.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p>PRS, 11 apr 2016: recreated in OV 3.5.1 also. <span class=info-text>Parameter modifications done in MHM configurations require a clear and load of the controller to come into effect while calculating measurement values. Changing release to OV 3.5.1.</span></p><p><span class=info-text><br></span></p><span class=info-text><p><span class=info-text>PRS, 9 May 2016: Finding fixed for Ov 3.5.1 in <span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">OVA351-068-05022016070057 patch.Thanks</span> .</span></p><p><span class=info-text>As this finding was initially reported for Ov3.6.0, changing its product version&nbsp;back to Ov 3.6.0 and State to Open-MIS to track with that release.</span></p></span> | 14 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps are:</p><p>- Configure Thrust measurement in channel 1&nbsp;with Sensitivity 406.40, range -2 to -18Volts.</p><p>- Load the controller. Display configured Thrust SMV point&nbsp;in Point Information.</p><p>- Give the DC input signal between -2 to -18 volts and record the result for different values. These are correct.</p><p>- Modify the value of sensitivity to 203.20. Load the controller.</p><p>- Give the DC input signal between -2 to -18 volts and record the result for previously measured input&nbsp;values. Results are the same as calculated with the 406.40 Sensitivity. They are not being calculated with now configured 203.20 Sensitivity.</p><p>- Clear and Load the Controller.</p><p>- Give the DC input signal between -2 to -18 volts and record the result for previously measured input&nbsp;values. These are now calculated correctly with 203.20 Sensitivity.</p><p><br></p> |  | U4 |  |  | FINDING | [6 empty] | 100119
35658 | FINDING | Description of a point is overlapping the algorithm on signal diagram. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-06 04:48 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-06 04:48 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-11 00:26 |  | Description of a point is overlapping the algorithm on signal diagram. |  |  |  |  | 0 |  |  |  | LB 05/06/16 -When user assigns any point on control&nbsp;sheets&nbsp;it automatically takes&nbsp;the description of point. I have attached two documents one is SIS control sheet and other one is screenshot of same sheet on signal diagram. If you open the sheet on control builder every thing looks fine but if you view the same sheet on signal diagram then description of points overlaps and crosses the sheet. | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U3</p><p>OS- WS12,WIN 64 BIT</p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Open the control sheet in the editor.</p><p>Does it look correct?</p><p>Is the editor connected to the database (Database icon in the bottom left corner)?</p><p>Save the sheet.</p><p>Load the controller.</p><p>Open the sheet in the signal diagram viewer.</p><p>Does it look right?</p><p>LB 03/10/16-Please find my comments below.</p><p>Open the control sheet in the editor. <strong>Opened the sheet on Control builder.</strong></p><p>Does it look correct?&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;<strong> Yes ,it was correct description of point&nbsp;was not overlapping the algorithm.</strong></p><p>Is the editor connected to the database (Database icon in the bottom left corner)? <strong>Yes, sheet&nbsp;was made on DBS drop.</strong></p><p>Save the sheet. <strong>Saved the sheet.</strong></p><p>Load the controller. <strong>Loaded the sheet.</strong></p><p>Open the sheet in the signal diagram viewer . <strong>Opened the sheet on signal diagram.</strong></p><p>Does it look right? <strong>No, description of point is overlapping the algorithm, but when we open the same sheet&nbsp;on control builder every thing looks fine.</strong></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Create a control sheet add some algorithms and&nbsp;LA,LD points&nbsp;with ED field 50 characters, EU,RS,ST field 12 characters or you can use the attached control sheet load it and monitor it on signal diagram.</p><p>2)Load the control sheet and open it on signal diagram.</p><p>3)Verify the description of a point and algorithm on signal diagram. The description appears to overlap the algorithm.</p><p>Screenshot and control sheet is also attached for your reference.</p><p><br></p> |  | U3 |  |  | FINDING | [6 empty] | 96355
35670 | FINDING | System Viewer: Add controller diagnostics button | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 12:31 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 12:31 | 66079 |  |  | 2016-04-18 12:31 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-12 07:45 |  | <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">In System Viewer, there should be a controller diagnostics button on the main form that will launch the controller diagnostics program</font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">--</font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">msb - OK in U6</font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"></font></span>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software | <p>msb - 3/23/2016 &gt; [<font color="#000000" size=3 face=Calibri>controller diagnostics] button is not present on the System Viewer Main Screen in Ov-3.6.0_U4&nbsp;</font></p> <p><font color="#000000" size=3 face=Calibri>---</font></p> <p><font color="#000000" size=3 face=Calibri>msb - 4/18/2016 -&nbsp;<font color="#1e1e1e" size=2 face="Segoe UI"> [</font><font color="#000000" size=3 face=Calibri>controller diagnostics] button is the System Viewer Main Screen in Ov-3.6.0_U6&nbsp;</font></font></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U4 |  |  |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U4 |  |  | FINDING | [6 empty] | 95150
35671 | FINDING | OSR reports in the log file errors while reading the new Licenses from the new License Manager | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 14:49 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 14:49 | 67053 |  |  | 2016-04-18 14:49 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-12 08:06 |  | <p>OSR reports in the log file errors while&nbsp;reading the new Licenses from the new License Manager:</p> <p>&nbsp;</p> <p><font color="#000000" size=3 face=Calibri>02/12/2016 08:06:52&nbsp;Info&nbsp;Retrieving licensing information...<br>02/12/2016 08:06:52&nbsp;Info&nbsp;Licensing information retrieval complete.<br>02/12/2016 08:06:52&nbsp;Error&nbsp;A problem occurred retrieving network licensing information. VLSgetFeatureInfo failed for feature 10, ret = 0x0000000B<br>02/12/2016 08:06:52&nbsp;Error&nbsp;A problem occurred retrieving network licensing information. VLSgetFeatureInfo failed for feature 11, ret = 0x0000000B<br>02/12/2016 08:06:52&nbsp;Error&nbsp;A problem occurred retrieving network licensing information. VLSgetFeatureInfo failed for feature 12, ret = 0x0000000B<br>02/12/2016 08:06:52&nbsp;Error&nbsp;A problem occurred retrieving network licensing information. VLSgetFeatureInfo failed for feature 13, ret = 0x0000000B</font></p> <p>....</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>msb - 04/18/2016 - In Ov-3.6.0_U6 -</p> <p>The Network Licenses installed on the DBS are reported correctly:</p> <p>&nbsp;&nbsp;&nbsp; Ex.&nbsp;&nbsp; Controllers (Feature=10), Type: Normal, Number of licenses: 20</p> <p>The Standalone OPC&nbsp;licenses installed on Opstations are incorrect&nbsp;&nbsp; (Finding 34811)</p> <p>&nbsp;&nbsp;&nbsp; Ex. A problem occurred retrieving OPC_EVENT_SERVER standalone licensing information on DROP149. VLScg_Initialize failed, ret = 0xFFFFFFFF</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 95153
35677 | FINDING | OSR SRU Ov.3.6.0 - Installer displays .NET 2.0 error on PC with no .NET | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 14:39 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 14:39 | 66845 |  |  | 2016-04-18 14:39 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-02-12 13:54 |  | <p>OSR SRU Ov.3.6.0 - Installer&nbsp;displays .NET 2.0 error on PC with no .NET</p> <p>---</p> <p>Using the SRU from the Ov-3.6.0_U3 DVD to install SRU on a non-Ovation (KAVMgr PC) with no pre-installed&nbsp;.NET, </p> <p>the installer displays:</p> <p>----</p> <p>&nbsp; Error:</p> <p>&nbsp;&nbsp; An error occured running the .NET Framewark 2.0 install (error=2).</p> <p>&nbsp;&nbsp; It is likely that a newer verion of the .NET frameork is installed...</p> <p>----</p> <p>&nbsp;&nbsp; See attached jpg</p> <p>&nbsp;</p> <p>When installer is continued, it proceeds to install 'OvSysReg&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;1.40.0000' without the .NET.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>msb - 4/18/2016 - Ok with SRU on Ov-3.6.0_U6 -&nbsp;SRU installs:</p> <p>&nbsp; a. .NET Framework 4.5.1</p> <p>&nbsp; b. Ovation System Registration Utility&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1.50.0000</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 95152
35680 | FINDING | Fieldbus port download does not work in U3 | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Wood, Thomas T AUTOSOL PWS PITT | 2016-03-29 11:40 | [11 empty] | Wood, Thomas T AUTOSOL PWS PITT | 2016-03-29 11:40 | 66484 |  |  | 2016-03-29 11:40 |  |  |  | Wood, Thomas T AUTOSOL PWS PITT | 2016-02-15 10:12 |  | <p>After the 3.6 system was updated to U3 fieldbus functionality was tested and found that it was still not functional. </p><p>The download of the latest firmware was successful but attempting to download the ports produced errors as shown in the attachment.&nbsp;</p> |  |  |  | <p>After upgrading to U4, check the system to ensure that the Firewall is turned on.</p><p>Then try a Fieldbus Task.&nbsp; View Live List is the fastest test I can think of off hand.</p><p>If it succeeds, the other Fieldbus Tasks should as well.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U4 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  | IC 3/1/16&gt; re-assigned to Gil. | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 93984
35693 | FINDING | LA point can not be assigned for Reverse Rotor SMV of Tachometer measurement in MHM configuration tool. | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-17 06:15 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-17 06:15 | 3.6.0 U4 |  |  | 2016-03-17 06:15 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-02-16 12:50 |  | In Ovation MHM UI when we drag and drop any LA point to Reverse Rotor SMV of Tachometer measurement, &nbsp;applying the changes give error message stating &quot;UpdateObject Failed&quot;.&nbsp; Please refer the attached snapshot for the detailed error message. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0 U4 |  | <span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Ov 3.6.0, Drop125 ( DBS Emily network), Controller drop2/52, MHM module in Branch 2, Slot1.Channel 7, Tachometer measurement.</span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>Fixed in source code. - Sunil</p><p>PRS&nbsp;17 Mar 2016: Fixed in Ov 3.6.0_U4. Thanks. Closing the Finding</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Steps are:</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Configure Tachometer measurement in channel 7.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Check the RPM measurement and assign&nbsp; any LA point to this smv. Apply configuration and load the controller.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- RPM calculations can be seen in Point Information.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">-&nbsp;Check the Reverse Rotor measurement and assign any LA point to this SMV. Apply configuration.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Error message is displayed saying UpdateObject failed. It will not let the Reverse Rotor smv assigned.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman"><br></font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Please refer the attched snapshot for complete errpr message.</font></span></p> |  | U3 |  |  | FINDING | [6 empty] | 93469
35718 | FINDING | Plugging in more than one MHM module in a controller breaks the communication of previously running MHM module. | Brown, Rick P EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Rick P EMR SYSS PWS PITT | 2016-07-23 11:12 | [11 empty] | Brown, Rick P EMR SYSS PWS PITT | 2016-07-23 11:12 |  |  |  | 2016-07-23 11:12 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-02-18 15:51 |  | <p>Controller drop2/52 has branch 1 and Branch 2&nbsp;configured with MHM modules in all the slots. But measurements are defined only&nbsp;for MHM module in Branch 2&gt; slot 1&nbsp;and it is functioning properly. </p><p>Configured&nbsp;measurements in another MHM at Branch2&gt;Slot6 and loaded the controller. As soon as&nbsp;another MHM is plugged in,&nbsp;the previously functioning Module at&nbsp;branch2&gt;Slot6 stop communicating with the controller, its communication LED&nbsp;goes low and all the associated RM and LA points go into Sensor alarm.&nbsp;</p><p>&nbsp;&nbsp; (Associated RM point&gt;A2 field&gt; Bit15&nbsp;goes high for channel error detection.)&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Ov 3.6.0, Drop125 ( DBS Emily network), Controller drop2/52, previously configured MHM module in Branch 2, Slot1. New MHM module plugged in Branch2&gt;Slot6.</span> |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>PRS, 4 apr 2016: Issue is not present in OV3.5.1. </p><p>Configured and inserted two MHM modules in&nbsp;DROP 8/58 in GEC.&nbsp;Both modules have their respective&nbsp;communication LED green&nbsp;and do not put any assigned SMV points in sensor alarm.</p><p><br></p><p>Thanks for the update. I have often suspected that the MHM software in 3.6 is old, as several of the findings written for 3.6 are old problems that were fixed for MHM beta.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps are:</p><p>- Configure MHM module in Branch2&gt;Slot1. Insert the module.</p><p>- configure measurements in this and load the controller. MHM module is calculating measurement values.</p><p>- Configure one more MHm module in branch2&gt;slot6.</p><p>- configure measurements in this and load the controller.</p><p>- &nbsp;Insert the module.</p><p>As soon as&nbsp;another MHM is plugged in,&nbsp;the previously functioning Module at&nbsp;branch2&gt;Slot6 stop communicating with the controller, its communication LED&nbsp;goes low and all the associated RM and LA points go into Sensor alarm.&nbsp;</p><p>&nbsp;&nbsp; (Associated RM point&gt;A2 field&gt; Bit15&nbsp;goes high for channel error detection.)&nbsp;</p><p><br></p> |  | U3 |  |  | FINDING | [6 empty] | 100118
35720 | FINDING | Test case 13 of TR “3.6.0_WIN_OPCON_SVTP_rev2.I_RS.doc“ is not applicable in Ovation 3.6.0 | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-02-22 10:29 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-02-22 10:29 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-02-19 04:32 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Test case 13: Ovation Control Logic Navigation&nbsp;of TR “3.6.0_WIN_OPCON_SVTP_rev2.I_RS.doc“ is not applicable in Ovation 3.6.0.</span></font></font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ovation 3.6.0 + U3</span></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><br></p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">As CLN functionality is not<span style="">&nbsp; </span>to be supported in Ovation 3.6.0 (please refer F#34810) hence the <a name=_Toc70297668></a><a name=_Toc426370702><span style="">TEST CASE 13 : Ovation Control Logic Navigation</span></a> is not applicable in Ovation 3.6.0.</span></p><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p> |  | U3 |  |  | FINDING | [6 empty] | 92555
35737 | FINDING | Ovation Developer Studio getting crashed while loading SIS Logic Solver with Runtime error | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:07 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-16 00:07 | 66567 |  |  | 2016-03-16 00:07 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-02-23 00:14 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Ovation Developer Studio is getting crashed while loading SIS Logic Solver. We can perform download, clear &amp; Load operation on Legacy SIS controller (27/77).</span><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Please find attached snapshot “Studio_crashed.jpg”, “SIS_dignstics.jpg” &amp; “SIS_dignstics1.jpg”.</span><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Note:&nbsp;This is net#36, having Legacy SIS (Legacy SIS configured on Drop27/77) &amp; SIS CHARMS (SIS CHARMS configured on Drop30/80) under Unit0.</span></p><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PP:03/16/2016-Veryfied in Ov3.6.0_U4&nbsp;of (Ws12R2, W764B) and&nbsp;observed the Ovation Developer Studio did not crashed while loading the SIS logic solver. </span></span></p><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Hence Finding is closed.</span></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | U4 |  | OV3.6.0_U3,DBS drop100 (192.168.36.100) WS12R2,Leagacy SIS controller 27/77 (OCR400,Processor G02,IOIC G02) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configured the “SIS Networks” as well as “SISNet Rings” under “SIS-System” of Network level. </span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configured the “Ovation SIS” driver &amp; <span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Performed Download, Clear &amp; Load operation on drop27/77</span></span>. </span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configured the SDS01 &amp; Logic Solvers in SIS controller 27/77(192.168.36.27/77).</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Created the node points for SDS01, all configured logic solvers &amp; all configured Control Modules.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Load operation on drop27/77</span>.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:10pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">While load the Logic Solver, the Ovation Developer Studio gets crashed.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:10pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"></span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Note: We are able to Ping SIS Switch &amp; SDS. </span></p></li></ol><font face="Times New Roman" size=3> </font> |  | U3 |  |  | FINDING | [6 empty] | 93408
35738 | FINDING | VxWorks.sym file keep appearing as download reguired even if it has been downloaded multiple time | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-15 04:17 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-15 04:17 | 66839 |  |  | 2016-04-15 01:54 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-02-23 02:17 |  | VxWorks.sym file&nbsp;of&nbsp;Field bus module&nbsp;keep appearing as download required even if it has been downloaded multiple times |  |  |  |  | 0 |  |  |  | <p><span class=info-text><br></span></p><p><span class=info-text>MS : Checked in U6 &quot;VxWorks.sym&quot; file is no longer available.&nbsp; Hence I am closing this finding</span></p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Plymire, Alvan AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U5 |  | Field bus module with Ovation 3.6.0_U3 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>Also noted in FINDING 34968:<span class=info-text> - Fieldbus module download causes module to be inoperative.&nbsp; Will be corrected in U4.&nbsp; This file is an extraneous file that should not be in the release.</span></p><p><span class=info-text><br></span></p> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Configure the field bus module at 1.2.3 in drop36/86 (OCR 1100).</p><p>2. Load the drop36/86.</p><p>3. Opened controller&nbsp;diagnostic&nbsp; (from Start menu &gt; Ovation &gt; Utilities)</p><p>4.&nbsp; Select drop36/86 from controller list&nbsp;and go to I/O information tab</p><p>5. Expand drop36/86 to&nbsp;select&nbsp;field bus module at 1.2.3</p><p>6.&nbsp;Click &quot;Download Available Firmware &quot;&nbsp;</p><p>7. Download all the required&nbsp;files</p><p>8. Reseated Field bus module &amp; perfomed step 5 and 6</p><p>&nbsp;&nbsp; it&nbsp;is observed that vxWorks.sym file came up for firmware download again&nbsp;even if it was downloaded earlier&nbsp;</p><p>&nbsp; (please refer attached snapshot )&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p> |  | U3 |  |  | FINDING | [6 empty] | 95023
35741 | FINDING | Online help not working for Controller Diagnostics - Qt problem | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-25 01:54 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-25 01:54 | 67696 |  |  | 2016-05-25 01:54 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-02-23 08:44 |  | LC 02/23/2016: Online help for Controller Diagnostics does not work in Ovation 3.6 U3 build. This is a problem with Qt. Please consult Steve Hutchison for fix. |  |  |  | Open Controller Diagnostics. Confirm no errors are displayed before the main Diagnostics window is displayed. Click Help-&gt;&quot;Contents and Index&quot;. Confirm help starts with no errors. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software | Fixed missing Controller Diagnostic help files, CHM path was wrong in build.bat. Pointed help at the working assistant.exe in CtrlBldr instead of the broken one in OvationBase. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Goyal, Ashish EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Documentation |  | <p>Help is now functioning properly.</p> <p>&nbsp;</p> <p>ASG May 25 2016&gt; Closing the finding after&nbsp;confirming&nbsp;that no errors are displayed before the main Diagnostics window is displayed and Help window opens without any errors for any of the tab except as reported in Finding#36602. Verification done on Ov3.6.0_U9 build</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U3 build |  |  | FINDING | [6 empty] | 97668
35749 | FINDING | Ov3.6.0_U3 Alarm Check Remove\ Shelve Comment field is not saved over reboot of Controller (reboot both the controllers if redundant), Virtual Controller, EWS drops after performing Alarm Check OFF | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-24 10:18 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-24 10:18 |  |  |  | 2016-02-24 10:18 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-02-24 05:35 |  | <p>Alarm Check Remove\ Shelve Comment (RE) field is not saved over reboot of controller, virtual controller, workstation as it is designed to be saved over reboot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | <p>Win7, 64 Bit + Ov3.6.0</p><p>Windows Server 2012 R2 + Ov3.6.0</p> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>I tried this with a digital point that was originated by an operator Station.&nbsp; I put the point in alarm and then alarm check removed it with a comment.&nbsp; I rebooted the originating drop and when it came back up, the comment and timestamp fields were maintained. Was the point originated on an operator station, controller or virtual controller?&nbsp; What was the point type?&nbsp; Please retest with points originated from an operator station, virtual controller, and a controller and let me know the results of each test.</p><p><br></p><p>Works as designed - Things are not synced to flash immediately.&nbsp; It&nbsp;may take up to 5 minutes to write the data to flash.&nbsp;</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.Open any point in Point Information window.</p><p>2.Take the point into alarm.</p><p>3.Perform Alarm Check OFF enter the comment and click OK.</p><p>4.Go to Alarm tab of Point Information window and verify the comments are present&nbsp;at the RE field.</p><p>5.Reboot controller(Reboot both controllers if redundant), virtual controller, workstation where the point is created/ originated.</p><p>6.Wait for the drop to come back online and observe the RE field of the point.</p><p>7.Comments which were entered are no more available on RE field.</p><p><br></p> |  | U3 |  |  | FINDING | [6 empty] | 92685
35752 | FINDING | Virtual CSLS Mac Ids are being displayed as Unassigned in the View Live Devices List for Hardware CSLS configured on different Controller Drop. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-02-29 22:50 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-02-29 22:50 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-02-25 00:41 |  | <p>Virtual CSLS Mac Ids are being displayed as Unassigned in the View Live Devices List for Hardware CSLS configured on different Controller Drop on the same Network. This creates confusion for the user about the available devices while viewing the Live Devices List.</p> <p>Please see the attached screenshot as <em>Unassigned VCSLS Mac Id.png</em></p> <p><strong>Note:</strong></p> <p>a. Hardware CSLS Mac Ids is not displayed in Virtual CSLS Live Devices List.</p> <p>b. VCSLS Mac Ids are not listed while assignment of Hardware CSLS. Only valid Hardware CSLS Mac Ids are visible in the Assignment window.</p> <p><em></em>&nbsp;</p> <p>&nbsp;</p> <p><em></em>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U3 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"></span>&nbsp;</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Right click on <span style="FONT-SIZE:10pt;COLOR:black;"><font face=Calibri>Drop</font></span><span style="FONT-SIZE:10pt;FONT-FAMILY:Wingdings;COLOR:black;">à</span><span style="FONT-SIZE:10pt;COLOR:black;"><font face=Calibri> I/O Devices </font></span><span style="FONT-SIZE:10pt;FONT-FAMILY:Wingdings;COLOR:black;">à</span><span style="FONT-SIZE:10pt;COLOR:black;"><font face=Calibri> I/O Device 5 Ovation SIS CHARMs --&gt; Local Safety Network - LSN1</font></span><span style="COLOR:black;"></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000">2. Right click on View Live Devices List.</font></span></p> <p><font size=3 face=Calibri><span style="COLOR:#1f497d;"></span></font>&nbsp;</p> |  | U3 |  |  | FINDING | [6 empty] | 92831
35753 | FINDING | Anchor functionality is not working properly while selecting the algorithm symbol. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:35 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 00:35 | 66660 |  |  | 2016-03-15 00:35 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-02-25 03:00 |  | Anchor functionality is not working properly while selecting the algorithm symbol. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U3</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-03/15/16-Verified on Ovation3.6.0_U4 and observed that Anchor functionality is working properly while selecting the algorithm symbol. Hence this finding is&nbsp;closed by validation. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the developers studio.</p><p>2)Create a new control sheet or open an existing control sheet.</p><p>3)Go to file menu and select New&gt;algorithm symbol.</p><p>4)Draw the symbol for selected algorithm.</p><p>5)Select the algorithm symbol and verify the position of anchor.</p><p>Screenshot is also attached for your reference.</p> |  | U3 |  |  | FINDING | [6 empty] | 93330
35754 | FINDING | HART AO modules not communicating with device when using OCR400 controller | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-04 10:22 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-04 10:22 |  |  |  | 2016-04-04 10:22 |  |  |  | Wood, Thomas T AUTOSOL PWS PITT | 2016-02-25 07:00 |  | <p>Using OCR400 controllers AMS can not connect to a live device on the HART AO module and Valve Link can not see the device either. I also attempted to download firmware to the module using Controller Diagnostics and this also failed. All of these tasks could be successfully completed when OCR1100 controllers were used.</p><p><br></p><p>Are there any messages in the error log when you try to download firmware to&nbsp;the I/O module?<br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | GWS&gt; Sarah I talked with Tom. &nbsp;He described the main issue was that the firmware downloading was timing out and it took 3 or 4 tries to successfully download. &nbsp;Sounds like this may be the &quot;killcode&quot; issue. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Investigate After Release | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  | GWS&gt; &nbsp;This is a duplicate of SDR 35654, which is currently being validated (first on 3.3.1). &nbsp;When we are done testing, we will release for 3.6.0. &nbsp;The SDR 35654 has a placeholder RR for this issue on 3.6.0. | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 94348
35762 | FINDING | One of the unit name defined in the local network is not appearing in the Filter tab, Network section of the alarm window. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-26 07:05 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-02-26 07:05 |  |  |  | 2016-02-26 07:05 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-02-25 21:14 |  | Name one of the unit is not appearing in the Filter tab, network section of the alarm window. |  |  |  | This is the same as Finding 35619.&nbsp; It has already been addressed and should be tracked with the original Finding. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | <p>3.6.0_U3_Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>controller drop37/87 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>EWS drop153 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <p><br></p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1. Open the alarm window.<br>2. Go to the filter tab and click on the network/unit section of the filter tab.<br>3. Then click on the Local network of that drop.<br>4. Randomly one of the units of the local network will not be visible.<br> |  | U3 |  |  | FINDING | [6 empty] | 92752
35772 | FINDING | Test procedure 3..6.0_CB_SVTP_rev_2.8_RL.doc needs changes | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-03-18 13:55 | [11 empty] | USPITTFSService | 2016-03-18 13:55 | [7 empty] | Lal, Ramesh External | 2016-02-26 02:28 |  | Test case 5.5.20 of Test Procedure 3..6.0_CB_SVTP_rev_2.8_RL.doc should be removed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U3 |  |  | FINDING | [6 empty] | 93595
35776 | FINDING | Modified ELC Configuration file does not load to ELC module. | Plymire, Alvan AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jha, Rahul AUTOSOL PWS NOIDA | 2016-06-22 05:13 | [11 empty] | Jha, Rahul AUTOSOL PWS NOIDA | 2016-06-22 05:13 |  |  |  | 2016-06-22 05:13 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-02-26 05:41 |  | <p>It is observed that&nbsp;if&nbsp;ELC module&nbsp;is configured with ‘communicate via network’ option enabled then&nbsp;modified&nbsp;configuration file&nbsp;does not&nbsp;load to ELC module.</p><p><font face="Times New Roman" size=3> </font>However, if ELC is configured with ‘communication via network’ option unchecked then&nbsp;modified configuration&nbsp;gets loaded into ELC module.</p><p><br></p><p>Please refer attached ELC configuration '4880.xml'.</p><p><font face="Times New Roman" size=3> <br></font></p><p><font face="Times New Roman" size=3><br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U3 with ELC1.3.0 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | <p>RJ 06/22/2016- Retested this issue with Ovation.3.6.0 (final build U9) and ELC.1.3.0 on OCR1100 (Drop38/88). Used the same set up of hardware, port, and configuration files (where the issue was seen earlier). </p><p>It is observed that the&nbsp;issue cannot be recreated&nbsp;with Ovation.3.6.0_U9 + ELC.1.3.0. Hence,&nbsp;closing this finding.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Steps followed:</font></p><font face="Times New Roman" size=3> </font><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Configured ELC module at 1.2.1 in drop38/88 (OCR 1100) with&nbsp;<strong>‘communication via network’</strong> option unchecked.&nbsp;</p></li><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Configured Modbus Master protocol in PCT (Protocol configuration Tool) &amp; loaded the drop38/88.</p></li><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Modbus&nbsp;Calta Simulator used as a Slave &amp; established communication between ELC module &amp; Calta.</p></li><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Verified that Scan point&nbsp;values are interchanging with&nbsp;Modbus registers (in Calta).</p></li><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Confirmed that loaded configuration&nbsp;are reflected at Protocol Analyzer Tool.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Now, configured ELC with <strong>communicate via network option checked</strong> and loaded the controller.(Please refer attached snapshot 'ELC Module _Configuration.jpg')</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Made new modifications in&nbsp;PCT (e.g. added&nbsp;new point or changed the port number etc.).</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Now, loaded&nbsp;drop38/88 to update ELC with modified configuration.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">&nbsp;It is observed that the new changes are not working and also the changes were not&nbsp;seen at protocol analyzer.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">At this state, if ELC is rebooted from controller diagnostic then it kept on rebooting continuously.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">However, if ELC is again configured with <strong>‘communication via network’</strong> option unchecked and controller is loaded then this issue is resolved.</p></li></ol><font face="Times New Roman" size=3> </font> |  | U3 |  |  | FINDING | [6 empty] | 98921
35780 | FINDING | DBS+DC Drop encounters error if primary cable of OHI connection is not connected | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 09:04 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 09:04 |  |  |  | 2016-06-08 09:04 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-02-29 03:43 |  | While performing OHI Connection Failover recovery for NIC1 &amp; NIC2, DBS+DC Drop encounters error if Primary cable (OHI1) of OHI connection is not connected&nbsp; <br>A Reboot&nbsp; after disconnecting the Primary cable (OHI1) encounters an error .A blue screen is seen with message. “Your DBS ran into a problem and needs to restart. We’re just collecting some error info, and then we’ll restart for you. (0% complete). If you ‘d like to know more, you can search online later for this error: ATTEMPTED_EXECUTE_OF_NOEXECUTE_MEMORY ”<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | DBS+DC Drop220;<br>Net#26;<br>Ws12_R2;<br> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>IC 5/12/16 &gt; seen again at GEC with U7, SDR &amp; DIR.<br><br></p><p>IC 6/8/16&gt; closed finding, added to DIR, track as SDR 36738. </p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Verify both the NICs (OHI1 connected to Primary switch&nbsp;&amp; OHI2&nbsp; connected to&nbsp;Backup switch) are connected and DBS is in healthy state. </p><p>Now, <br>a&gt; Disconnect Primary cable (OHI1),&nbsp; Re-Connect Primary cable (OHI1)&nbsp; :&nbsp; Result OK<br>b&gt; Disconnect Secondary cable (OHI2),&nbsp; Re-Connect Secondary cable (OHI2) : Result OK<br>c&gt; Disconnect Both cable, Connect Both Cable : Result OK<br>d&gt; Disconnect Secondary cable (OHI2), Reboot, Re-Connect Secondary cable (OHI2) : Result OK<br>e&gt; Disconnect Primary cable (OHI1), Reboot : ERROR<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;A blue screen is seen with message. “Your DBS ran into a problem and needs to restart. We’re just collecting some error info, and then we’ll restart for you. (0%&nbsp; complete). If you ‘d like to know more, you can search online later for this error: ATTEMPTED_EXECUTE_OF_NOEXECUTE_MEMORY ”</p><p>The DBS reboots and reaches the login screen, here again DBS goes to the same blue error page as reported above. After&nbsp;the mentioned stage repeats&nbsp;twice, the DBS reboots to normal working condition.<br>PS: At any time the DBS reboots without the Primary NIC connected, “ATTEMPTED_EXECUTE_OF_NOEXECUTE_MEMORY” error occurs. </p><p>OHI1-disconnect on GEC DBS_DCdrop.jpeg attached for reference.</p> |  | U3 |  |  | FINDING | [6 empty] | 98401
35792 | FINDING | Test case 2 "SRF 1881 Controller Diagnostics and SRU" of SVTP "3.6.0_OV_and_SIS_CHARMS_SVTP_rev1.1_SHS.docx" needs to be modified | Gupta, Chandresh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:36 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:36 |  |  |  | 2016-03-18 13:47 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-02-29 22:42 |  | Test case 2 &quot;SRF 1881 Controller Diagnostics and SRU&quot; of SVTP &quot;3.6.0_OV_and_SIS_CHARMS_SVTP_rev1.1_SHS.docx&quot; &nbsp;needs to be modified.<div>Test case 2 contains Controller Diagnostics, but it needs to be replaced with SIS Diagnostics. Test case 5.2.1 is written for controller diagnostics but it should be SIS diagnostics as controller diagnostics does not support third party (SIS CHARMs in this case).</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>IC 3/29/16&gt; Shiva, please proceed with your testing per the changes you mentioned above. <br>Put your above mentioned notes in a Comments box in your TR and mention this Finding # as well. </p><p>The SVTP will be update in the future for the next release. </p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0 U3 |  |  | FINDING | [6 empty] | 108977
35793 | FINDING | Inconsistent behaviour observed during SIS CHARMs Network Interface Redundancy test | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-22 07:14 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-22 07:14 |  |  |  | 2016-05-22 07:14 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-01 00:40 |  | <p>Inconsistent behaviour observed during SIS CHARMs Network Interface Redundancy test. Please find below few observations:</p> <p><br>a. Bit#3, Bit#4 and Bit#13 of CSLS RN Point which indicates Not Registered, Communication Error and Communication Alert gets high for 10-15 sec when Primary Network Interface N1 port cable of Primary Controller Drop&nbsp;(In Control)&nbsp;&nbsp;is removed. CSLS gets Registered on it's own after 10-15 sec removing the communication error. Point Information shows status of SIS CHARMs points as 0003H.</p> <p><br>b. When we remove N1 or N4 port cable&nbsp;of any Controller Drop (Primary or Secondary) then following message appears in Error log which is expected:<br>&nbsp;&nbsp;&nbsp;&nbsp; <font face="Courier New">FRI FEB 26 08:45:19 2016 : &lt;133&gt; Interface Status : gei0[N1]: down<br></font>But when the cable is connected again and the Port comes up then along with the message of the port being up, following message also appears:<br>&nbsp;&nbsp;<font face="Courier New">&nbsp;&nbsp; <strong>FRI FEB 26 09:02:15 2016 : 0x7526158 (csLsnInbound): RtWarning in CtrlXface.cpp(1266): IO Buffer add failed - out of free buffers (status=0000000F)</strong><br>&nbsp;&nbsp;&nbsp;&nbsp; FRI FEB 26 09:02:15 2016 : &lt;133&gt; SISCHARM: Notice: Primary LSN interface gei0 is up</font></p> <p><br>c.&nbsp;Following messages of I/O Data Timeout have&nbsp;also been observed in Ovation Error log:<br><strong>&nbsp;&nbsp;<font face="Courier New"> &lt;Err dts=&quot;02/29/16 12:16:10&quot; dtl=&quot;1456728370&quot; source=&quot;drop100&quot; priority=&quot;1&quot; identifier=&quot;drop30&quot;&gt;0x74ce680 (csCslsDataMonito): RtWarning in RtcPioCslsNode.cpp(1508): decrementDataMonitorCounters() CSLS name D30-CSLS009, id 9, IO Data Timeout (status=00020013)&lt;/Err&gt;</font></strong></p> <p>But these messages appear mostly when there is no communication or a switchover is happening. So it seems expected in some cases while in some it's occurrence is unexplained.</p> <p>&nbsp;I/O Driver Timeout as configured in Developer Studio -- 10000 msec</p> <p>&nbsp;</p> <p>Please find attached:</p> <p>1. Historical Review data</p> <p>2. PrintErrorBuffer logs</p> <p>3. Ovation Error logs</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U3 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>More information required. Please provide:</p> <p>1. A screenshot of LSN configuration</p> <p>2. Config.sis, Config.dpu and Config.dl files from &quot;/ata0/wdpf/dpu/config&quot;</p> <p>3. hostinfo.1 file from &quot;/ata0/etc&quot;</p> <p>4. Network setup and switch information</p> <p>&nbsp;</p> <p>PA - 05/22/16 - Issue is no more observed. Hence closing the Finding.</p> <p>PA - 03/29/2016 - </p> <p>Please find attached the required information in the folder <em>Finding#35793-29032016.zip</em></p> <p><em><br></em></p> <p><em><br></em></p> <p>MZ&nbsp;- 03/29/2016 - </p> <p>Are the switch ports 1.1 and 1.2 uplink ports? If so - was it intended to connect them to controllers? That's probably why the connections on the sis links are 1Gbps. I don't know how controller behaves with such high-speed connectivity.</p> <p>&nbsp;</p> <p>PA - 03/30/2016 - </p> <p>Yes the switch ports 1.1 and 1.2 are uplink ports. They were connected to the Controller ports N1 and N4. Now we have changed the connections and connected the Controller ports N1 and N4&nbsp;to 2.1 and 2.2 respectively. We&nbsp;have kept the&nbsp;logs on monitoring now to check whether we again face the errors mentioned in the Finding.</p> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 97413
35803 | FINDING | NumaLogic RNCs do not successfully boot | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:31 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:31 | 67847 |  |  | 2016-06-07 13:31 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-03-01 11:47 |  | OCR400 Controller 43/93 (Timothy) is configured with multiple NumaLogic nodes.&nbsp; The RNCs do not complete the boot process.&nbsp; Ovation Error Log messages are attached.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software | <p>Numalogic nodes are now reminded of their IP address on boot via an ifconfig() call, based on the address in the boot params, which comes from bootp. VxWorks 6.9 normally ignores the IP address in the boot params if the DHCP flag is set.</p><p><br></p><p><br></p><font face=Arial size=3><p><br></p><p style="margin:0in 0in 0pt;line-height:normal;"><span style="color:black;"><br></span></p><p style="margin:0in 0in 0pt;line-height:normal;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 0pt;line-height:normal;"><br></p><p><font face="Times New Roman" size=3> <br></font></p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U8 |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>IC 6/1/16&gt; closed finding, track as SDR #36731. <br><br>IC 6/7/16&gt; Per SCB 5/25/16 email: </p><font face=Arial size=3><p style="margin:0in 0in 0pt;line-height:normal;">Regarding NumaLogic in U9.&nbsp; It still isn’t working.<font face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;line-height:normal;"><span style="color:black;">The RNCs are behaving differently, but they’re not reporting the correct states and there’s no communication.</span></p></font><p style="margin:0in 0in 0pt;line-height:normal;"><br>The Numalogic nodes now remember their IP address after boot.</p> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 98350
35806 | FINDING | Alarm check remove functionality is not working as per SRF2048 | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-19 22:17 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-19 22:17 | 66597 |  |  | 2016-04-19 22:17 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-03-01 21:16 |  | <p>When alarm check remove function is performed in alarm window the comment inserted are not visible in the corresponding alarm suppressed tab of the alarm window. This is observed for <strong>packed(LP), deluxe packed(DP), node(RN) and module(RM) </strong>points. </p><p>As per SRF2048 description when alarm suppressed operation is performed for any point, a 80 byte ASCII comment can be added for that point which is visible in the alarm suppressed tab of the alarm window. </p><p>However, when alarm check remove operation is performed for the same points through point information application, comments added during alarm check remove operation are visible in alarm suppressed tab of the alarm window.<br></p><font face="Times New Roman" size=3><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p><p> <br></p></font><p><font face="Times New Roman" size=3><br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U5 |  | <p>3.6.0_U3_Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Controller drop37/87 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;</p><p>Controller drop36/86 (OCR1100)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>EWS Drop111 (WS08 32-bit)</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a node point in developer studio.</p><p>2. Put that point in alarm so that it can be seen in alarm window.</p><p>3. Select that point in alarm window and click the alarm check off option in the alarm window.</p><p>4.&nbsp;A dialog box will appear for adding the comment for that point. write a comment.</p><p>5. Go to the alarm suppressed tab and find that point on which alarm check remove operation was performed.</p><p>6. The reason section of that point is empty.</p> |  | U3 |  |  | FINDING | [6 empty] | 95272
35810 | FINDING | An OCR1100 will not boot | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Durbin, Michael EMR SYSS PWS PITT | 2016-03-18 09:55 | [11 empty] | Durbin, Michael EMR SYSS PWS PITT | 2016-03-18 09:55 |  |  |  | 2016-03-18 09:55 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-03-02 08:41 |  | OCR1100 Controller 32/82 (Emily) has been undergoing continuous hardware reboots for four days.&nbsp; It is currently &quot;stuck&quot; and won't boot.&nbsp; Error messages are attached.<br> |  |  |  |  | 0 |  |  |  | IOIC hardware problem. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U3 |  |  | FINDING | [6 empty] | 93558
35813 | FINDING | SIS diagnostics tool is unable to detect SIS CHARMS, CSLS and CHARMS controller drop | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-23 03:23 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-23 03:23 |  |  |  | 2016-05-23 03:23 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-02 23:57 |  | SIS diagnostics tool is unable to detect SIS CHARMS, CSLS and CHARMS controller drop. |  |  |  |  | 0 |  |  |  | Issue has tested and found fixed in 3.6.0_U9. Still unable to get data for 16th CSLS for which finding F#36520 is present. | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  | Implementation | U7 |  | <span style="font-family:Calibri, sans-serif;font-size:14.6667px;">Windows 7-64 Bit + Ov3.6.0 U3</span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | The SIS Charm diagnostics functionality has been added. | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>SIS CHARMS is added in a Controller drop in network</li><li>Open SIS diagnostics tool on an EWS.</li><li>Unable browse the CHARMS controller drop, CSLS and SIS CHARMS.</li></ol> |  | U3 |  |  | FINDING | [6 empty] | 97451
35820 | FINDING | RSR Module : Unable to calibrate G06 module as per the steps mentioned in Section 3.2.2 of CON_047. | Shaw, Scott External Artech | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 11:01 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-03-30 11:01 | [7 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-03-04 07:31 |  | <p>When trying to&nbsp;access the Servo Drive module&nbsp;by connecting the user port of module to the COM port of PC , it generates a message &quot;C interp: syntax error&quot;</p><p>Typing HELP&lt;return&gt; at the prompt does not return the list of commands mentioned in manual.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Firmware/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0</p><p>Servo Drive Module (1C31199G06)</p> |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1) Connect a serial cable between the COM port and the user port on the Servo Driver.</p><p>2) Start Putty.exe </p><p>3) Connect serial port using settings </p><p>Baud Rate: 38400</p><p>Bits : 8 Bits</p><p>Stop Bits:&nbsp; One Stop bit</p><p>Parity: No Parity</p><p>4) Type HELP&lt;return&gt;</p><p>Observation: </p><blockquote style="margin-right:0px;" dir=ltr><p>help&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print this list<br>dbgHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print debugger help info<br>edrHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print ED&amp;R help info<br>ioHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print I/O utilities help info<br>nfsHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print nfs help info<br>netHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print network help info<br>rtpHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print process help info<br>spyHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print task histogrammer help info<br>timexHelp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print execution timer help info<br>h&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; [n]&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Print (or set) shell history<br>i&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; [task]&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Summary of tasks' TCBs<br>ti&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; task&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Complete info on TCB for task<br>sp&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; adr,args...&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Spawn a task, pri=100, opt=0x19, stk=20000<br>taskSpawn name,pri,opt,stk,adr,args... Spawn a task<br>tip&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;dev=device1#tag=tagStr1&quot;, &quot;dev=device2#tag=tagStr2&quot;, ...<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Connect to one or multiple serial lines<br>td&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; task&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Delete a task<br>ts&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; task&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Suspend a task<br>tr&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; task&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Resume a task</p><p>Type &lt;CR&gt; to continue, Q&lt;CR&gt; or q&lt;CR&gt; to stop: q&lt;CR&gt;</p></blockquote><p dir=ltr>As&nbsp; per manual , it should return Calibration Commands.</p><p><br></p> |  | U3 |  |  | FINDING | [6 empty] | 94085
35830 | FINDING | Moving MHM module configuration between slots of a drop in Studio doesnt configure the new hardware address in SMV points. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-01-17 00:24 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-01-17 00:24 |  |  |  | 2017-01-17 00:24 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-07 03:58 |  | <p>Moving MHM module configuration from one slot (slot1)of drop2/52 to another empty slot (Slot6) of that drop in Ovation developer studio&nbsp;do move the configuration and all the measurement parameters configured in Ovation MHM UI. However if any LA&nbsp;point is assigned to SMV of these measurement, then the hardware address for the slot1 keeps associated with it. Moving the configuration does not change its hardware address to that&nbsp;for slot6.</p> |  |  |  | <p>The affected area is in the software which identifies referenced points during a move operation of a hardware item.&nbsp; In this cases, specifically an Embedded Platform module (MHM or DGC).&nbsp; </p><p>Tests should include the following.</p><p>An Embedded Platform module to which multiple points have been assigned (including RM points, points assigned to hardware registered, and points assigned to pure SMV variables) should be moved in the Ovation Developer Studio from one branch/slot location to another.&nbsp; After the originated drop has been loaded, the hardware addresses of the applicable points should be inspected to confirm that they have been changed to values consistent with the new I/O location.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | [9 empty] | Implementation | 3.6.0_U4 |  | <span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Ov 3.6.0, Drop125 ( DBS Emily network), Controller drop2/52, previously configured MHM module in Branch 2, Slot1 and moved to&nbsp;Branch2,Slot6.</span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>The software which updates points assigned to moved hardware items has been changed to take into account Embedded Platform modules (MHM or DGC) which do not contain direct references back to SMV-only points.</p><p><br></p><p>prs, 11apr2016: This issue does not exist in OV3.5.1.</p><p>PRS 17 Jan 2017: Issue is fixed. Checked in Ov3.6.0FP1.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Steps are:</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Configure MHM module in Branch2&gt;Slot1. </font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- configure measurements in this and assign few LA points to the SMVs.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Load the controller.</font></span></p><font face="Times New Roman" size=3> </font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Move this MHM module configuration to Branch 2, Slot 6.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- Configuration is moved.&nbsp;Load the controller.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">- check the associated module hardware address of the points which are configured as SMVs.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Its still the hardware address for Branch2, slot 1 instead of Branch2, slot6.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">We need to touch the point and load controller for updating the hardware address.</font></span></p><font face="Times New Roman" size=3> </font> |  | U3 |  |  | FINDING | [6 empty] | 107743
35831 | FINDING | AMS 13.0 DM can't be installed if OSC components are already installed on same drop. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 07:08 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 07:08 |  |  |  | 2016-06-08 07:08 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-03-07 05:30 |  | <p>A note should be added in DIR that&nbsp;&nbsp;AMS 13.0 DM can't be installed if OSC&nbsp;components are already installed on same drop.</p><p>It will be required to un-install OSC components to install AMS13.0 DM (server or client).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <ol><li>WS12-R2 drop with OSC components installed.</li><li>AMS 13.0</li></ol> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.&nbsp;&nbsp;<font color="#1f497d" face=Calibri size=3>Install all OSC 3.3 components</font> <span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">( LAV,LDC,,LAC and LPR) in drop128 (WS12-R2)</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2. Ensure drop128 is in&nbsp;unsecured mode.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3. Now&nbsp;try to Install AMS DM 13.0 , errors of dll &amp; exe files will appear &amp; installation will fail.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">&nbsp;&nbsp;&nbsp;&nbsp; ( please refer attached snapshots )&nbsp;</span></p> |  | U3 |  |  | FINDING | [6 empty] | 98387
35836 | FINDING | “rt lsn comm msg timeout” message appeared instead of “LS_SLS_IS_LOCKED" if tried to load locked VCSLS(every time) and CSLS (sometime) | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-08 09:40 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-08 09:40 |  |  |  | 2016-03-08 09:40 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-03-08 05:25 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face="Times New Roman" size=3>“rt lsn comm msg timeout”</font></b><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"> message appeared instead of&nbsp; <b>“LS_SLS_IS_LOCKED&quot;,</b> If tried to Load Locked VCSLS. For VCSLS this message is coming every time and in CSLS its coming sometimes (Average once in 7 Load operation).</span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [5 empty] | Implementation |  |  | <p>Ovation 3.6.0 U3 + VCSLS+VCH machine&nbsp;Win 7 64 Bit + ORC1100 drop configured as Virtual Controller Drop.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p>This is the direct response from the CSLS.&nbsp; We do not decode or interpret the results.</p><p><br></p><p>No Plans To Fix.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">1. Lock the VCSLS and check the status of VCSLS lock operation in PI.</span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">2. Try to load this locked VCSLS. </span></p><font face="Times New Roman" size=3> </font><p><strong><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">3. “rt lsn comm msg timeout”</span></strong><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"> message appeared in every load operation for locked VCSLS.</span></p><font face="Times New Roman" size=3> </font><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;</span></p><font face="Times New Roman" size=3> </font><p><b style=""><u><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">NOTE:</span></u></b><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"> For Clear and Reboot operation <b style="">“LS_SLS_IS_LOCKED&quot;</b></span><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">appeared if VCSLS is locked.</span></p><font face="Times New Roman" size=3> </font> |  | U3 |  |  | FINDING | [6 empty] | 93064
35837 | FINDING | Inconsistency in different CHARM Class in Attribute tab for HART Errors column | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Swartz, Mark EMR SYSS PWS PITT | 2016-06-20 09:09 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-06-20 09:09 |  |  |  | 2016-06-20 09:09 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-08 06:43 |  | <p class=MsoNormal style="margin-bottom:12.0pt;">There is inconsistency in different CHARM Class for the <b>HART errors</b> Column that appear in <b>Attribute</b> tab for SIS I/O CHARMs:</p> <p class=MsoListParagraph style="text-indent:-.25in;">2.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:'Times New Roman';">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b>RTD Input CHARM</b> : HART errors appear as Greyed Out</p> <p class=MsoListParagraph style="text-indent:-.25in;">3.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:'Times New Roman';">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b>Thermocouple_mV CHARM </b>: HART errors appear as Greyed Out</p> <p class=MsoListParagraph style="text-indent:-.25in;">4.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:'Times New Roman';">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b>Voltage CHARM</b> : HART errors do not appear</p> <p class=MsoNormal>&nbsp;</p> <p class=MsoNormal>As the HART Errors are applicable to only Analog Input CHARMs, they should appear as greyed out in all charms or should not appear in any CHARMs in which they are not applicable.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  | Implementation |  |  | 3.6.0 + U3 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>The HART Error attributes are shown or not based on the CHARM Class.&nbsp; If shown, they are grayed out or enabled based on the CHARM functionality (which may or may not support HART Alerts).</p><p>HART devices are not applicable for Voltage class, so they are not shown.</p><p>It could be argued that the same is true for RTD and Thermocouple CHARM classes.&nbsp; If so, then perhaps for these two CHARM Classes, the HART Error attributes should also not be visible.&nbsp; This matter will be taken into consideration.</p> | 8 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | 1. Add the CHARMs of various classes<div>2. Open the attributes tab of each CHARMs</div> |  | U3 |  |  | FINDING | [6 empty] | 98820
35838 | FINDING | Improve virtual controller startup speed | Silvaggio, Gregory W EMR SYSS PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-05-24 22:39 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-05-24 22:39 | 66958 | [6 empty] | Shiferaw, Tedla AUTOSOL PWS PITT | 2016-03-08 10:31 |  | Using the VcoordManager to start a virtual controller appears to delay the start of the VC relative to the index number. For example, starting VC index 1 is fairly immediate (3 seconds), but starting VC index 18&nbsp;takes nearly a minute.&nbsp; The VCoordmanager actually times out waiting for the VC start and it looks like it didn't work, though it eventually does change to the proper state in the manager.<br>See attached file. |  |  |  |  | 0 |  |  |  | <p>CG (5/25) -&nbsp;Ramesh to retest&nbsp;and update the finding with observations.</p> | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lal, Ramesh External | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U5 |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Shiferaw, Tedla AUTOSOL PWS PITT | Development |  | &nbsp;updated Planned Release = U3 as was in RR. RR should not be used/created for Findings since Findings are a release record themselves. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use to Vcoordmanager to stop a VC with a high index number. After it is stopped, start the VC and notice the time necessary for it to start. |  | U4 |  |  | FINDING | [6 empty] | 97652
35853 | FINDING | While loading logic solver (1508), it gives error as “Error when trying to load sis script 1 & Unable to open sis sheet file”. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:19 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:19 | 66791 |  |  | 2016-04-17 06:19 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-09 00:42 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>As per&nbsp;Developer suggestion, I have replaced the OvSisSw.dll (File version-3.6.0.9999 &amp; size-157KB&nbsp;)file in the Ovation\OvationBase folder in DBS drop100 &amp; took a backup of old OvSisSw.dll file.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Steps followed:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>After that rebooted the DBS drop100. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Once drop100 is up, I tried to load the Logic solver followed by downloaded, Clear &amp; loaded the SIS controller drop27/77. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Observation: While loading logic solver (1508), it gives error (Please find attached snapshot “Error_SIS_script 1.jpg”), however the logic solver gets commissioned (verified in logic solver node point). Tried&nbsp; on different logic solver (1508) also but got same issue.</font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>PP:04/17/2016-Verified in Ov3.6.0_U6 &amp; found the loading issue of logic solver is resolved but I have a observations which&nbsp;are tracked by F#36018.</font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Hence it is closed.</font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software | this issue is related to CM naming for SIS 1508 which is fdifferent than CSIS. also there was change that the empty CMs generates empty .sif files, therefore CRC =0 is allowed number.<br> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hutchison, Steven EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U5 |  | OV3.6.0_U3,DBS Drop100 (192.168.36.100) WS12R2,SIS Controller OCR400 G02, Logic Solver (1508) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | fix for U4 will be provided via mail. <br> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Created a SIS sheet in logic solver 01</p><p>2. Compile the SIS sheet successfully.</p><p>3. Error occurred while loading Logic solver 01</p> |  | U3 |  |  | FINDING | [6 empty] | 95097
35854 | FINDING | Dump CRC saves as an HTML file for CSLS, but there is no option to select HTML file type in Dump CRC window | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-28 08:40 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-28 08:40 |  |  |  | 2016-04-28 08:40 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-09 03:33 |  | There is no option select HTML as file type for dump CRC in the dump CRC window for CSLS. But even after selecting .txt (text file) option, Dump CRC of CSLS is saved in HTML file.<div>There should be an option to select HTML file type in this window.</div><div><br></div><div>Please check attached dump CRC file and screenshot of dump CRC window for further reference.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA |  |  |  | Implementation |  |  | 3.6.0 + u3 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | The CSLS only generates an HTML report. | 5 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <ol><li>Right click a CSLS and select dump crc</li><li>Check the file types in dump CRC window, save the dump CRC as .txt file.</li><li>Check the extension of the output file location is HTML</li></ol> |  | U3 |  |  | FINDING | [6 empty] | 95886
35856 | FINDING | CSLS goes in to confused state after clear operation is performed on a CSLS without loading it | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 14:26 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 14:26 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-09 04:57 |  | <p class=MsoNormal>If a CSLS is cleared directly after assigning and commissioning of CSLS (Without loading the CSLS), then it is decommissioned and goes into a confused state (It is not possible to load CSLS after this). </p> <span style="font-size:11.0pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Also even after performing unassign operation through developer studio, the mac address is not released by the CSLS as we are not able see the mac address when next assign operation is performed.</span><div><span style="line-height:1.5em;">It is required to manually unassign the CSLS to get it back to normal state.</span><br></div><div><span style="line-height:1.5em;">Please refer to attached screenshot</span><br></div><div><p class=MsoNormal></p></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <p>It happens, because while assigning the CSLS the script is loaded into Controller's RAM, but not on flash memory.</p><p>The&nbsp;easiest way&nbsp;to&nbsp;prevent such situations is&nbsp;to&nbsp;set &quot;cleared flag&quot; on the CSLS right after assigning it, so user will not be allowed to clear it.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  | Implementation |  |  | 3.6.0 + u3 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>After assigning and commissioning CSLS user should not be allowed to clear the CSLS&nbsp;and reboot the controller before performing CSLS and (or) Controller load. Documentation should be updated accordingly.</p><p>If it happens anyway: the workaround is&nbsp;to load the active controller in order to return to the normal state.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Assign an unassigned CSLS</li><li>Commission window come up, Commision it.</li><li>Clear the CSLS</li></ol> |  | U3 |  |  | FINDING | [6 empty] | 95724
35857 | FINDING | LP and DP points are showing bad quality. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:46 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:46 |  |  |  | 2016-03-22 10:46 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-09 05:19 |  | <p><font face=Calibri size=3>LP&nbsp;and DP points are showing bad quality in signal diagram but in actual LP&nbsp;and DP points don’t have quality(PI showing correctly).</font></p><p><font face=Calibri size=3><br></font></p><p><font face=Calibri size=3>Do they have ANY invalidity bits set?</font></p><p><font face=Calibri size=3><br></font></p><p><font face=Calibri size=3><br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U3</p><p>OS-WS12,WIN7 64 BIT.</p><p><u><br></u></p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>LB-03/10/16-Yes all the invalidity bits are set you can view the same on attachment. One more thing I would like to add. If user creates&nbsp;the LP&nbsp;point on <strong>developers studio</strong> and assign it&nbsp;to algorithm in this case quality of LP point appears BAD on signal diagram and&nbsp;status of invalidity bit&nbsp;appears FFFFH on Point information window&nbsp;. But if user creates the point on control builder using <strong>Create user point</strong> feature in this case no quality appears on signal diagram and&nbsp;status of invalidity bit&nbsp;appears 0000H on Point information window.</p><p><br></p><p>Invalidity bits display as bad quality in signal diagram.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Following are the steps to reproduce-</p><p>1)Make a control sheet and add&nbsp;2XMTR algorithm.</p><p>2)Create a LP or DP&nbsp;point and&nbsp;set its initial value 0.</p><p>3)Assign the above LP or DP point to&nbsp;PBPT pin.</p><p>4)Load the control sheet and observe the quality of PBPT point in signal diagram.</p><p>&nbsp;Screenshot is also attached for your reference.</p><p>&nbsp;</p><p><font face="Times New Roman" size=2><br></font></p> |  | U3 |  |  | FINDING | [6 empty] | 93789
35862 | FINDING | STP Note: Safety Shell Infrastructure is in 3.6.0_U4 | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-09 14:02 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-09 14:02 |  |  |  | 2016-03-09 14:02 |  |  |  | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-09 14:02 |  | <p>IC 3/9/16&gt; per 3/8/16 Dev + Val meeting:&nbsp;</p><p>-the Safety Shell infrastructure is in 3.6.0_U4. <br>-It should be transparent to 3.6.0 users and does not require any specific testing. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 93157
35876 | FINDING | PWTTS - Wireless device RN points keep going in and out of BAD status every minute | Ritchie, Mark AUTOSOL PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Ritchie, Mark AUTOSOL PWS PITT | 2016-03-28 08:15 | [11 empty] | Ritchie, Mark AUTOSOL PWS PITT | 2016-03-28 08:15 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-03-10 13:36 |  | <p>Wireless devices commissioned in Ovation and assign LA points to PV, SV, TV, FV, and PRange.&nbsp; Monitor in Alarm system and note that some devices RN points keep going in and out of BAD status.</p><p>See attached for details.</p><p>There are 3 different gateways configure on the system:</p><p>Gateway 1 - Simplex, Firmware 4.6.43, 7 out of 77 devices report BAD status</p><p>Gateway 2 - Redundant, Firmware 4.4.45, 2 out of 3 devices report BAD status</p><p>Gateway 3 - Simplex, Firmware 4.4.45, 1 out of 2 devices report BAD status</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br> A device is configured with a PV value and a LOOP CURRENT value.<br> <br> The driver periodically sends a command 9 and gets a response. The response is always good and contains a value for PV and CURRENT LOOP. The points are updated and given a good quality.<br> <br> Immediately after a command 9 is sent a command 3 is sent.<br> <br> But when the driver is building the status command it decides whether a command 2 is needed. If a device has a LOOP CURRENT point configured then a command 2 is sent.<br> <br> Command 2 just gets the LOOP CURRENT value which is always the same as what was returned from command 9.<br> <br> Every other time a command 2 is sent the response message has an error 33. This causes the LOOP CURRENT point to be set to BAD quality. The polling rate was set to 30 seconds, one minute and three minutes and always the second request would return an error.<br> <br style=""> <br style=""> </span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>A device is configured with a PV value and a LOOP CURRENT value.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>The driver periodically sends a command 9 and gets a response. The response is always good and contains a value for PV and CURRENT LOOP. The points are updated and given a good quality.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>Immediately after a command 9 is sent a command 3 is sent. This is a status command.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>But when the driver is building the status command it decides whether a command 2 is needed. If a device has a LOOP CURRENT point configured then a command 2 is sent. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>Command 2 just gets the LOOP CURRENT value which is always the same as what was returned from command 9.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>Every other time a command 2 is sent the response message has an error 33. This causes the LOOP CURRENT point to be set to BAD quality. The polling rate was set to 30 seconds, one minute and three minutes and always the second request would return an error.</font></p><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3>I do not know why the gateway returns an error for every other command 2. The solution may be to simply this command.</font></p><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face="Lucida Sans Unicode" size=3><br></font></p><font face="Times New Roman" size=3> </font> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Bind devices to Ovation and assign RN and LA points to device and its primary variables |  | U3 |  |  | FINDING | [6 empty] | 93922
35877 | FINDING | PWTTS - Fieldbus port allowed to configure multiple devices as Backup Link Master | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Phan, Quang EMR ENT TECH AUS | 2016-05-27 12:48 | [11 empty] | Phan, Quang EMR ENT TECH AUS | 2016-05-27 12:48 | 66751 |  |  | 2016-05-27 12:48 |  |  |  | Phan, Quang EMR ENT TECH AUS | 2016-03-10 13:57 |  | <p>During FF commissioning process, BLAS already assigned previously, 2nd device is allowed to be configured as BLAS.</p><p>See attached email for details.</p> |  |  |  | <p>Please commission 2 BLAS capable devices.&nbsp; When asked for &quot;As Backup Link Master&quot; for the first device, click yes.&nbsp; Any and all subsequent BLAS capable devices being commissioned&nbsp;will not be asked to be commissioned as Backup Link Master.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  | Verified issue was fixed using build U9 | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Commission 1st device as BLAS.&nbsp; Commission 2nd device and click Yes when ask if it be assign as BLAS. |  | U3 |  |  | FINDING | [6 empty] | 97943
35878 | FINDING | PWTTS - Fieldbus port download fail after configure device function block on a module | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Phan, Quang EMR ENT TECH AUS | 2016-05-27 12:46 | [11 empty] | Phan, Quang EMR ENT TECH AUS | 2016-05-27 12:46 | 66851 |  |  | 2016-05-27 12:46 |  |  |  | Phan, Quang EMR ENT TECH AUS | 2016-03-10 14:06 |  | <p>Fieldbus port download failed after a module was update with more function blocks added.</p><p>See attached email for details that was sent to Steve and Gil.</p><p><br></p><p>This is different from Finding 35680 which was due to Window Firewall setting.&nbsp; Gil already put a temporary fix on Austin system.</p><p><br></p><p>GWS&gt; Changing to Gil per the 3.6.0 dev\val\doc meeting</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | <p>This finding is related to Finding&nbsp;35917 (Changeset 66851) as well as Finding 35680 (Changeset 66484).&nbsp; Changeset 66484 only added the HSEServer to the firewall exceptions, but after systems were upgraded to U3, it was discovered that the Firewall Exception was not enough to satisfy the Fieldbus Communications Errors.&nbsp; Changeset 66851 was a restructuring of how the HSEServer gets installed and reconfigures it to be a Network Service which will satisfy the Fieldbus Communications.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Wood, Thomas T AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0 U5 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  | <p>Port download was successful on both Simplex and Redundant modules using build U9.&nbsp; </p><p>Note that it took an average of 26 minutes to complete and single port download on a fully loaded segment with minimum of 1 block from each device&nbsp;assigned. </p><p>During download, the Server Busy keep popping up which required user to click on Retry in order to advance.&nbsp; 26 minutes reported included an automation script that click thru Retry whenever Server Busy window popup.</p><p><br></p> | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | See attached. |  | U3 |  |  | FINDING | [6 empty] | 97942
35881 | FINDING | Macro interface window could not highlight the algorithm of selected point. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 05:33 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-15 05:33 |  |  |  | 2016-03-15 05:33 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-11 00:04 |  | <p>Macro Interface Editor window is only&nbsp;highlighting the algorithm of&nbsp;first selected point. However no other algorithms are highlighted&nbsp; by selecting the remaining points on&nbsp;&quot; Macro Interface Editor window&quot;.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U3</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | LB-03/15/16-This issue was observed on Ovation3.6.0_U3. but on Ovation3.6.0_U4&nbsp;, it is observed that Macro Interface Editor window is highlighting the algorithm of&nbsp;selected point. Hence this finding is&nbsp;closed by validation. | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Create a control macro or open an existing&nbsp;control macro.</p><p>2)Go to edit menu and select Macro Interface.</p><p>3)After this Macro Interface Editor window will open. Now click or select any point, this highlight the corresponding algorithm on the sheet. <br>4) Further click or select another point , corresponding&nbsp; algorithms are not seems to be highlighted on sheet.</p><p>Screenshot is also attached for your reference<br></p> |  | U3 |  |  | FINDING | [6 empty] | 93350
35882 | FINDING | Algorithm symbols are editable while creating control macros. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:44 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:44 |  |  |  | 2016-03-22 10:44 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-11 00:04 |  | While creating a control macro it is observed that user can edit the algorithm symbol.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U2</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the developers studio.</p><p>2)Create a control macro.</p><p>3)Insert any algorithm.</p><p>4)Try to edit the algorithm symbol.</p><p>Screenshot is also attached for your reference.<br></p> |  | U3 |  |  | FINDING | [6 empty] | 93788
35885 | FINDING | Controller can not be load due to large sheet size. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-01 07:45 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-01 07:45 |  |  |  | 2016-04-01 07:45 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-03-14 06:31 |  | Controller&nbsp;can not be load due to large sheet size.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U4 with OCR1100 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | The U3 contained an abnormally large value for sheet set size. &nbsp;This was changed in U4, but the change only affected new control tasks. &nbsp;This will not be an issue for the customer since they will not get the value that was defined in U3. | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">1.&nbsp;Insert the cleared flash in drop38/88 and hard boot drop38/88</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2.&nbsp; Performed download &amp; hard boot of&nbsp;&nbsp;drop38/88 </span></p><p>3.&nbsp;<span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Tried to load drop38/88 but&nbsp;</span><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">after load preview window, the loading hangs at “Processing Internal Referenced Point” window</span>&nbsp;&nbsp;&nbsp;</p><p>&nbsp;&nbsp;&nbsp; and<font face=Calibri><font size=3><span style=""> </span></font><font size=3>error message appeared</font><span style=""><font size=3>&nbsp; </font></span><font size=3>in error log “Unable to connect Host” (please refer attached snapshot U4_Controller Loading error.jpg ).</font></font></p><p><font face=Calibri size=3>4. <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Waited for approx. 10-15 mins and then clicked somewhere in the studio, then studio crashes (please refer the screen shot controller_U4 crash.jpg).</span></font></p><p><font face=Calibri size=3><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">5. <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Later, when option “Try to restore program” is selected in pop-up window then controller seen fails in 1800.diag. However, the message that appears in the pop up screen</span></span></font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>&nbsp;&nbsp;&nbsp; and error log is target drop38 is offline” (please refer attached screen shot Error pop up after restore_U4.jpg ) and now when clicked “OK” button then</font></p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;<font face=Calibri size=3>Ovpt studio error appeared (Please refer attached screen shot OvPtStudioErr.txt)&nbsp;</font>&nbsp;</p><p><br></p><p><font face="Times New Roman" size=3> <span style="color:rgb(0, 112, 192);">However&nbsp;when </span></font><span style="color:rgb(0, 112, 192);">Controller's sheet set size (for drop38/88) was&nbsp;changed to 1 00 00 00 bytes ( from 6 29 14 56)&nbsp;in Dev. Studio for Control Task 1 to 5.</span></p><p><span style="color:rgb(0, 112, 192);">(Path: Controller Drop\Configuration\[Control]\Control Task\Task x) then&nbsp; performed step 1 to&nbsp;2 and&nbsp; tried again to load drop38/88.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"> This time controller loaded successfully</span></p><font face=Calibri size=3><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p></font><p><br></p><p><font face="Times New Roman" size=3> <br></font></p><font face=Calibri size=3><p><br></p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><br></p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p>&nbsp;&nbsp;&nbsp; <font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3><br></font></p></span><p><br></p></span><p><br></p></font><p><br></p><p><font face="Times New Roman" size=3> <br></font></p> |  | U4 |  |  | FINDING | [6 empty] | 94200
35886 | FINDING | In 3.6.0_U4, New Controller OCR400 can not be added to studio. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-13 08:14 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-13 08:14 | 67224 |  |  | 2016-05-13 08:14 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-03-14 07:03 |  | <p>In 3.6.0_U4, New Controller OCR400 can not be added to studio. </p><p>Tried to create Controller drop9/59 (OCR400) to studio, Upon saving&nbsp;studio gives following error. &lt;OvPtSystemValidate.cpp:8938&gt; [OvPtApi]: (Control Memory Size for DROP9/DROP59 cannot accommodate all of the Control tasks)</p><p>For reference Screenshot and Studio Error&nbsp;attached.</p><p>Workaround: First create drop9/59, controller type OCR 1100 then&nbsp;modify the controller type to &quot;OCR400&quot;. Following steps to be followed:</p><p>Step-1: While insertion of a new controller, select &quot;OCR1100&quot; controller type. </p><p>Step-2: Save</p><p>Step-3: Change controller type from &quot;OCR1100&quot; to&nbsp;&quot;OCR400&quot;</p><p>Step-4: Save&nbsp;&nbsp;&nbsp;</p> |  |  |  | The affected area is in the software which assigns default values for control task memory sizes based on the controller style.&nbsp; The software has been changed to permit the initial creation of an OCR400 controller (not the default controller style) to have satisfactory values for memory sizes.&nbsp; No specific test recommendations other than what would be considered to be obvious. | 0 |  |  |  | Verified in U7, New OCR 400 can be added to studio. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | <p>3.6.0_U4+OCR400</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>create Controller drop9/59 (OCR400) to studio. Upon saving following error appeared</p><p>&lt;OvPtObject.cpp:2088&gt; [OvPtApi]: (Unable to expand node)</p><p>&lt;OvPtObject.cpp:3917&gt; [OvPtApi]: (Unable to expand drop object)</p><p>&lt;OvPtRef.cpp:11661&gt; [OvPtApi]: (Unable to commit the new controller configuration into the database.)</p><p>&lt;OvPtObject.cpp:2088&gt; [OvPtApi]: (Unable to expand node)</p><p>&lt;OvPtObject.cpp:4123&gt; [OvPtApi]: (Unable to expand controller object)</p><p>&lt;OvPtRef.cpp:9211&gt; [OvPtApi]: (Unable to commit the new Control Task Configuration into the database)</p><p>&lt;OvPtObject.cpp:1639&gt; [OvPtApi]: (System Validation Failure)</p><p>&lt;OvPtSystemValidate.cpp:8938&gt; [OvPtApi]: (Control Memory Size for DROP9/DROP59 cannot accommodate all of the Control tasks)</p> |  | U4 |  |  | FINDING | [6 empty] | 96808
35887 | FINDING | In certain scenario, CSLSs go in unknown state, need manual steps to restore the CSLS. Scenarios and steps need to be documented. | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:21 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:21 |  |  |  | 2016-05-20 06:21 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-03-14 09:34 |  | <font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>In certain scenario, CSLSs go in unknown state, need manual steps to restore the CSLS. Scenarios and steps need to be documented.</font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>&nbsp;</font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri><b><u><span lang=EN-IN style="COLOR:rgb(31,73,125);">Scenario-1</span></u></b><span lang=EN-IN style="COLOR:rgb(31,73,125);">: If DBS OS re-installed, where CSLSs are in Commissioned state before uninstallation of OS.</span></font></font></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>Need to perform manual steps to assign and commission the CSLS</font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri><br></font></span></p> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>As observed in 3.6.0_U3, for upgrade of Ovation from U2 to U3, OS of the Ovation stations (DBS and EWS) re-installed due to new Oracle support.</font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font face=Calibri><font size=3>In Ovation 3.6.0_U2, CSLSs were in commissioned state. For Upgrade to U3, OS of the DBS and EWS re-installed. After reinstallation of OS and Ovation 3.6.0_U3, CSLSs (were in commissioned state in U2) <span>&nbsp;</span></font><font size=3>go in unknown state.</font></font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>CSLSs not recognise by studio. Not available in Live device window. So un-assignment/ assignment/ Load etc can not be performed.</font></span></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3 face=Calibri>&nbsp;</font></span></p><span lang=EN-IN style="COLOR:rgb(31,73,125);"><span style="TEXT-DECORATION:none;"><font size=3 face=Calibri> <p style="MARGIN:0cm 0cm 0pt;"><b><s><u><span lang=EN-IN style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">Scenario-2</span></u></s></b><s><span lang=EN-IN style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">: Mentioned in Finding#35856, CSLS is in commissioned state then performed &nbsp;Unassign of the CSLS- Assign the CSLS- After assignment of CSLS (Not Loaded)- Perform Clear operation. CSLS goes in unknown state. CSLS cannot be unassigned/load/assigned. </span></s><s><span lang=EN-US></span></s></p> <p style="MARGIN:0cm 0cm 0pt;"><s><span lang=EN-IN style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">In this case, we need to perform above manual steps to restore/ unassigned the CSLS. </span></s>(Mikolaj Raciborski - this may be resolved by just loading the active controller, F#35856 resolution)</p></font></span></span><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><b><u><span lang=EN-IN style="COLOR:rgb(31,73,125);"><span style="TEXT-DECORATION:none;"><font size=3 face=Calibri><br></font></span></span></u></b></p><font size=3 face="Times New Roman"></font> <p style="MARGIN:0in 0in 0pt;"><font face=Calibri><b><u><span lang=EN-IN style="COLOR:rgb(31,73,125);"><font size=3>Following manual steps (1 to 10) for Un</font></span><span style="COLOR:rgb(31,73,125);"><font size=3>Assignment of <span>&nbsp;</span></font><font size=3>the CSLS</font></span></u></b><span style="COLOR:rgb(31,73,125);"><font size=3> </font></span></font></p><font size=3 face="Times New Roman"></font> <ol style="LIST-STYLE-TYPE:decimal;DIRECTION:ltr;"> <li style="FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Disconnect power from CSLS,</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Disconnect CSLS devices from the base (both yellow boxes)</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Swap the box order (left will be right, right will be on Left)</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Disconnect IOPs (Ethernet ports)</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Swap IOPs as the CSLS devices</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Insert CSLS devices into the base</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Plug power back</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Wait until the CSLS goes on and will blink as UnAssign (red led blinking) </span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">Plug IOPs back</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);">In Studio, Unassigned the CSLS via right click [UnAssign]option.</span></p></li> <li style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(31,73,125);FONT-STYLE:normal;"> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"><span style="COLOR:rgb(31,73,125);"></span><font face=Calibri><span style="COLOR:rgb(31,73,125);"><font size=3>After performing step-1 to step-10 CSLS get recognized by Studio, then assignment and&nbsp;</font><font size=3>commissioned can be done via studio.</font></span><font size=3> </font></font></p></li></ol><font face=Calibri><font size=3> <p class=MsoNormal style="BACKGROUND:#f1f1f1;MARGIN:0cm 0cm 0pt;LINE-HEIGHT:normal;"><span lang=EN-IN style="FONT-SIZE:12pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">(Mikolaj Raciborski - The manual unassignment procedure is already described in the documentation, please just reference it)</span></p> <p style="MARGIN-BOTTOM:0pt;FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;FONT-WEIGHT:normal;COLOR:rgb(0,0,0);FONT-STYLE:normal;MARGIN-TOP:0in;"></font></font>&nbsp;</p> |  |  |  | MM (4/25/16): Added the section 5.1.3 &quot;<b><font size=3>To manually unassign an SIS CHARMs Smart Logic Solver&quot;. Check the &quot;OW360_43-21_Apr&quot;pdf&nbsp; at <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>. Check the online help too.</font></b> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Documentation | MM (4/25/16): Added the section 5.1.3 &quot;<b><font size=3>To manually unassign an SIS CHARMs Smart Logic Solver&quot;. Check the&nbsp;&quot;OW360_43-21_Apr&quot; pdf&nbsp;&nbsp;at <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>. Check the online help too.</font></b> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p><font size=3>MM (4/25/16): <strong>The issue is fixed and resolution is available in 3.6.0_U7 Built.</strong></font></p><p><font size=3>Verified in U8, found fixed.</font></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U3 |  |  | FINDING | [6 empty] | 97324
35889 | FINDING | Misc 3.6.0 DIR items | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 16:56 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 16:56 |  |  |  | 2016-06-07 16:56 |  |  |  | Capani, Innocenzo AUTOSOL PWS PITT | 2016-03-14 11:01 |  | <p>Misc. items to add to DIR:</p><p>-CLN is removed from 3.6.0 (F#34810). <br>IC 6/7/16&gt; did not DIR since no CLN section exists in DIR. <br><br></p><p>-new OHI version&nbsp;is introduced -&nbsp;&nbsp;<span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">OHI.sys (3.6.0.4758), OHI.dll (3.6.0.4758) <br>&nbsp; (<font face=Calibri size=3>(IC 6/7/16 &gt; done, DIR'd, per Mati versions are now 3.6.0.8116) <br><br></font></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">-Lumension AV issue? (SDR 35692)<br><font face=Calibri>(IC 6/7/16 &gt; done, DIR'd in Ov &amp; LAV DIR. </font><br><br></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">-Server 2012 .net install workaround. <br>&nbsp; <font face=Calibri size=3>(IC 6/7/16 &gt; done, DIR'd for ELC, SPO, AMS) <br><br></font></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">-OPC AES &amp; OPH Scanner incompatibility - see F#32058</span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">IC 6/7/16&gt; Done, Note is in OPC AES 2.0 DIR.<br><br></span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">-add Battery related Wireless HART note - see F#28567.<br><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">IC 6/7/16&gt; Done, Note is in 3.6.0 DIR.</span><br><br></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">-add note for SRF 2137 limits:&nbsp;<br><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">&nbsp;The new default values&nbsp;apply only to new control logic.<span>&nbsp; </span>Projects with existing control logic will retain their current values.<br></span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">IC 6/7/16&gt; did not DIR since we do not get into this level of detail for SRFs and this is not really a discrepancy.&nbsp; <br><br>-If F#33589 is not fixed, report issue as discrepancy in the DIR (SRU does not support SIS CHARMs).&nbsp; <br>(IC 6/7/16 &gt; done, SDR'd &amp; DIR'd) </span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br>-Note SIS CHARMs support hotfix for AMS 13.0<br>&nbsp; (IC 6/7/16 &gt; done, DIR'd) </span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 15 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U3 |  |  | FINDING | [6 empty] | 98363
35892 | FINDING | SIS Charms has stopped working in U4 | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:55 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:55 | 66785 |  |  | 2016-04-13 23:47 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-15 01:53 |  | <p>SIS Charms has stopped working in U4. In U3, it was working fine.&nbsp;</p> <p>Observed on SIS Controller Drop 30/80: Not able to perform any SIS Charms operation. Please find the details below:</p> <p>a. Upon clicking on View Live Devices List, Ovation Developer Studio hangs and after some time gives following error without opening the Live Devices&nbsp; List:</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p><font face="Courier New"><em>Status Execution encountered a problem.</em></font></p> <p><font face="Courier New"><em>Op Response code of 0x11 expected. Received: 34</em></font></p></blockquote> <p><font face="Courier New"><font face="Segoe UI">Please see the attached screenshot as</font> <em>Error.png</em></font></p> <p>&nbsp;</p> <p>b. Clear and load operation of the CSLS also give the above mentioned errors in point a.</p> <p>&nbsp;</p> <p>c. Upon giving&nbsp;some SIS Secure Write commands (Unassign, Lock, Unlock, Reboot) RT_FAILURE error comes after timeout occurs in SIS Secure Write Confirmation window. Please see the attached screenshot as <em>RT_FAILURE.png</em></p> <p><em></em>&nbsp;</p> <p>d. Manual Switchover of the CSLS was done to check if the status is updated in PI, but the status of CSLS RN points does not get updated.</p> <p>&nbsp;</p> <p>e. printErrorBuffer logs of Primary Controller Drop30 (In Control) shows following errors:</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p><font face="Courier New">MON MAR 14 11:07:25 2016 : 0xed5d2b0 (csDiagWorker): task 0xed5d2b0 has had a failure and has been stopped.<br>MON MAR 14 11:07:25 2016 : 0xed5d2b0 (csDiagWorker): The task been terminated because it triggered an exception that raised the signal 11.</font></p></blockquote> <p><font face="Courier New"><font face="Segoe UI">Please find attached the printErrorBuffer logs as</font> <em>printErrorBuffer-Drop30.txt</em></font></p> <p><em></em>&nbsp;</p> <p dir=ltr>f. Controller load fails with following errors:</p> <blockquote style="MARGIN-RIGHT:0px;" dir=ltr> <p dir=ltr><font face="Courier New">SIS Data File Download Failed for &quot;Drop30/Drop80&quot;</font></p> <p dir=ltr><font face="Courier New">Invalid code received from the Controller on Operation Code. Code&nbsp;Received:&nbsp;REQUEST STATUS SERVER BUSY</font>&nbsp;</p></blockquote> <p dir=ltr>Please see the attached screenshot as <em>SIS Data File Download Error.png</em>&nbsp;</p> <p><em></em>&nbsp;</p> <p><em>Note: In U4, configuration at the level of Controller and SIS I/O CHARMS device have been regenerated and the Controller is downloaded with the latest configuration.</em></p> <p><em></em>&nbsp;</p> <p><font face="Courier New"></font>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | csDiagWorker thread was crashing without returning a lock. So it affected all other sis tasks. Null checks has been implemented so the csDiagWorker does not crash. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | U5 |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>Additional checks has been implemented to prevent problematic situation.</p> <p>&nbsp;</p> <p>PA 4/14/16: Retested with U6 and found fixed</p> | 9 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94876
35893 | FINDING | SVTP issue:SVTP "3.6.0_SysViewer_SVTP_rev2.2_xxx.doc", Testcase 5.13.2.0-g needs to be deleted | Joshi, Parmesh EMR SYSS PWS NOIDA | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Joshi, Parmesh EMR SYSS PWS NOIDA | 2018-12-10 03:09 | [11 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2018-12-10 03:09 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-03-15 03:41 |  | SVTP issue: SVTP &quot;3.6.0_SysViewer_SVTP_rev2.2_xxx.doc&quot;, Testcase 5.13.2.0-g is incorrect and needs to be removed. The reason is that Secure Parameters cannot be analog and are always digital (which is covered in testcase 5.13.2.0-f) |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/System Viewer | SVTP/STP | In Validation | 3.6.0 |  |  | Released to Library | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | PJ 12/10/2018&gt; Attached SVTP rev 2.3 addresses the issue. Please verify . | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [6 empty] | EPM Validation | U4 |  |  | FINDING | [6 empty] | 135364
35895 | FINDING | OSV does not show Point Attributes for Ovation SIS I/O CHARMs | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wozniak, Diane M EMR SYSS PWS PITT | 2016-03-28 13:16 | [11 empty] | Wozniak, Diane M EMR SYSS PWS PITT | 2016-03-28 13:16 |  |  |  | 2016-03-28 13:14 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-03-15 05:34 |  | <p>In System Viewer when a CSLS containing SIS I/O CHARMs is selected, it shows the status of CSLS in Point Attributes whereas it is expected to show the status of all SIS I/O CHARMs.</p> <p>If compared to Ovation I/O module, when an I/O module is selected, the Point Attributes tab shows details of all hardware I/O channels</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software | <p>works as designed. reflects the current data model. individual channel details can be found beneath the csls in the hierarchy.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sachan, Pallavi EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | Net#36 EWS Drop155 (W7-SP1 64-bit) |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol> <li>In System Viewer, expand upto any CSLS containing SIS I/O CHARMs.</li> <li>Select the CSLS in left pane so that tabs showing different informations are displayed in right pane.</li> <li>Point Attirbutes tab shows the information of CSLS whereas it is expected to show the information of all SIS I/O CHARMs configured on that CSLS</li></ol> | EPM Validation | U4 |  |  | FINDING | [6 empty] | 93936
35900 | FINDING | Please add total size to sheet set size configuration warning message. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2016-05-01 10:50 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-05-01 10:50 | 3.6.0_U6 / 66752 |  |  | 2016-05-01 10:50 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-03-15 06:55 |  | If an entered control task sheet set size value causes the total limit for the OCR to be exceeded, an error message will be displayed.&nbsp; This message does not state what the limit is, however.<br> |  |  |  | <p>The affected area is in the generation of the error message displayed when the summation of a controller's configured control set memory sizes exceed the total control memory size.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | The system validation error message will be changed to include the total control memory limit. | 7 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U4 |  |  | FINDING | [6 empty] | 96014
35905 | FINDING | Some files for the Virtual Controller configuration are missing | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-26 10:49 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-26 10:49 | 67094 |  |  | 2016-04-26 10:49 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-15 15:12 |  | There are files used for the configuration of a Virtual Controller host, including a batch installation file and registry file.&nbsp; These are missing in U4. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U5 |  | Windows Ovation 3.6.0 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | Verified *bat and *reg files are present. &nbsp;Also added the wrlmapi* files. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Install Ovation 3.6.0 U4, check folder Ovation\OvationVirtual for .bat or .reg files. |  | U4 |  |  | FINDING | [6 empty] | 95699
35907 | FINDING | vxsim does not need a license file to start up. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-20 12:51 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-20 12:51 | 66827 |  |  | 2016-04-20 12:51 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-15 16:57 |  | <p>The vxsim in U4 is starting up without a license.&nbsp; It gives error about not finding the license file, even though the previous license file is in place.&nbsp; See attached file.&nbsp; But the vxworks continues to boot up and the controller is operational. </p><p>But even removing the license file completely, the vxsim still starts up. The additional licensing of virtual controllers has always been a requirement. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U5 |  | Ovation 3.6.0. |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Run vxsim without having a license installed. |  | U4 |  |  | FINDING | [6 empty] | 95313
35908 | FINDING | Microsoft bridge can not be configured for virtual controller on 2012 Server R2 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-19 15:35 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-19 15:35 | 68021 |  |  | 2016-05-19 15:35 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-15 17:11 |  | <p>With U4, the WRTap has been able to be installed on the two 2012 VCH machines in the Validation lab. But the attempt to bridge the WRTap to the Ovation NIC has been unsuccessful.&nbsp; It either just hangs up creating the bridge or it fails (see attached file). </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U8 |  | Ovation 3.6.0 on Server 2012 R2 VCH |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | Updated the installation procedure and moved WRTap driver to a folder directly on the Ovation DVD so that it may be installed prior to Ovation. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Install WRTap and bridge it to Ovation NIC. </p> |  | U4 |  |  | FINDING | [6 empty] | 97273
35909 | FINDING | Character field length of ED,EU,RS,ST is not updated as per the SRF1725 on help file. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 01:52 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 01:52 | 3.6.0_U5 |  |  | 2016-04-13 01:52 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-16 00:37 |  | <p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman"><font face="Segoe UI">As per the SRF1725 Functional Overview: </font></font></font><font size=3><font face="Times New Roman">The Ovation Software will be enhanced to support ED fields of 50 bytes, EU fields of 12 bytes, RS fields of 12 bytes, and ST fields of 12 bytes.<span>&nbsp; </span>This means the internal Ovation WESAPI will need to be enhanced to support the bigger ED, EU, RS, and ST fields, and also all of the Ovation programs that display and/or store the ED, EU, RS, and ST fields will need to be modified to be able to display/store the 50 byte ED field and the 12 byte EU, RS, and ST fields.</font></font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font face="Times New Roman" size=3>&nbsp;</font></p><font face="Times New Roman" size=3></font><p class=MsoNormal style="margin:0in 0in 0pt;text-align:justify;"><font size=3><font face="Times New Roman">Not only will the base Ovation Software need to be modified, but all Ovation add on products will need to support the larger ED, EU, RS, and ST fields.<span>&nbsp; </span>Most of these add on products will need to support running on older Ovation systems with 30 character ED fields and 6 character EU, RS, and ST fields, so new versions of these products will need to support Ovation Systems with both 30 and 50 byte ED fields and 6 and 12 byte EU, RS, and ST fields.</font></font></p> | SJ March 18, 2016: Information related to characters updated the ED,EU,RS, and ST fields. |  |  | SJ March 18, 2016: Updated the ED,EU,RS, and ST fields. Check OvationApplications.chm and Record Types book (OW360_R1140.pdf) placed @ Q:\Communication\TechComm\Share\Validation\OW360_R1140.pdf in Ovation 3.6.0 U5 build. | 0 |  |  |  | LB 04/13/16-Verified on Ovation3.6.0_U6 help file and observed that&nbsp;ED, EU, RS, and ST fields are updated as per the SRF1725. Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Operator Station/Point Information/Documentation | SJ March 18, 2016: Updated the ED,EU,RS, and ST fields. Check OvationApplications.chm and Record Types book (OW360_R1140.pdf) placed @ Q:\Communication\TechComm\Share\Validation\OW360_R1140.pdf in Ovation 3.6.0 U5 build. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U4</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | SJ March 18, 2016: Updated the ED,EU,RS, and ST fields. Check Ovation 3.6.0 U5 build. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open the help file and verify the details of ED,EU,RS,ST character length. Screenshot is also attached for your reference. |  | U4 |  |  | FINDING | [6 empty] | 94819
35910 | FINDING | Algorithm Online help is unable to open the algorithm help details of specific algorithm. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 14:00 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 14:00 |  |  |  | 2016-04-22 14:00 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-16 02:00 |  | <p>When user adds an algorithm on control sheet and open its help by right clicking and selecting the help option ,details of that particular algorithm will open. But when user is adding an algorithm on control sheet and try to open its help file by right clicking and selecting the help option ,it is observed that details of last opened algorithm help&nbsp;got open&nbsp;which is not correct.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Documentation | AA (03-17-2016): The online help file for Control Builder_U4 version is not correct. There are some issues with the Qt help file and is being verified by Pittsburgh. Once, the issue gets resolved this problem would be taken care of. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Casteel, Linda EMR SYSS PWS PITT | Hutchison, Steven EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | <p>Ovation 3.6.0_U4</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Documentation | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>AA (03-17-2016): The online help file for Control Builder_U4 version is not correct. There are some issues with the Qt help file and is being verified by Pittsburgh. Once, the issue gets resolved this problem would be taken care of.</p><p><br></p><p>LC 04/22/2016:&nbsp; Closing this finding because it is not a documentation issue. It is a software issue (Qt).&nbsp; Created Finding 36263 to assign it as a software issue and to assign it to Steve Hutchison.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developers studio.</p><p>2)Add a control sheet or open an existing control sheet.</p><p>3)Add an algorithm say AND, now right click on that algorithm and select help option, this will open the help of last opened algorithm help.&nbsp; </p><p>Same thing is also observed when user try to open the help of some control builder features like, <strong>Find points</strong>, <strong>add algorithm, Macro Interface&nbsp;</strong>etc.</p> |  | U4 |  |  | FINDING | [6 empty] | 95495
35911 | FINDING | Functional description of Recent files is not correct in help file. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 03:14 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 03:14 | 66708 |  |  | 2016-04-13 03:14 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-03-16 02:01 |  | <p>Recent files option is available on &nbsp;control builder File menu option. When user opens and saved a control sheet the entry of that control sheet becomes available on recent files. But help file states that it displays a list of sheets that user has opened which is not correct.</p> | AA (03-17-2016): I have corrected the Control Builder user manual as per the issue related in this Finding. Section 6.2.1&nbsp;has been modified. I have also attached the online help screenshot. The updated&nbsp;online help&nbsp;would be available in 3.6.0_U5 Build. The user manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is OW360_80. |  |  |  | 0 |  |  |  | <div class=message-content>LB 04/13/16-Verified on Ovation3.6.0_U6 control builder&nbsp;help file and observed that&nbsp;Functional description of Recent files is correct. Hence this finding is closed by validation.</div> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Documentation | AA (03-17-2016): I have corrected the Control Builder user manual as per the issue related in this Finding. Section 6.2.1 has been modified. I have also attached the online help screenshot. The updated&nbsp;online help&nbsp;would be available in 3.6.0_U5 Build. The user manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is OW360_80. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | <p>Ovation 3.6.0_U4</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>AA (03-17-2016): I have corrected the Control Builder user manual as per the issue related in this Finding. Section 6.2..1 has been modified. I have also attached the online help screenshot. The updated online help would be available in 3.6.0_U5 Build. The user manual is kept at: <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is OW360_80.</p><p><br></p><p>The modified sentence is: </p><p class=tablebodytextl>Displays the recent control sheet entry of the saved control sheet. There is also a selection on the menu to clear the Recent Files list.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open the help file and verify the functional description and working of recent files. Screenshot is also attached for your reference. |  | U4 |  |  | FINDING | [6 empty] | 94822
35912 | FINDING | Functional Symbol of some Algorithms in help & Manual is not same as the default symbol in Controller Builder | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Casteel, Linda EMR SYSS PWS PITT | 2016-03-16 08:45 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-03-16 08:45 |  |  |  | 2016-03-16 08:45 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-16 03:40 |  | The functional symbol of some algorithms in help &amp; manual is bot same as the default symbol in Controller Builder.<div><ol><li>LEADLAG</li><li>LOWMON</li><li>MASTATION</li><li>PID</li></ol><div>Please refer to the attached screenshots for reference</div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | 3.6.0 +U4 |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | LC 03/16/2016: This is not a valid finding.&nbsp; The symbols in the online help/book are not meant to look like the what is shown in the Control Builder. The online help/documentation shows &quot;functional symbols.&quot;&nbsp; Control Builder shows them in a different way.&nbsp; This issue comes up from time to time, but it is not an issue, and it is not going to change. hence, I am closing the finding. | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Go to add algorithm.</li><li>Browse the above mentioned Algorithm and&nbsp;check the symbol that appears.</li><li>Compare the above symbol with symbol in help or manual for the same algorithm.</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 93444
35913 | FINDING | Online help for LOSELECT algorithm contains incorrect functionality for Quality Parameter "NOTBAD" | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:55 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-13 23:55 |  |  |  | 2016-04-13 23:55 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-16 05:15 |  | <p><u>Functionality of LOSELECT</u>: The LOSELECT algorithm performs a gain and bias on the four inputs. The output is equal to the smallest of the four values, according to the quality (QUAL) parameter.</p> <p>&nbsp;</p> <p>Online help for LOSELECT algorithm contains incorrect functionality for Quality Parameter &quot;NOTBAD&quot;. It is mentioned that:</p> <p><em>a.&nbsp;T<font size=2>he NOTBAD option selects the greater gained and biased input value, providing the qualities of both inputs are not BAD. </font></em></p> <p><font size=2><em>b. The output of LOSELECT is equal to the greater gained and biased input value and contains BAD quality if both input qualities are BAD.</em> </font></p> <p>&nbsp;</p> <p><font size=2><u>Observed&nbsp;Functionality of LOSELECT Algorithm</u>:&nbsp;&nbsp;LOSELECT algorithm always selects the lowest value amongst the available gained and biased input values. </font></p> <p><font size=2></font>&nbsp;</p> <p><font size=2>Please see the attached screenshot as LOSELECT-NOTBAD.png</p></font> | Updated the LOSELECT algorithm to indicate that the <font size=2>LOSELECT algorithm always selects the lowest value amongst the available gained and biased input values. </font> |  |  | <p>Check the LOSELECT algorithm (U5 build and OW360_R1100.pdf in V:\Tests\3.6.0\DOCS_for_Validation).</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | U5 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>LC 04/08/2016:&nbsp; Updated the LOSELECT algorithm in the following way: </p> <p><br></p> <p><font size=3 face="Times New Roman"><br></font></p> <p style="MARGIN:6pt 0in;"><font size=2><font face=Arial>The NOTBAD option selects the <strong><u>lowest</u></strong> gained and biased input value, providing the qualities of both inputs are not BAD. The quality of the output is set equal to the quality of the input selected or to the better quality of the two inputs if the gained and biased input values are equal. If one input has BAD quality, the gained and bias input value and the quality of the input with the not BAD quality are assigned to the output. The output is equal to the <strong><u>lowest</u></strong> gained and biased input value and contains BAD quality if both input qualities are BAD.</font></font></p> <p style="MARGIN:6pt 0in;"><font face=Arial>PA 4/14/16:</font></p> <p style="MARGIN:6pt 0in;"><font face=Arial>Tested in U5 and found fixed in the Online Help as well as the document kept at <font face="Segoe UI">V:\Tests\3.6.0\DOCS_for_Validation.</font></font></p> <p style="MARGIN:6pt 0in;"><font size=2><font face=Arial><span style="BACKGROUND:yellow;"><font face="Segoe UI"></font></span></font></font>&nbsp;</p> <p><font size=3 face="Times New Roman"><br></font></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94875
35914 | FINDING | FACEPLATE algorithm -> reconcile operation doesnot update the online changes | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:02 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:02 | 67523 |  |  | 2016-05-16 04:02 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-03-16 06:20 |  | For FACEPLATE algorithm -&gt; reconcile operation does not update the changes of online tuned parameters in database |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Control Options/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U7 |  | <p>OV360_U4;</p><p>W7 EWS; Ws2012_R2;</p><p>OCR1100; OCR400</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Control Options | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>PS 18Apr16: The&nbsp;reconcile operation is now enabled and working fine for XU and XR fields. However, there is still a problem with X1 field reconcile operation.</p> <p>Please find the attached FACEPLATE.jpeg&nbsp;which denotes that the sheet was loaded with X1/XU/XR parameters and verified the same on Signal Diagram (Step1 and 2). </p> <p><br></p> <p>Now, the same parameters are tuned from signal diagram and reconcillation operation reflects only XU and XR tuning changes not X1 (Step3 and 4).</p> <p>Hence finding is changed to Open failed retest.&nbsp;&nbsp;</p> <p>&nbsp;</p> <p>It is not reasonable to tune the X! type field.&nbsp; Marked as not tunable.</p> <p>&nbsp;</p> <p>PS 15May16: Verified in U7build the X1 field is non-tunable.Now the available tunable fields of XU &amp; XR can be reconciled correctly.&nbsp;Hence Finding is Closed.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create Control sheet with faceplate algorithm connected to any algorithm. Here MASTATION </p><p>2. Parameters are set as X1=1; XU=1; XR=1; TT=TITLE (1.jpg)</p><p>3. Load and verify the signal diagram for the parameters configured above.</p><p>4.&nbsp;Tune X1=25; XU=10; XR=5; TT=TITLE IS CHANGED. Verify the same on PI. (2.jpg)&nbsp;No other parameters are changed.</p><p>5. Go to Dev. Studio-&gt; Drop39-&gt; Reconcile. No results are seen for the above tuned parameters in the sheet. (3.jpg)</p><p><br></p><p>Observations: (On both OCR400 &amp; OCR1100)</p><p>1. The Control Builder sheet carriers the older parameters SET as in Step2 above.</p><p>2. The Signal diagram &amp; PI carriers the newly tuned values as in Step4 above.</p><p>3. Load performed on the controller does not change the values of above parameters in Signal Diagram.</p><p>4. Clear and load the controllers, now the values are set as in Step2 above.&nbsp;&nbsp;</p><p><br></p><p>This is observed with the faceplate.tft in OV3.6.0 also with the one attached in the SDR34581.</p> |  | U4 |  |  | FINDING | [6 empty] | 96875
35915 | FINDING | TT field: The new description overlaps the older one | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-13 06:01 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-13 06:01 | 66920 |  |  | 2016-04-13 06:01 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-03-16 06:40 |  | <p>In TT field the new description overlaps the older one.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>I was able to reproduce this issue.&nbsp; The data stored in the SHC field contains what is seen. This is not a PI issue.&nbsp; PI simply displays what is in the TT field.&nbsp; The software that writes the data to the SHC is the issue.</p> <p><br></p> <p><br></p> <p>Disabled tuning for Title Fields in face place algorithms&nbsp;</p> <p>&nbsp;</p> <p>PS13April16: On OV3.6.0_U6build:&nbsp;The TT field tuning is disabled in FACEPLATE algorithm and is non-tunable on any other point. Hence this finding is closed as fixed.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Step1&gt; Open the Signal Diagram, here Faceplate algorithm.</p><p>Step2&gt; Tune the TT field with description up to 46characters.</p><p>Step3&gt; Verify in Signal Diagram ; verify in PI.</p><p>Step4&gt; Re-Tune the TT field with 10characters description.</p><p><br></p><p>Observation:</p><p>The TT field&nbsp;retains the previous description;&nbsp;the new description looks as overlapping on the previous one.</p> |  | U4 |  |  | FINDING | [6 empty] | 94833
35916 | FINDING | Loading of some virtual controllers causes multiple errors in Error Log | Shiferaw, Tedla AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 13:58 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 13:58 | 67371 |  |  | 2016-05-16 13:58 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-16 08:29 |  | During the load of some virtual controllers, constant errors are being output.&nbsp; See attached file. Some of these are 'couldn't get local memory' errors. For the few points that I looked up, they were OCB points.&nbsp; This was seen on at least drops 141 and 142 on the Tim network. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | <p>GWS&gt; Monitor this in the U5, not sure what's going on, this wasn't reproducible for Tedla.\</p><p>Recreated in U5.&nbsp; Not seen on every VC, just a few.</p><p><br></p><p>GWS&gt; Nuisance message from OPP during point loading. OPP creates LMEM for points on it's own. &nbsp;The first time it does it, it was producing this nuisance message. &nbsp;The message will only be generated if there is an actual error.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U7 |  | Ovation 3.6.0 U4 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Load virtual controllers 141 or 142 on Tim network in Validation lab |  | U4 |  |  | FINDING | [6 empty] | 96968
35917 | FINDING | Can not perform Port Downloads to Fieldbus Ports from Engineering Work Stations | Morris, Gilbert L AUTOSOL PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Morris, Gilbert L AUTOSOL PWS PITT | 2016-03-21 15:02 | [11 empty] | Morris, Gilbert L AUTOSOL PWS PITT | 2016-03-21 15:02 | 66851 | [6 empty] | Wood, Thomas T AUTOSOL PWS PITT | 2016-03-16 12:10 |  | When attempting to &quot;View Live Devices&quot; or perform a Port Download to a port on a Fieldbus Module through the Studio on the 3.6 database server, the requests are successful.&nbsp; When the same thing is attempted on the engineering workstations however errors are encountered. |  |  |  | Please retest Fieldbus&nbsp;Port Downloads from an Engineering Workstation after upgrading to U5 | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U5 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Wood, Thomas T AUTOSOL PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 93712
35920 | FINDING | Ovation Security Manager online help is not linked correctly with few options | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sharma, Puneet EMR SYSS PWS NOIDA | 2018-01-12 02:54 | [11 empty] | Sharma, Puneet EMR SYSS PWS NOIDA | 2018-01-12 02:54 |  |  |  | 2018-01-12 02:54 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-03-17 07:56 |  | Ovation Security Manager online help is not linked correctly with few options |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Casteel, Linda EMR SYSS PWS PITT | [6 empty] | Implementation |  |  | <p>OV360_U4;<br>W7 EWS; Ws2012_R2; </p><p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Documentation | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>PSH (May 17, 2016): Per Linda's mail on May 16, 2016:</p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">UT was looking at Finding 35920, and he can fix it, but it can’t be fixed for the initial release of 3.6. &nbsp;Right not, there is a help ID for the topic “To reset a database password” but there is no help ID for the topic, “To reset a user password.”&nbsp; UT will have to generate a number and put it in the code before you can add it to the topic.&nbsp; He plans to do it with the first patch of 3.6.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Created an SDR 36517 to track this issue in the future revision of the Managing Security manual. Closing this finding as MNR.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">PSH (12-Jan-2018): Closing this finding as it now tracked by SDR 36517.</span></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><span lang=EN-US style="color:blue;">Open Dev. Studio -&gt; Security -&gt; Ovation Security -&gt; Ovation Security Manager.</span></p><p><span lang=EN-US style="color:blue;"><br></span></p><p><span lang=EN-US style="color:blue;">The below listed help&nbsp;options are not linked to correct pages in online help:</span></p><ol><li><span lang=EN-US style="color:blue;">Manage Users</span><font face="Times New Roman" size=3> -&gt; <span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Reset Password -&gt; Help </span></font></li><li><font face="Times New Roman" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"></span></font><font face="Times New Roman" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span lang=EN-US style="color:blue;">Manage Group Policies</span><font color="#000000" size=3> -&gt; <span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Group Policy Properties -&gt; Help </span></font></span></font></li><li><font face="Times New Roman" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><font color="#000000" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"></span></font></span></font><font face="Times New Roman" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><font color="#000000" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span lang=EN-US style="color:blue;">Manage Domain Policies</span><font color="#000000" size=3> -&gt; <span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Default Domain Policies -&gt; Help</span></font></span></font></span></font></li><li><font face="Times New Roman" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><font color="#000000" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><font color="#000000" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><font color="#000000" size=3><span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><span lang=EN-US style="color:blue;">Manage Domain Policies</span><font color="#000000" size=3> -&gt; <span lang=EN-US style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Default Domain Controller Policies -&gt; Help </span></font></span></font></span></span> </font></span> </font></span></font> </li></ol> |  | U4 |  |  | FINDING | [6 empty] | 122526
35921 | FINDING | 16-Channel Selectable Timeout relay modules are configured incorrectly in the module 0xC register | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2016-05-10 14:00 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-05-10 14:00 | 3.6.0_U7 / 67224 |  |  | 2016-05-10 14:00 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-03-17 09:31 |  | Two problems exist when configuring 16-Channel Selectable Timeout relay modules:<br><ol><li>Only the lower eight registers of the 0xC registers are configured.</li><li>The relay module's RM point must be touched in order for the 0xC register to be configured.</li></ol> |  |  |  | The affected area is in the software responsible for generating hardware information for RM points assigned to 16-channel selectable timeout relay modules and in the software which updates RM points based on changes to the RM points assigned hardware item (specifically the inclusion of the new Timeout Action (Latch) attribute). | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>The software which transferred the value of the 16-bit channel selectable timeout action attribute (labeled &quot;Timeout Action (Latch)&quot;) to the RM point register C Data register had mistakenly only included the lowest 8 bits.&nbsp; This will be corrected such that all 16 bits will be transferred.</p><p>The software which implicitly updates applicable RM points based on changes made to Ovation Module objects mistakenly did not include the 16-bit channel selectable timeout action attribute.&nbsp; This will be corrected such that changes to this attribute will automatically touch the assigned RM point and a subsequent load operation will result in new register C values in the loaded RM point.&nbsp; The work-around (prior to this fix) is to manually touch the RM point following a change to the module's Timeout Action (Latch) attribute.</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 96580
35926 | FINDING | Problems seen loading controller after deleting multiple points | Souders, Sarah EMR SYSS PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-06-10 11:54 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-06-10 11:54 | 67962 |  |  | 2016-06-10 11:54 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-17 13:16 |  | <p>GWS&gt; Created SDR 36764.</p><p><br></p><p>Some sheets and points were deleted from the controller and the controller was loaded successfully.&nbsp; Afterwards, some new points and sheets were added and the controller could not be loaded. Pedit error 6,7,-11 was seen from Studio (see attached files).&nbsp;&nbsp; From within the controller, it was seen that findMaxLid returned a negative number (see attached files).&nbsp; The controllers had to be cleared and loaded in order to correct this. </p><p>mp 3/18/16 - Update.&nbsp; Found that the findMaxLid is reset to zero (0) on reboot. Not sure if this should reset, but any deletes after a reboot will cause this to go negative, causing the above problem. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U8 |  | Ovation 3.6.0 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The used Lids count is now properly initialized on boot. | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Delete multiple points from a controller and load it. then add points and attempt to load the controller. |  | U4 |  |  | FINDING | [6 empty] | 98515
35929 | FINDING | OV 3.6.0 Group Policy: Windows Explorer Policies- Remove "Map Network Drive" and "Disconnect Network Drive" setting when enabled still allows the user to access "Map as drive". | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Costlow, Kim EMR SYSS PWS PITT | 2016-04-26 14:35 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-04-26 14:35 |  |  |  | 2016-04-26 14:35 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-03-17 16:53 |  | User is able to access &quot;Map as drive&quot;&nbsp;by navigating&nbsp;through Home toolbar even when &quot;Remove Map Network Drive and Disconnect Network Drive&quot; is enabled. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U4</p> <p>Windows 2012 R2</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>On DBS:<br>1) Open Ovation Security Manager in Ovation Developer Studio.<br>2) Navigate to Manage Group Policies<br>3) Open properties of Engineer/Operator user .<br>4) Navigate to Windows Explorer<br>5) Change value to Enabled.<br>6) Click on apply and Ok.<br>7) Close Ovation Security Manager<br>8) Now run gpupdate command on command prompt.<br>On EWS:<br>On Windows 2012 R2 EWS machine login with <strong>Engineer/Operator</strong> User.<br>Open Windows Explorer. <br>Navigate to &quot;Easy access&quot;in Home Toolbar.<br><strong>Observation</strong>: Map as drive option available .<br>The option allows the user to map a drive when using Domain Administrator credentials.</p> |  | U4 |  |  | FINDING | [6 empty] | 95728
35930 | FINDING | Ovation Security Manager application crashes if Secondary Domain controller is not available | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-23 00:13 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-23 00:13 |  |  |  | 2016-04-23 00:13 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-03-18 01:02 |  | Ovation Security Manager application crashes if Secondary Domain controller is not available |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <p>OV360_U4;<br>W7 EWS; Ws2012_R2; </p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>UT - 03/23/2016 -</p> <p>Here is PGH lab we tried the same scenario and didn't see the error happening. Even after shutting down the redundant domain controller, the Security Manager UI works fine (it may take a while very first time to load the properties, but will eventually show up). </p> <div>That is how OvSecManUI is suppose to work. It only needs access to PDC and does not have any reference to RDC at all.&nbsp;</div> <div><br></div> <div>On further analyzing the attached event log file, all the crashes that occurred with OvSecManUI is pointing towards a problem with accessing the C:\Windows\System32\hhctrl.ocx file, which is used to display help topics by all Ovation applications, including OvSecManUI.</div> <div>So the conclusion is that OvSecManUI crash is not related to the RDC availability, but because of hhctrl.ocx issue.&nbsp;</div> <div>To further investigate the problem:</div> <div>1. Could you please confirm whether the OvSecManUI crash is isolated to one drop and happening in all drops (with RDC offline)?</div> <div>2. Could you re-insall Ovation (may fix/repair the hhctrl.ocx) in the problematic drop and re-run the test?</div> <div>---&nbsp;</div> <div>PS 05Apr16:</div> <p>*The OSM UI would hang for several minutes and also eventviewer&nbsp;logged event for APP HANG.&nbsp;&nbsp;</p> <p>*As mentioned in steps to reproduce, yes the APPCRASH would result only on clicking the help tab. This happened only when RDC was found either in hang mode or shutdown mode. The help worked fine if RDC was healthy.</p> <p>&nbsp;</p> <p>Replies to the above query for investigation are:</p> <div>1. Could you please confirm whether the OvSecManUI crash is isolated to one drop and happening in all drops (with RDC offline)? : <strong>This happened on all the drops on the network.</strong></div> <div>2. Could you re-insall Ovation (may fix/repair the hhctrl.ocx) in the problematic drop and re-run the test?: <strong>It happened on all drops (DBS &amp;&nbsp;EWS)</strong></div> <p>&nbsp;</p> <div>PS: The RDC has experienced some hardware problem and is being recovered. The issue is not seen right now on any of the drops. This issue could be recreated or monitored only after the RDC is back and inhealthy condition.&nbsp;&nbsp;</div> <div>---</div> <div>msb - 04/19/2016 -</div> <div>In U6 - Tried both steps on PDC(Em-125) while RDC(Dave-135) is shut down.</div> <div>AppCrash or&nbsp;AppHang could not be duplicated.</div> <div>&nbsp;</div> <div>PS 23Apr16: Tried the above steps in U6 and have similar observations as Mati. Hence finding is closed as cannot duplicate in U6.&nbsp;</div> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p><span lang=EN-US style="color:blue;">Open Dev. Studio -&gt; Security -&gt; Ovation Security -&gt; Ovation Security Manager.</span></p><p><span lang=EN-US style="color:blue;">Step1&gt;&nbsp; Click on Manage Computers -&gt; Select any available computers -&gt; Open properties </span></p><p><span lang=EN-US style="color:blue;">Observation: This hangs the security manager UI; this event is logged in event viewer </span>(AppHang-OSM-Eventviewer.jpg)</p><p>Here, we kill the application and have to re-open the same.</p><p><span lang=EN-US style="color:blue;"><br></span></p><p><span lang=EN-US style="color:blue;">Step2&gt;&nbsp;Click on Manage&nbsp;Ovation Roles&nbsp;-&gt; Select any role-&gt; Open properties -&gt; Click on Help</span></p><p><span lang=EN-US style="color:blue;">Observation: This results in APPCRASH. </span></p><p><span lang=EN-US style="color:blue;">Attached are the snapshots and eventviewer files for reference</span></p> |  | U4 |  |  | FINDING | [6 empty] | 95500
35931 | FINDING | Point description(ED field) is not updating in signal diagram. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:42 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-22 10:42 |  |  |  | 2016-03-22 10:42 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-03-18 04:13 |  | <span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">It is observed that if the point description of a point, which is being used in the control logic, is modified from developer studio and loaded to controller then the modified description is not updated in signal diagram.</span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV-3.6.0_U4, EWS Drop153(W7_64bit), Controller Drop36/86.&nbsp; |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | Sheet must be compiled or saved before the controller is loaded to see the change in the signal diagram. | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3><font face=Calibri>Steps followed:</font><p> 1. Open a control sheet from signal diagram.</p><p>2. Right click on a point and select the developer studio option to open the point editor window.</p><p>3. Modify the point description.</p><p>4. Open the respective control sheet using control builder and verify the change has been reflected in the sheet.</p><p>5. Load the controller drop.</p><p>6. Now open the same control sheet in signal diagram</p><p> <span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">7. Observation: The control sheet is not updated with modified point description.</span></p></font><p><br></p> |  | U4 |  |  | FINDING | [6 empty] | 93787
35932 | FINDING | SIS Events are not appearing properly in Historical Review application | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:14 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:14 |  |  |  | 2017-02-24 07:14 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-18 07:15 |  | <p>SIS Events are not appearing properly&nbsp;in Historical Review application. Please find following observations:</p> <p>&nbsp;</p> <p><strong>Issue#1:</strong></p> <p>a. SIS Events corresponding to CSLS load start operation, gives the reference of the CSLS on which load operation is being performed. But the SIS Event corresponding to Controller load start and Controller load end operation gives the reference of the 13th CSLS <strong>D30-CSLS0013-CM01</strong> irrespective of the CSLS on which load operation has been given.</p> <p>b. There is no SIS event to notify the user of CSLS load end. </p> <p>Please see the logs below:</p> <p><font face="Courier New">03/18/2016 13:57:34&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D30-CSLS0013-CM01&gt;:&nbsp;&nbsp;Controller Load: Ended 0<br>03/18/2016 13:57:34&nbsp;DROP30&nbsp;&lt;OtherSisEvent: 0.D30-CSLS008: 0.D30-CSLS008&gt;:&nbsp;&nbsp;CSLS download Started<br>03/18/2016 13:57:34&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D30-CSLS0013-CM01&gt;:&nbsp;&nbsp;Controller Load: Started 0</font></p> <p>&nbsp;</p> <p><strong>Issue#2:</strong></p> <p>For some of the CSLSs we are observing&nbsp;LsEvents which&nbsp;are not indicative of any specific event. Please find the messages below:</p> <p><font face="Courier New">03/18/2016 13:57:36&nbsp;DROP30&nbsp;&lt;LsEvent: 0.D30-CSLS008: 0.D30-CSLS008&gt;:&nbsp;&nbsp;Set: Right unit:<br>03/18/2016 13:57:36&nbsp;DROP30&nbsp;&lt;LsEvent: 0.D30-CSLS008: 0.D30-CSLS008&gt;:&nbsp;&nbsp;Set: Left unit:</font></p> <p><font face="Courier New"></font>&nbsp;</p> <p><strong>Issue#3:</strong></p> <p>Some of the SIS Events take reference of Control Module#1 Node point alongwith the reference of the CSLS's node point against which the SIS Event is generated. Please see the message below for reference:</p> <p><font face="Courier New">03/18/2016 16:47:50&nbsp;DROP30&nbsp;&lt;Hac: D30-CSLS0013: <strong>D30-CSLS0013-CM01</strong>&gt;:&nbsp;&nbsp;Set:&nbsp;CSLS is not communicating</font></p> <p><font face="Courier New"></font>&nbsp;</p> <p><strong>Issue#4:</strong></p> <p><em>'VOTERx Voting to Trip'</em> and <em>'Analog/Digital Voter Tripped/Not Tripped'</em>&nbsp;SIS Events (SifModule Type)&nbsp;contain incorrect Control Module Information in Historical Review application. If LSAVTR and LSDVTR algorithms are present&nbsp;in&nbsp;Control Module#x, then the listed Control Module in these SIS Events is Control Module#(x+1). Please see the examples below for reference:</p> <p><font face="Courier New">03/20/2016 14:22:39&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS007-CM04: CM4: OCBC000002&gt;:&nbsp;&nbsp;VOTER1 voting to trip<br>03/20/2016 14:22:39&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS007-CM04: CM4: OCBC000002&gt;:&nbsp;&nbsp;Digital Voter Tripped</font></p> <p>Here this LSDVTR algorithm with LC Record OCBC000002 is present in CM#3 in actual while here the listed Control Module is CM#4.</p> <p>&nbsp;</p> <p><strong>Issue#5:</strong></p> <p><em>SifAlerts</em> and <em>OtherSisEvents</em> pick up the name of CSLS's First Control Module node point name instead of the CSLS for which SIS events/SifAlert is generated. Please see the example for reference:</p> <p><font face="Courier New">03/20/2016 15:22:25&nbsp;DROP30&nbsp;&lt;OtherSisEvent: <strong>D30-CSLS0013-CM01</strong>&gt;:&nbsp;&nbsp;Standby Controller is Available</font></p> <p><font face="Courier New">03/20/2016 15:24:19&nbsp;DROP30&nbsp;&lt;SifAlert: <strong>D30-CSLS007-CM01</strong>: CM3&gt;:&nbsp;&nbsp;Set:&nbsp;Trip consensus in an AVTR or DVTR block</font></p> <p>&nbsp;</p> <p><strong>Issue#6:</strong></p> <p>Power Failure messages related to CSLS units do not contain <em>&lt;param1&gt;</em> parameter indicating the duration of Power Failure in seconds.</p> <p><font face="Courier New">03/19/2016 16:47:04&nbsp;DROP30&nbsp;&lt;LsEvent: D30-CSLS004: D30-CSLS004-CM01&gt;:&nbsp;&nbsp;Power failure occured for Left unit: <strong>seconds</strong></font><font face="Courier New"><br></p></font> <p><strong>Issue#7:</strong></p> <p>Some of the SIS Events are followed by wrong and additional Timestamp after the message. </p> <p><font face="Courier New">03/17/2016 10:51:25&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS004-CM02: CM2: 0x0&gt;:&nbsp;&nbsp;VOTER1 voting to trip <strong>03/15/2016 05:51:06</strong></font></p> <p><font face="Courier New">03/23/2016 14:56:02&nbsp;DROP30&nbsp;&lt;Hac: D1_VCSLS3: D1_VCSLS3&gt;:&nbsp;&nbsp;Cleared:&nbsp;Proof-test reminder is Active <strong>03/23/2016 00:10:44</strong></font></p> <p><strong><font face="Courier New"></font></strong>&nbsp;</p> <p><strong>Issue#8:</strong></p> <p>Sometimes SifModule Events show zeroed SIDs for the Algorithm, while sometimes they show up correctly.&nbsp;Please see the example below:</p> <p><font face="Courier New">04/14/2016 11:17:36&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS003-CM02: CM2: <strong>0x0</strong>&gt;:&nbsp;&nbsp;VOTER2 voting to trip<br>04/14/2016 11:17:36&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS003-CM02: CM2: <strong>0x0</strong>&gt;:&nbsp;&nbsp;VOTER1 voting to trip</font></p> <p><font face="Courier New">04/14/2016 10:48:39&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS003-CM02: CM2: <strong>0x80011360</strong>&gt;:&nbsp;&nbsp;VOTER2 voting not to trip<br>04/14/2016 10:48:39&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS003-CM02: CM2: <strong>0x80011360</strong>&gt;:&nbsp;&nbsp;VOTER1 voting not to trip</font></p> <p><font face="Courier New"></font>&nbsp;</p> <p><strong>Issue#9:</strong></p> <p>CM Partial Download SIS Event messages appear CSLS#2 and CSLS#4 when the load operation is being performed on CSLS#3. Please see the reference of SIS Events below:</p> <p><font face="Courier New">04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_IOIC5&gt;:&nbsp;&nbsp;Controller Load: Ended<br><strong>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS4: D1_VCSLS4&gt;:&nbsp;&nbsp;CM partial download<br>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS2: D1_VCSLS2&gt;:&nbsp;&nbsp;CM partial download</strong><br>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS3: D1_VCSLS3&gt;:&nbsp;&nbsp;CSLS download Succeeded<br>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS3: D1_VCSLS3&gt;:&nbsp;&nbsp;CSLS download Started<br>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS3: D1_VCSLS3&gt;:&nbsp;&nbsp;CM partial download<br>04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_IOIC5&gt;:&nbsp;&nbsp;Controller Load: Started</font></p> <p>It was seen multiple times and it was made sure that no operation was being performed on CSLS#2 and CSLS#4.</p> <p>&nbsp;</p> <p><strong>Issue#10:</strong></p> <p>LsEvents, Hac Events and OtherSisEvents show multiple reference of the originating CSLS from which Events are generated.</p> <p><font face="Courier New">04/14/2016 14:38:06&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_VCSLS3: D1_VCSLS3&gt;:&nbsp;&nbsp;CM partial download</font></p> <p><font face="Courier New">04/14/2016 11:18:41&nbsp;DROP30&nbsp;&lt;LsEvent: D1_VCSLS12: D1_VCSLS12&gt;:&nbsp;&nbsp;Set: Left unit:&nbsp;CSLS secondary network Error</font></p> <p><font face="Courier New">04/14/2016 11:18:21&nbsp;DROP30&nbsp;&lt;Hac: D1_VCSLS1: D1_VCSLS1&gt;:&nbsp;&nbsp;Set:&nbsp;CHARM Error</font></p> <p>&nbsp;</p> <p><em>Note:</em> </p> <p>1. Even if D30-CSLS0013 is powered off, still Controller load related SIS Events give reference of D30-CSLS0013-CM01.</p> <p>2. Please find attached printErrorBuffer logs of SIS Controller Drop30 (in Control) and Historical Review data (SIS Events).</p> |  |  |  | This Finding was partially resolved, all unresolved issues are tracked by separate SDRs<br> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>SIS Controller Drop30/80</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>In total, 13 CSLSs have been configured and commissioned on the setup. (D30-CSLS001-D30-CSLS0013)</font></span></p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | #7 is not a issue, the timestamp shows that this is past issue - this timestamp is only displayed if it is significant different from Historian timestamp. If the events should have same timestamp as historian, then this may be a problem with time synchronization of CSLSs<br>#2, #4 should be fixed in u5<br> | 16 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Perform load operation on any CSLS.</p> <p>2. Open Historical Review application and observe the corresponding SIS Events.</p> |  | U4 |  |  | FINDING | [6 empty] | 109265
35936 | FINDING | Update OW360_60 manual regarding loading of backup Controller. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-26 01:58 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-26 01:58 | 67256 |  |  | 2016-05-26 01:58 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-03-18 14:18 |  | In the topic, &quot;To load a Controller (for a redundant I/O module),&quot; it states that you should load the Secondary / Backup Controller first. According to KBA 240, this is incorrect. You should always load the Controller that is in control first. |  |  |  | <p>MG 18/04/2016: According to this finding, updated the point no. 6 of the <strong>Section 10.4.7 To load the Controller (for a redundant I/O module)</strong> of the Developer Studio User Guide for 3.6.0. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp; <a href="file://\\USPIT-FP05\Ohara\Communication\TechComm\Share\For">\\USPIT-FP05\Ohara\Communication\TechComm\Share\For</a> Megha Ovation 3.6.0 manuals\Manuals\Developer Studio User Guide (OW360_60)\OW360_60.pdf</p><p>Online help: <a href="file://\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a><br></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Morgan, James EMR SYSS PWS PITT | Garg, Amit AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation | 3.6.0_U6 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Development |  | MG 18/04/2016: This finding has been fixed and is available in U6 build. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 97782
35937 | FINDING | Update OCR 400 and OCR1100 manuals in regard to load order | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-26 01:57 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-26 01:57 | 67256 |  |  | 2016-05-26 01:57 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-03-18 14:21 |  | Add a note to both OW360_54 and OW360_58 manuals that explicitly states that you should always drop load the Controller that is in control first. |  |  |  | <p>MG 18/04/2016: According to this finding, added a note after point no. 5 in the <strong>Section&nbsp;4.3.3 To load a Controller&nbsp;drop</strong>&nbsp;of the Controller (OCR 1100) and Controller (OCR 400) User Guide for 3.6.0. </p><p>This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp; </p><p>OCR 1100 - <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: <a href="file://uspit-fp04/SourceIntegrity/TechWriters/3.6.0CHMs/OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Garg, Amit AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U6 |  |  |  | Ovation for Windows | Ovation | Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Documentation |  | <p>MG 19/04/2016: This finding has been fixed and is available in U6 build.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 97781
35938 | FINDING | Add troubleshooting information to Controller manuals | Gola, Megha EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Gola, Megha EMR SYSS PWS NOIDA | 2016-05-30 03:27 | [11 empty] | Gola, Megha EMR SYSS PWS NOIDA | 2016-05-30 03:27 | 3.6.0_U8 |  |  | 2016-05-26 04:52 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-03-18 14:47 |  | <p>Based on KBA 1233, a procedure must be written regarding a <span id=KB.D.V.R1.TITLE>Controller Failure During Drop Load Operation.&nbsp; This procedure is documented in KBA 1233, and given in a Word document that is attached to this finding.&nbsp; Please update OW360_54 (OCR400) and OW360_58 (OCR1100) manuals.</span></p><p><span><br></span></p> |  |  |  | <p>MG (April 26, 2016): According to this finding, added the&nbsp;<strong>Section 4.3.4 To recover from a Controller failure during a drop load operation&nbsp;in</strong> the Controller (OCR 400 and 1100) user guide for Ovation 3.6. This is available in online help for U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2016): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p><p><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">MG (May 30, 2016): This will be fixed in Ovation feature pack. Create SDR for this.<br></span></p> | 0 |  |  |  | <span style="color:rgb(34, 34, 34);">MG (May 30, 2016): This will be fixed in Ovation feature pack. Create SDR for this.</span> | 0 |  | Ovation for Windows/Controller/General/Documentation | <p>MG (April 26, 2016): According to this finding, added the&nbsp;<strong>Section 4.3.4 To recover from a Controller failure during a drop load operation&nbsp;in</strong> the Controller (OCR 400 and 1100) user guide for Ovation 3.6. This is available in online help for U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2016): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 30, 2016): This will be fixed in Ovation feature pack. Create SDR for this.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Morgan, James EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation | 3.6.0 |  |  |  | Ovation for Windows | Ovation | Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Documentation |  | <p>MG (April 26, 2016): This finding has been fixed and is available in U7 build.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 97963
35946 | FINDING | "Enable automatic proof test to run at reminder time" option in Proof Testing tab is not disabled for Simplex Charms Smart Logic Solver | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-22 07:35 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-22 07:35 | 3.6.0_U7 |  |  | 2016-05-22 07:35 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-21 03:45 |  | <p>&quot;Enable automatic proof test to run at reminder time&quot; option in Proof Testing tab is not disabled for Simplex Charms Smart Logic Solver. </p> <p>According to the online help </p> <p>&quot;<font size=2>Enable automatic proof test to run at reminder time‖ check box (this check box is grayed-out for simplex CHARMs Smart Logic Solvers). &quot; </font></p> <p><font size=2>Please see the attached screenshot of the online help on Automatic Proof Testing.</p></font> |  |  |  | <p>MM(4/27/16): Check the <span lang=EN-US><strong><em><font face=Arial size=2>CHARMs Smart Logic Solver attributes in Proof Testing tab </font></em></strong></span>table in the section 4.10.3 and the section 5.18.1&nbsp;in the pdf (<strong>OW360_43-25_Apr</strong>) at the following location:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a></p><p style="margin:12pt 0cm 6pt;"><span lang=EN-US><strong><em><font face=Arial size=2><br></font></em></strong></span></p><font face="Times New Roman" size=3> </font> | 0 |  |  |  | Working Fine in 3.6.0_U9. Closing the Finding. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software | <p>MM(4/27/16): Check the <span lang=EN-US><strong><em><font face=Arial size=2>CHARMs Smart Logic Solver attributes in Proof Testing tab </font></em></strong></span>table in the section 4.10.3 and the section 5.18.1&nbsp;in the pdf (<strong>OW360_43-25_Apr</strong>) at the following location:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation | 3.6.0 |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>After reviewing both the 1508 and CSLS, we believe they both operate the same way.&nbsp; The fields are not disabled for either when configured as simplex.</p> <p><br></p> <p>If you find otherwise, let me know.&nbsp; This may require a documentation update.</p> <p>&nbsp;</p> <p>PA 03/28/2016: According to FINDING#29693, same behaviour is observed for 1508 as well.</p><p><br></p><p>DOCUMENTATION UPDATE:</p><p>Please Update the SIS documentation to warn users against configuring the &quot;Automatic Proof Testing&quot; for simplex logic solvers (Both the 1508 and CSLS)</p> | 12 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open Ovation Developer Studio and go to SIS Controller Drop --&gt; I/O Devices --&gt; I/O Device Ovation SIS CHARMs --&gt; LSN --&gt; SIS CHARM Logic Solvers</p> <p>2. Right click on the simplex CHARMs Smart Logic Solver.</p> <p>3. Go to Proof Testing tab.</p> |  | U4 |  |  | FINDING | [6 empty] | 97414
35947 | FINDING | CHARMs Smart Logic Solver Control Module RN point's information in the document is incomplete and incorrect | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-21 05:17 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-21 05:17 |  |  |  | 2016-03-21 05:17 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-21 04:04 |  | <p>CHARMs Smart Logic Solver Control Module RN point's information in the document is incomplete and incorrect. </p> <p>According to Online help, Bit#0, Bit#1, Bit#11 and Bit#12 shows information related to Control Module Registration, Debug mode, Active SIF Error and Active SIf Alert respectively and other bits are ununsed. While in Point Information application, these bits show different status corresponding to each bit from Bit#0 to Bit#7 and rest of the bits are unused.</p> <p>Please see the attached screenshots of Point Information application and Online help for showing Control Module RN point.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"> <p class=MsoNormal style="MARGIN:0cm 0cm 10pt;LINE-HEIGHT:18pt;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on&nbsp;Workstation Drop155&nbsp;(OS: Windows 7 Professional, Service Pack1)&nbsp;</span></p></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | PA: 3/21/2016: Closing the Finding as there has been linking issue with the online help which is tracked through another Finding#35910 | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 93660
35948 | FINDING | Error message is received if CSLS is cleared when 1 controller is powered off | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Morris, Gilbert L AUTOSOL PWS PITT | 2016-04-25 07:45 | [11 empty] | Morris, Gilbert L AUTOSOL PWS PITT | 2016-04-25 07:45 |  |  |  | 2016-04-25 07:45 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-21 04:40 |  | Error message is received if &nbsp;a CSLS is cleared when 1 controller is powered off. But CSLS gets cleared as when tried to clear again it gives a message that CSLS is already cleared.<div>Error Message received:</div><div>Load Controller encountered a problem</div><div>Communication Failure connecting to controller for DROP80</div><div>Unable to find controller&nbsp;</div><div><b>Note:</b> Drop 80 is the controller powered off in the above case.<br></div><div>Please refer to attached screenshot</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | This is not a critical error.&nbsp; The Ovation Developer Studio - Alert box is not an error condition in this instance, but merely a reporting mechanism and requires the user to perform some investigation as to what exactly went wrong.&nbsp; The fact that you turned off DROP80 and received&nbsp;the &quot;Communication Failure connecting to DROPx&quot; will require a user to investigate whether or not the Controller is in a healthy/loadable state.&nbsp; In the case described above, DROP80 was turned off and the software tried to inform the controller of a CSLS Configuration Change.&nbsp; We cannot handle the &quot;... controller is offline and proceed ...&quot; as we do during a load operation because they follow different paths. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>This is because OvPtStudio is trying to send CSLS &quot;LoadController&quot; command to both drops regardless of their states and displaying error when any of those does not respond. However the clear operation succeeds in such case.</p><p>It should display warning that the backup controller is offline and proceed with load of only active drop, as it is done in case of load operation.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Power off a Controller (Primary or Partner).</li><li>Clear a CSLS.</li><li>Error message is received.</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 95584
35949 | FINDING | Bit description of SIS I/O Device Charms RN point should be available in Point Information application value tab | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:02 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-21 08:02 |  |  |  | 2016-03-21 08:02 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-21 04:55 |  | <p>Bit description of SIS I/O Device Charms RN point&nbsp;should be&nbsp;available in Point Information application value tab. </p> <p>Please see the attached screenshot of Point Information application.</p> <p><em>Note: Bit description of SIS I/O Device Charms RN point in Point Information application value tab is supported in Ovation 3.5.2</em></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | Bit description are only provided when the point is created from the within the CSLS edit.&nbsp; If the point already exists and is just associated with CLSL, the bit descriptions are not updated. | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U4 |  |  | FINDING | [6 empty] | 93686
35951 | FINDING | Unable perform Force operation and Debug On/Off control Module when Partner Controller is in Control | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-16 03:31 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-16 03:31 | 66859 |  |  | 2016-04-16 03:31 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-21 05:14 |  | When Partner Controller is in control it is not possible to perform Force, Debug On/Off operation on CSLS.<div>Case I : Primary in Backup, Partner in Controller</div><div>An error stating &quot;OVSIS_ERROR_SERVER_OFFLINE&quot; is received when Force or Debug On/Off is performed.</div><div><br></div><div><div>Case II : Primary off, Partner in Controller</div><div>An error stating &quot;OVSIS_ERROR_SOCKET&quot; is received when Force or Debug On/Off is performed.</div></div><div><br></div><div>Please refer to attached screenshots</div> |  |  |  |  | 0 |  |  |  | The finding is fixed and has been verified in 3.6.0 + U6 | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | There was a problem finding out that the target of secure write is a drop. Check was failing because of case sensitivity. The problem is resolved now. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation | U5 |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | The problem has been resolved. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>CASE I:</div><ol><li>Put Primary Controller in Back up and Partner Controller in Control</li><li>Perform a Force, Debug On/Off &nbsp;operation.</li><li>Error message appears unable to perform the desired operation. &nbsp;</li></ol><div><div>CASE II:</div><ol><li>Power off Primary Controller and Partner Controller in Control</li><li>Perform a Force, Debug On/Off &nbsp;operation.</li><li>Error message appears unable to perform the desired operation. &nbsp;</li></ol></div> |  | U4 |  |  | FINDING | [6 empty] | 95087
35952 | FINDING | Coefficient Calculation for Thermocouple should be consistent for all type of thermocouple CHARMS | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Swartz, Mark EMR SYSS PWS PITT | 2016-04-04 15:57 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-04-04 15:57 |  |  |  | 2016-04-04 15:57 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-21 06:45 |  | <div>Developer Studio does not allow to calculate coefficients for these Thermocouple CHARMS: Type B Thermocouple Input,&nbsp;Type E Thermocouple Input,&nbsp;Type J Thermocouple Input,&nbsp;Type K Thermocouple Input,&nbsp;Type N Thermocouple Input,&nbsp;Type R Thermocouple Input,&nbsp;Type S Thermocouple Input,&nbsp;Type T Thermocouple Input. &nbsp;It gives a message &quot;Conversion coefficient calculation not applicable for SIS I/O CHARM Functionality configuration: &quot;SIS_CHMIO_TC_J_CHAN&quot;&nbsp;&quot; and the coefficient are manually put by the user.</div><div><br></div>Developer Studio should not allow Coefficient caluclation for rest of the 3 type of Thermocouple CHARMS also, Because these Thermocouple CHARMS calculate coefficient&nbsp;using linear Conversion instead of&nbsp;5th order Polynomial equation. hence the coefficient calculated are not correct and of no use. The above message should appear for these CHARMS as well and coefficients have to be put manually by the user. The Thermocouple CHARMS type are:<div><ol><li>+/- 20 mV</li><li>+/- 50 mV</li><li>+/- 100 mV</li></ol></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>Works per design.&nbsp; The&nbsp;three mV versions of this CHARM class are for generic millivolt inputs and are not necessarily intended for use as a temperature reading.</p><p>The coefficient calculation software is intended to provide linear coefficients for these millivolt type versions.&nbsp; The population of 5th order for thermocouples is not included -- nor will it be.</p><p>Note that the user can always specify their own coefficients for any of these inputs.</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Select any of the 3 types of thermocouple CHARMS mentioned above.</li><li>Calculate Coefficient automatically.</li><li>It calculates coefficient with linear equation</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 94365
35957 | FINDING | Clear CSLS does not delete SisEmbedded#.csis file from the controller | Daly, Joshua D EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:39 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:39 |  |  |  | 2017-02-16 15:39 |  |  |  | Zochowski, Michal AUTOSOL DX WRSW | 2016-03-21 10:58 |  | While clearing the CSLS, LoadDone message is sent with no change in files. The cleared csls' SisEmbedded#.csis file should be deleted.<br><br>This issue is related to LOAD_DONE flag that is send by the studio to the controller. It sends&nbsp;flags indicating that both, SisAssign and SisEmbedded script should be saved on the flash. But only SisAssign should remain for the drop being cleared.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Zochowski, Michal AUTOSOL DX WRSW | Development |  | IC 2/16/17&gt; entered SDR #38707 to track this issue, closed Finding. | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 108981
35964 | FINDING | Ov3.6.0_Unable to reboot DeviceNet module from Controller Diagnostics | Souders, Sarah EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-13 10:58 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-13 10:58 |  |  |  | 2016-04-01 10:33 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-03-21 15:55 |  | <p>Unable to reboot DeviceNet module from Controller Diagnostics. </p> <p>&nbsp;</p> <p>When trying to reboot the module from Controller Diagnostics a window opens mentioning &quot;Reboot request failed: script file missing&quot;</p> <p>Please see the screenshot attached.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U4 |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1) Open Controller Diagnostics.</p> <p>2) Navigate to DeviceNet Module.</p> <p>3) Right click on the module.</p> <p>4) Click on reboot.</p> <p>&nbsp;</p> <p>Observation: An error window opens mentioning &quot;Reboot request failed: script file missing&quot;</p> |  | U4 |  |  | FINDING | [6 empty] | 94858
35965 | FINDING | MASTATION- PRLI parameter is not working correctly when configured as NO. | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-21 23:18 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-21 23:18 | [7 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-21 22:11 |  | <p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><font face="Times New Roman">Manual OW351_R1100, MASTATION-Mode Transfers, page 306 says&nbsp;“If the LI interface is selected and RLI priority (PRLI) is NO, then the algorithm changes the RLI card mode from local to the last mode before the card is powered down. The LI analog output value is initialized to the last output value before the card was powered off”.</font></span></p><p style="margin:12pt 0in;"><span style="font-size:11pt;"><font face="Times New Roman"><span style="">&nbsp;</span>For testing above statement we configured&nbsp;RLI priority (PRLI) as NO in the MASTATION of Drop32/82&gt;Task2&gt;sheet 151 in PGH. And performed below steps-</font></span></p><p style="text-indent:-0.25in;margin-left:0.5in;"><span style="font-size:11pt;"><span style=""><font face="Times New Roman">1.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Start with MA station in auto and a setpoint value of 33.</font></span></p><p style="margin-left:0.5in;"><span style="font-size:11pt;"><font face="Times New Roman">Slim shows Auto with value of ~33.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">2.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Put MA station in manual – Change output value of 44.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><font face="Times New Roman">Slim shows manual with value ~44.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">3.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Remove card.&nbsp;&nbsp;&nbsp;&nbsp; </font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><font face="Times New Roman">Slim goes “Down” and MA station stays at manual mode with output of 44</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">4.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Reinsert card.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><font face="Times New Roman">Slim goes to local mode with value of ~44</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-size:11pt;"><font face="Times New Roman">MA station goes to Local Mode with value of 44.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=3><br></font></span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font size=3>However with above reference of manual I understand that, with configured RLI priority-NO, at step-4 the MASTATION and SLIM both should have come in Manual mode with value=44 (As the last mode was Manual before module was re-seated). </font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | <p><font size=3><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">Ov 3.6.0, </span>Drop32/82(Emily network)&gt;Task2&gt;sheet 151 in PGH. </font></p><p><font size=3>RLI and Slim configured to <span style="font-size:11pt;"><font face="Times New Roman">Drop32/82, Branch 6, slot 6</font></span><font face="Times New Roman"> </font></font></p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps are :</p><p>1&gt; <font size=3>configured&nbsp;RLI priority (PRLI) as NO in the MASTATION of Drop32/82&gt;Task2&gt;sheet 151 in PGH</font></p><p><br></p><font size=3><p>2&gt;<font size=1> </font><font face="Times New Roman"><span style="font-size:11pt;">Start with MA station in auto and a setpoint value of 33.</span></font><span style="font-size:11pt;"></span></p><p style="margin-left:0.5in;"><span style="font-size:11pt;"><font face="Times New Roman">Slim shows Auto with value of ~33.</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">3&gt;</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Put MA station in manual – Change output value of 44.</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><font face="Times New Roman">Slim shows manual with value ~44.</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">4&gt;</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Remove card.&nbsp;&nbsp;&nbsp;&nbsp; </font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><font face="Times New Roman">Slim goes “Down” and MA station stays at manual mode with output of 44</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><span style=""><font face="Times New Roman">5&gt;</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="font-size:11pt;"><font face="Times New Roman">Reinsert card.</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><font face="Times New Roman">Slim goes to local mode with value of ~44</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:11pt;"><font face="Times New Roman">MA station goes to Local Mode with value of 44.</font></span></p></font><p><br></p><p>However, at step-4 the MASTATION and SLIM both should have come in Manual mode with value=44 </p> |  | U4 |  |  | FINDING | [6 empty] | 93722
35970 | FINDING | SDR 34964 Failed (RR 35869 ) : "Ov.3.5.2 + OVA352001: Wrong Control module no.s is displayed in SIF module messages" | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-13 09:43 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-13 09:43 | 67095 | [6 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-22 05:35 |  | SDR 34964 (RR 35869) failed in 3.6.0 U4.<div><span style="font-family:Calibri, sans-serif;font-size:14.6667px;">Control module in SIF Alert and SIF module do not match, the control module nos displayed in SIF module message is wrong.</span><div><br></div><div><div><div>Observation:</div></div><div><ol><li>Control Module of SIF Alert and SIF module does not match. SIF alert has control module as 1(Correct), but SIF module has control &nbsp;module as 2 (Incorrect).&nbsp;</li><li>Control Module of SIF module messages should be 1.</li></ol><div><b>Logs:</b></div><div><div><i>03/22/2016 10:09:30<span class=Apple-tab-span style="white-space:pre;"> </span>DROP30<span class=Apple-tab-span style="white-space:pre;"> </span>&lt;SifAlert: D30-CSLS004-CM01: CM1&gt;:<span class=Apple-tab-span style="white-space:pre;"> </span>Set:<span class=Apple-tab-span style="white-space:pre;"> </span>Trip consensus in an AVTR or DVTR block</i></div><div><i>03/22/2016 10:09:28<span class=Apple-tab-span style="white-space:pre;"> </span>DROP30<span class=Apple-tab-span style="white-space:pre;"> </span>&lt;SifModule: D30-CSLS004-CM02: CM2: OCBC02900C&gt;:<span class=Apple-tab-span style="white-space:pre;"> </span>VOTER2 voting to trip</i></div><div><i>03/22/2016 10:09:28<span class=Apple-tab-span style="white-space:pre;"> </span>DROP30<span class=Apple-tab-span style="white-space:pre;"> </span>&lt;SifModule: D30-CSLS004-CM02: CM2: OCBC02900C&gt;:<span class=Apple-tab-span style="white-space:pre;"> </span>Analog Voter Tripped</i></div><div><i>03/22/2016 10:08:36<span class=Apple-tab-span style="white-space:pre;"> </span>DROP30<span class=Apple-tab-span style="white-space:pre;"> </span>&lt;SifModule: D30-CSLS004-CM02: CM2: OCBC02900C&gt;:<span class=Apple-tab-span style="white-space:pre;"> </span>VOTER1 voting to trip</i></div></div></div></div></div> |  |  |  |  | 0 |  |  |  | Unable to test SIS Events in U7 and Finding cannot be verified. Finding F#36492 &nbsp;has been raised by PA against SIS Events. | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation | U5 |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>Steps:<br></div><div><div><ol><li>Create a SIS Alert (LSDVTR/LSAVTR &nbsp;created in Control Module 1 are tripped).<br></li><li>2 SIF module and 1 SIF alert message related ton the trip appear in SIS tab of historical review application.<br></li><li>Check the Control &nbsp;Module for SIF Alerts and SIF module messages.</li></ol></div></div> |  | U4 |  |  | FINDING | [6 empty] | 96829
35971 | FINDING | Unable to browse points( LP, DP and RN) created in a Controller Drop in PI application from Workstations | Swartz, Mark EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-30 11:04 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-30 11:04 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-22 06:51 |  | The issue is very&nbsp;<span style="font-size:11.0pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;color:#1F497D;">inconsistent and occurs only some times.</span><div><span style="color:rgb(31, 73, 125);font-family:Calibri, sans-serif;font-size:11pt;">When a point is created in controller and controller drop is loaded, It is not possible to browse the point in PI from a Workstation. It is possible to browse the point from PI of Database Server.</span><br></div><div><b style="font-size:14.6667px;color:rgb(31, 73, 125);font-family:Calibri, sans-serif;">Workaround:</b><span style="font-size:14.6667px;color:rgb(31, 73, 125);font-family:Calibri, sans-serif;">&nbsp;</span><br></div><div><font color="#1f497d" face="Calibri, sans-serif"><span style="font-size:14.6667px;">After performing clear and load operation on each workstation it is possible to browse the point in PI from the respective workstation.</span></font></div><div>Till now the behaviour has been observed in LP, DP and Node points.</div> |  |  |  |  | 0 |  |  |  | Issue has not been observed in 3.6.0 U9 till now. | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirming Issue is Resolved | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | More information required:&nbsp; When PI on the workstation is unable to browse the point on the workstation (but PI on the database server is able to), is the workstation fully distributed?&nbsp; Are there DB_XMIT type errors on the workstation's Ovation Error Log?&nbsp; When the problem occurs, is it for all non-database server workstations or only one?<div><br></div><div>SHS 3/28/2016&gt; Yes the workstation was fully distributed. When the problem occurred it was checked in 3 non - database server &nbsp;workstation and it was for all 3. Ovation Error log was not checked previously and since the issue is inconsistent I was unable to reproduce it after trying, so cannot comment of DB_XMIT &nbsp;type errors, but will update about it when the issue is recreated.</div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Create a LP, DP or Node point in controller drop.</li><li>Load the controller drop</li><li>Try to browse &nbsp;the point created in PI application from a Workstation</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 97984
35972 | FINDING | Online Logic sheets with macros and symbols are printing with missing descriptions. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-28 13:08 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-03-28 13:08 |  |  |  | 2016-03-28 13:08 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-03-22 07:41 |  | <span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Online Logic sheets with macros and symbols are printing with missing descriptions.</span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><br></p><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation Release: - Ov 3.6.0</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Used build:- OV 3.6.0_U4</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>OCR Controller: - OCR 1100 G02</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Network: - Net#36</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>DBS Drop: - Drop100</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | <p>This appears to have worked this way from the beginning.&nbsp; The Z-order of rectangles appear to be on top of the text.&nbsp; Rectangles are solid in the current pdf generator.&nbsp; </p><p><br></p><p>The symbol can be corrected by using the object hierarchy panel.</p><ol><li>Select all the text by Ctrl-LeftMouseButton </li><li>Use the move button until the text is between the rectangles and the control pins.</li></ol><p>This must be done on every control sheet where the symbol was inserted.<br></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><b style=""><font face=Calibri size=3>Steps Followed:-</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- Import all control sheets, symbols and control macros.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Note:- All control sheets, symbols and control macros are attached with this finding.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Create all the undefined points.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- Compile all the sheets, macros, symbols and load the controller.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>4:- Open the above loaded sheets in signal diagram and print the sheet into pdf by using CutePDF </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Writer. See attached file “Sheet-printout-issue.pdf” and “descriptions-as-seen-in-signal-diagram.jpg”</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>It is observed that the print is coming incomplete with missing descriptions inside the macro symbol. See attached file ”sheets printout issue.pdf”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Note:- </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- Same issue has been observed when using the XPS printer.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Same issue has been observed on Ov 3.5.1 release also.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- This issue is also reported from one of the customer sites.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 93934
35975 | FINDING | Ovation Net Device-Configuration Tool of sycon for Profibus or DeviceNet module configuration shows wrong ovation version information | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-30 22:11 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-30 22:11 |  |  |  | 2016-03-30 22:11 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-23 00:55 |  | It has been observed that Ovation Net Device configuration tool for PROFIBUS and DEVICENET module configuration shows wrong version information of OCR400TCP driver. Please check the attached snapshot. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab, Ov3.6.0_U4, </p><p>OCR400 (G03_IOIC):Drop24/74</p><p>EWS195</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>How do you know this is incorrect? What is the correct version number?</p><p><br></p><p>ST(03/30/2016): Rechecked version number for OCR400TCP driver which shows 3.6.0.5129 for Ovation3.6.0. hence we thought 5129 might be an unwanted number. We also checked on older Ovation release (3.5.1 &amp; 3.5.2) which shows OCR400TCP driver version number as 1.0.0.0,&nbsp;therefore OCR400TCP driver version number may not be related to particular ovation release. In view of this please advice whether finding should be closed.</p><p><br></p><p>Yes, I think this should be closed.</p><p><br></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please check the attached snapshot. |  | U4 |  |  | FINDING | [6 empty] | 94120
35976 | FINDING | Changing Node point associated with slave device or segment ports will cause all process points to go bad | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-30 04:38 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-30 04:38 |  |  |  | 2016-03-30 04:38 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-03-23 01:01 |  | It has been observed that If NODE point associated with a PRODFIBUS module segment (P01 or P02) or PROFIBUS Slave Device is changed, then after loading the controller process points associated with&nbsp; the same PROFIBUS module (both segments P01 and P02) and also points associated with the other PROFIBUS module (both segments P01 and P02) go to bad quality. To restore&nbsp; process points to Good quality, the controller has to be cleared and loaded. The same behaviour has been observed with DEVICENET module also. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | <p>If rebooting the controller does not solve the problem then this is a configuration issue and not a driver issue.</p><p><br></p><p>ST(03/30/2016): Rebooting the controller solves the problem, so closing this finding.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab, Ov3.6.0_U4, </p><p>OCR400 (G03_IOIC):Drop24/74</p><p>EWS195</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configured a PROFIBUS module at position 1.1.1 of controller drop 24/74, and attached a WAGO device to its segment P01. Configured&nbsp;process points to this WAGO device and checked that they are in good quality.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>2. Configured a PROFIBUS module at position 1.1.5 of controller Drop 24/74, configured&nbsp;WAGO devices on&nbsp; segments P01 and P02.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>3. Now changed the node point associated with the WAGO device configured at segment P02 of Profibus module located at position 1.1.5 of controller 24/74.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>4. Loaded controller drop24(in control). After loading completes WAGO device Process point associated with all the PROFIBUS module segments&nbsp;goes bad (position 1.1.1 and 1.1.5).&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;5. To get back the points in good quality again controller needs to be cleared and loaded.</p> |  | U4 |  |  | FINDING | [6 empty] | 94029
35981 | FINDING | PWTTS - System doesn't report alert for missing redundant cable(s) after FF module reboot | Plymire, Alvan AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Rick P EMR SYSS PWS PITT | 2016-03-30 10:20 | [11 empty] | Brown, Rick P EMR SYSS PWS PITT | 2016-03-30 10:20 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-03-23 11:46 |  | <p>When setup fieldbus module for redundant option with redundant cross cable missing, alert will clear out and never report again if modules are reboot.</p><p>Redundancy capability is completely loss when cable is missing.</p><p>See attached for details.</p><p><br></p><p>This issue existed in previous version 3.5.1 with minor behavior different mentioned in the attachment.</p><p><br></p><p>Also see another scenario reported in Finding# 28455 (in 3.3.1) where both cables removed. &nbsp;Alert cleared on both modules when only 1 cable reconnected. &nbsp;Issue was reproducible on both 3.5.1 and 3.6.0</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | See attached for steps to reproduce. |  | U3 |  |  | FINDING | [6 empty] | 94075
35983 | FINDING | In Alarm Historical Review: Value tab is showing only 8 characters of RS and ST field of digital point. | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | McMaster, James External Artech | 2016-03-23 14:45 | [11 empty] | McMaster, James External Artech | 2016-03-23 14:45 |  |  |  | 2016-03-23 14:45 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2016-03-23 14:36 |  | In Alarm Historical Review, Value tab is showing only 8 characters of RS and ST field (out of 12 character string) for a &nbsp;digital point.&nbsp;<div>Please see the attached snapshot comparing the Actual Set &amp; Reset description (RS and ST field) of digital point with retrieved alarm historical &nbsp;data.&nbsp;</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U4<div>Drop Name: Drop126 (OPH Scanner + EWS) EMILY</div><div>OS: Win 7 64 bit</div> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | closing since this is duplicate of finding 35983 | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Historical review application --&gt; Alarm Tab --&gt; Retrieve alarm for digital point having 12 character&nbsp;&nbsp;Set &amp; Reset description --&gt; Only 8 characters are displayed in value tab. |  | U4 |  |  | FINDING | [6 empty] | 93861
35984 | FINDING | [Network & Unit] filter in Alarm application is not operating when ovation network is configures for Multi network. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2016-05-09 13:52 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2016-05-09 13:52 | 67024 |  |  | 2016-05-09 13:52 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2016-03-23 14:50 |  | [Network &amp; Unit] filter in Alarm application is not operating when ovation network is configures for Multi network. [Network &amp; Unit] filter is not responding on clicking.<div>However it is observed that on removing multi-network configuration from the drop, [Network &amp; Unit] filter button is responding and works fine.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | <div>Ovation 3.6.0_U4</div><div>Drop Name: Drop126 and Op127 (OPH Scanner + EWS) EMILY</div><div>OS: Win 7 64 bit</div>&nbsp; |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Open Alarm application when multi-net is configured to see [Network &amp; Unit] filter --&gt;filter is not responding on clicking.<div>Remove the multi-network configuration and see&nbsp;[Network &amp; Unit] filter --&gt;filter is responding on clicking.</div><div><br></div><div>YJ: Tested in U7. Working fine.</div> |  | U4 |  |  | FINDING | [6 empty] | 96498
35987 | FINDING | Logic Solver control module name should be limited to 16 characters. | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-25 03:31 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-25 03:31 | 67055 |  |  | 2016-05-25 02:57 |  |  |  | Zochowski, Michal AUTOSOL DX WRSW | 2016-03-24 10:35 |  | <p>LS and CSLS name is limited to 15 characters. Names of Control Modules are created by appending &quot;#N&quot; to the solver name (where N is Control Module number). It means that it's possible to create CM name of 17 or even 18 characters (for modules 10-16). This results in errors being reported by Controller. Control Module name should be no longer than 16 characters.</p> |  |  |  | After updating to U5, retest against Steps to Reproduce.&nbsp; You will notice that you cannot enter more than 13 characters for CSLS Names. | 0 |  |  |  | Verified for both LS (Legacy SIS) and CSLS (SIS CHARMs) in 3.6.0_U9. Verified Control Module names in SIS&nbsp;CHARMs&nbsp;from CSLS load script. | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Arora, Priyanka AUTOSOL PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation | 3.6.0 U5 |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ov3.6.0_U4 on OCR1100</span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Zochowski, Michal AUTOSOL DX WRSW | Development |  | Limit&nbsp;CSLS Names to 13 characters.&nbsp;&nbsp; This results in valid module name lengths; 16 characters or less.&nbsp; (1 for the # delimiter and 2 digits for the module number). | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Name LS/CSLS&nbsp;using&nbsp;maximum number of characters (15).</p><p>2. Create any test sheet with algorithms on this LS/CSLS.</p><p>3. Load the LS/CSLS.</p><p>4. Watch Ovation Error Log for errors about Invalid TT field or invalid modname.</p> |  | U4 |  |  | FINDING | [6 empty] | 97675
35991 | FINDING | Shelve option is not disabled when point already shelved for LD, DD, RM, RN, LP & DP. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Augustine, Lisa EMR SYSS PWS PITT | 2016-03-28 08:51 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-03-28 08:51 |  |  |  | 2016-03-28 08:51 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-28 04:21 |  | <p><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Shelve option is not disabled when point already shelved LD, DD, RM, RN, LP &amp; DP. Please find attached shelve.jpg</span></p><p><br></p><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><p> <span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Note: when a point is Unshelved then the Unshelve option is not available. which is the correct scenario. Please find attached unshelve.jpg</span></p><p> <br></p></span><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | OV3.6.0_U4,Ws07,Ws12R2 |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | WIW - The user can perform another shelve operation to change the shelve duration | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">1. Opened a digital point in point information </span><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">2. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Take point in alarm</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">3. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Right click on point information &amp; click on shelve via Operations-&gt;Shelve </span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">4.</span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">The point is shelved </span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">5. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Again Right click on point information, now the shelve option is available however point is already shelved.</span></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 93923
35992 | FINDING | The shelve/unshelve options are not correct as per point record type in graphics. | Spillane, Donal AUTOSOL PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 15:16 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2016-03-31 15:16 | 67004 | [6 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-28 04:27 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">The shelve/unshelve options are not correct as per point record type in graphics for below point types: </span></p><font face="Times New Roman" size=3> </font><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">When a packed/module/Node points called on graphics with the use of Poke0 then right clicked on same point &amp; go to Operations:</span></p><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Observation: The shelve option is not available although the point is Unshelved but the unshelve option is available which is incorrect. Please find attached snapshot of<span style="">&nbsp; &quot;shelve option is not available.jpg.&quot;</span></span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">When a digital point called on graphics with the use of Poke0 then right clicked on same point &amp; go to Operations:</span></p><p style="color:rgb(0, 0, 0);line-height:18pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:10pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Observation: The options (e.g. High4,3,2,1. etc) available in shelve are of Analog type. Please find attached snapshot of &quot;shelve option incorrect for digital point.jpg&quot;.&nbsp;</span></p></li></ol><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U5 |  | Ov3.6.0_U4,WS07,Ws12R2 |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><span style="">1. &nbsp;</span>Opened a GBNT</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">2. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Clicked on poke button</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">3. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Set poke type<span style="">&nbsp; </span>as process pt (0)</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">4. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Put pt name: packed or module or node or digital point type (as per requirement).</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">5. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Save &amp; Compile the modified GBNT</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">6. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Download the EWS where you want to see this graphics</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">7. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Opened same graphics &amp; performed steps 1 &amp; 2 describes in description field. </span></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 94140
35993 | FINDING | Profibus manual must be updated to show correct module groups | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-25 00:05 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-25 00:05 | 67256 |  |  | 2016-05-25 00:05 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-03-28 13:04 |  | LC 03/28/2016: The Profibus manual is missing a module group. See attachment. |  |  |  | <p>MG 18/04/2016: According to this finding, updated the <strong>Section 2.1.1 Electronics module- Profibus (DP) and 2.1.3 Valid module combinations&nbsp;</strong>of the Profibus User Guide for 3.6.0. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp;<a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_36.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_36.pdf</a></p><p>Online help: <a href="file://uspit-fp04/SourceIntegrity/TechWriters/3.6.0CHMs/OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a></p> | 0 |  |  |  | ST(05/25/2016):&nbsp;Checked in Ov3.6.0_U9 build, Online help has been updated as per the comments in attachment.&nbsp;So closing this finding. | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Casteel, Linda EMR SYSS PWS PITT | Tripathi, Sandeep AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation | 3.6.0_U6 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Development |  | MG 18/04/2016: This finding has been fixed and is available in U6 build. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 97663
35994 | FINDING | Position of Current value indicator for High Performance Analog Indicator is inconsistent | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Johnson, Kathy EMR SYSS PWS PITT | 2016-03-29 08:52 | [11 empty] | Johnson, Kathy EMR SYSS PWS PITT | 2016-03-29 08:52 |  |  |  | 2016-03-29 08:52 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-03-28 23:40 |  | <div>Position of Current value indicator for High Performance Analog Indicator is inconsistent.</div><div>For a top/down the Current value indicator appears outside the &nbsp;High Performance Analog Indicator in default state (No Inversion).&nbsp;</div><div>For a left/right the Current value indicator appears inside the &nbsp;High Performance Analog Indicator in default state (No Inversion).</div><div>The position should be same in both cases.</div><div>Please refer to attached screenshot</div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Agarwal, Gaurav EMR SYSS PWS NOIDA | Garg, Amit AUTOSOL PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p>When you switch from up/down to left/right, you will also have to potentially change the inversion and position fields depending on where you want the current value indicator to be. Same applies to control setpoint positions. Code is working the way it was designed. And because the&nbsp;software has already been released in 3_5_1 patch, we cannot re-define/re-design how&nbsp;the inversion and position params are interpreted for left/right indicators&nbsp;in 3.6.0, because all existing graphics would have to be changed when customers upgrade to 3.6.0 ... Plus, we cannot have 3.5.1 and 3.6.0 interpreting params and drawing things differently...</p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Create a High performance Analog Indicator in graphics.<br></li><li>Change it from top/down to left right.</li><li>Observe the position of current value indicator.</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 93970
35996 | FINDING | CSLS SIS Events are taking reference of VCSLSs created and configured on the same network | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-29 04:41 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-29 04:41 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-29 04:38 |  | <p>CSLS SIS Events are taking reference of VCSLSs created and configured on the same network.</p> <p>While performing any operation on the CSLS, corresponding SIS events are generated but they take reference of the VCSLS with the same index number as that of CSLS. For example, when a load/Reboot/Unlock operation is being performed on D30-CSLS003, then the SIS Events generated are:</p> <p><font face="Courier New">03/29/2016 11:21:10&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_IOIC5&gt;:&nbsp;&nbsp;Controller Load: Ended 0<br>03/29/2016 11:21:10&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_<strong>VCSLS3</strong>: D1_VCSLS3&gt;:&nbsp;&nbsp;CSLS download Started<br>03/29/2016 11:21:10&nbsp;DROP30&nbsp;&lt;OtherSisEvent: D1_IOIC5&gt;:&nbsp;&nbsp;Controller Load: Started 0</font></p> <p><font face="Courier New">03/29/2016 11:33:01&nbsp;DROP30&nbsp;&lt;LsEvent: D1_VCSLS3: D1_<strong>VCSLS3</strong>&gt;:&nbsp;&nbsp;CSLS Switchover: Manual</font></p> <p><font face="Courier New">03/29/2016 11:29:56&nbsp;DROP30&nbsp;&lt;LsEvent: D1_VCSLS3: D1_<strong>VCSLS3</strong>&gt;:&nbsp;&nbsp;CSLS is Unlocked</font></p> <p>Drop#1 is the Virtual Controller Drop on which VCSLSs have been configured and D1_VCSLS3 is the name of the Virtual CSLS configured in Drop#1.</p> <p>&nbsp;</p> <p>Sisev.log file&nbsp;on Active Scanner&nbsp;shows following messages:</p> <p><font face="Courier New">OvSisEvents.Service.exe Warning: 0 : Exception occured while parsing SIS RN point <a href="mailto:D1_VCSLS03.UNIT0@NET36">D1_VCSLS03.UNIT0@NET36</a></font><font face="Courier New"> SID 800081ACH Value not available.&nbsp;&nbsp; at Emerson.Ovation.OvData.OvSHC.SHC.GetBitArray32Field(OvSID sid, String field, OvBitArray32&amp; bitArrayVal)</font></p> <p>&nbsp;</p> <p><strong>Note:</strong></p> <p>a. VCSLSs were created and configured before Ovation3.6.0_U4 installation.</p> <p>b. SIS Events were coming properly till 03/22/2016 with the reference of the CSLS on which operation was performed. After that this issue with SIS Events has been observed.</p> <p>c. Later Active Scanner Drop159 was rebooted and OvSisEventService was restarted which corrected the references in the SIS Events.</p> <p>d. But later some action again led to change of CSLS reference with VCSLS reference in SIS Events.</p> <p>e. After performing the same series of action as in step#c, the SIS Events did not get corrected this time.</p> <p>&nbsp;</p> <p>Please find attached Historical Review Data and sisev logs.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>SIS Controller Drop30/80 (OCR1100 Controller)&nbsp;and Drop1 (Advanced Virtual Controller)</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>In total, 13 CSLSs&nbsp; (D30-CSLS001-D30-CSLS0013) on Drop#30&nbsp;and 16 VCSLSs (D1_VCSLS1-D1_VCSLS16)&nbsp;on Drop#1 have been configured and commissioned on the setup.</font></span></p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Perform some action (load/reboot/lock)&nbsp;on one of the CSLS, say D30-CSLS003.</p> <p>2. Open Historical Review application and check for SIS Events in SIS tab.</p> <p>3. Gather fresh sisev logs from Active Scanner.</p> |  | U4 |  |  | FINDING | [6 empty] | 93960
35997 | FINDING | Upgrade of firmware of logic solver (1508) gets failed due to error “Unable to find an entry point named ‘OvSisDevice_GetCardState’ in DLL ‘OvSisDevice.dll’. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-18 03:00 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-18 03:00 | 67145 |  |  | 2016-04-18 03:00 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-29 06:55 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);font-size:12pt;"><font face=Calibri>Upgrade of firmware of logic solver (1508) gets failed due to error “Unable to find an entry point named ‘OvSisDevice_GetCardState’ in DLL ‘OvSisDevice.dll’.</font></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);font-size:12pt;"><font face=Calibri>Please find attached snapshot.</font></span><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face="Times New Roman" size=3>Note: <font face=Calibri><span style="color:rgb(31, 73, 125);font-size:12pt;">As per&nbsp;Developer suggestion,&nbsp; </span><span style="color:rgb(31, 73, 125);"><font size=3><strong>OvPtSysApi.dll</strong></font></span><span style="color:rgb(31, 73, 125);font-size:12pt;"> was replaced in the Ovation\OvationBase folder in DBS drop100&nbsp; for work around of Finding#35853</span></font></font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face="Times New Roman" size=3><font face=Calibri><span style="color:rgb(31, 73, 125);font-size:12pt;"><span style="color:rgb(31, 73, 125);"><font size=3>Latest OvPtSysApi.dll </font></span>(File version-3.6.0.0 &amp; size-1.12MB) file&nbsp; &amp; now able to load the Logic Solver successfully.</span></font></font><font face="Times New Roman" size=3><font face=Calibri><span style="color:rgb(31, 73, 125);font-size:12pt;"><br></span></font></font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | Saklani, Rajnish EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | [5 empty] | Implementation | U5 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);font-size:12pt;"><font face=Calibri>OV3.6.0_U4,DBS Drop100 (192.168.36.100) WS12R2,SIS Controller OCR400 G02, Logic Solver (1508)</font></span></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | <p>The SDS name parameter is incorrect, there should be IP address OR name, not both. Please retest </p><p>PP:04/06/2016-We have checked with single option &amp; found same behaviour. Please find attached snapshot of &quot;Error_while_updating_ls_firmware_with single option.jpg&quot;.</p><p>PP:04/18/2016-Verified the logic solver firmware up gradation on Ov3.6.0_U6 &amp; found the Logic Solver Firmware up gradation is successfully with using SDS name or SDS IP address.</p><p>Hence, it is closed.<br></p> | 9 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-size:12pt;">1. Retrieve the new Logic Solver firmware package from c:\Ovation\SIS\Firmware\SLSFirmware.zip. It consists of four files</span></p><p><span style="color:rgb(31, 73, 125);font-size:12pt;">2. </span><span style="color:rgb(31, 73, 125);font-size:12pt;">Unzipped &amp; Stored the files in C:\tmp\SIS</span></p><p><span style="color:rgb(31, 73, 125);font-size:12pt;">3. </span><span style="color:rgb(31, 73, 125);font-size:12pt;">Cleared the target Logic Solver in the Ovation Developer studio</span></p><p><span style="color:rgb(31, 73, 125);font-size:12pt;">4. </span><span style="color:rgb(31, 73, 125);font-size:12pt;">Cleared the SIS controller</span></p><p><span style="color:rgb(31, 73, 125);font-size:12pt;">5. </span><span style="color:rgb(31, 73, 125);font-size:12pt;">Run the upgrade application from the command prompt</span></p><p><span style="color:rgb(31, 73, 125);font-size:12pt;">6. </span><span style="color:rgb(31, 73, 125);font-size:12pt;">It gives error as “Unable to find an entry point named ‘OvSisDevice_GetCardState’ in DLL ‘OvSisDevice.dll’. Please find attached snapshot.</span></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 95111
36001 | FINDING | Virtual controller manual needs updating for bridge creation in regard to DDB protocol | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-26 11:09 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-26 11:09 | 67256 |  |  | 2016-04-26 11:09 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-03-29 14:24 |  | The Virtual Controller User Guide needs to be updated in regard to the bridge and the DDB protocol.&nbsp; The DDB protocol can only be added to one NIC in 3.6.0.&nbsp; The document should be updated so that the DDB protocol is removed from the physical NIC, the bridge then created and the DDB protocol assigned to the bridge. | <p>AA (31/03/2016): I have addressed the issue related to the Finding in the Virtual Controller User Guide.&nbsp;Topic number 4.3.2 has been modified. The following note has been added:</p><i><font size=2></font><p><font size=2><b>Note: </b></font><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>You </font></font><b><font size=2>MUST </font></b><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>remove the DDB protocol from the physical NIC before creating a bridge and assigning a DDB protocol to the created bridge. </font></font></p><p><font face=Arial size=2>The updated user guide is kept at: <a href="file://uspit-fp05/Ohara/Communication/TechComm/Share/Abhinav_Ovation">\\uspit-fp05\Ohara\Communication\TechComm\Share\Abhinav_Ovation</a> 3.6.0 manuals\Virtual Controller User Guide (OW360_57)</font></p></i> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | <p>AA (31/03/2016): I have addressed the issue related to the Finding in the Virtual Controller User Guide.&nbsp;Topic number 4.3.2 has been modified. The following note has been added:</p><i><font size=2></font><p><font size=2><b>Note: </b></font><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>You </font></font><b><font size=2>MUST </font></b><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>remove the DDB protocol from the physical NIC before creating a bridge and assigning a DDB protocol to the created bridge. </font></font></p><p><font face=Arial size=2>The updated user guide is kept at: <a href="file://uspit-fp05/Ohara/Communication/TechComm/Share/Abhinav_Ovation">\\uspit-fp05\Ohara\Communication\TechComm\Share\Abhinav_Ovation</a> 3.6.0 manuals\Virtual Controller User Guide (OW360_57)</font></p></i> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | Ovation 3.6.0 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>MG (30/03/2016): Assigning this finding to Abhinav.</p><p><br></p><p>AA (31/03/2016): I have addressed the issue related to the Finding in the Virtual Controller User Guide.&nbsp;Topic number 4.3.2 has been modified. The following note has been added:</p><i><font size=2></font><p><font size=2><b>Note: </b></font><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>You </font></font><b><font size=2>MUST </font></b><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>remove the DDB protocol from the physical NIC before creating a bridge and assigning a DDB protocol to the created bridge. </font></font></p><p><font face=Arial size=2>The updated user guide is kept at: <a href="file://\\uspit-fp05\Ohara\Communication\TechComm\Share\Abhinav_Ovation">\\uspit-fp05\Ohara\Communication\TechComm\Share\Abhinav_Ovation</a> 3.6.0 manuals\Virtual Controller User Guide (OW360_57)</font></p></i><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 95702
36003 | FINDING | SDR 35771 Failed (RR 35873 ) : Wrong SIS Event Descriptions for Proof-Testing SIS Charms | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:42 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:42 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-03-30 04:08 |  | <p>SDR 35771 (RR 35873 ) failed in 3.6.0 U4.</p> <p>All the related SIS Events according to the manual OW352_43, for Proof Testing are still not coming. Only below mentioned SIS Events have been observed in the logs:</p> <p><font face="Courier New">03/17/2016 07:31:15&nbsp;DROP30&nbsp;&lt;LsEvent: 0.D30-CSLS0011: 0.D30-CSLS0011&gt;:&nbsp;&nbsp;Proof-test Success</font></p> <p><font face="Courier New">03/21/2016 11:53:13&nbsp;DROP30&nbsp;&lt;LsEvent: D30-CSLS003: D30-CSLS003-CM01&gt;:&nbsp;&nbsp;CSLS Switchover: Proof-test</font></p> <p>&nbsp;</p> <p>But there have been no SIS Events for power up mentioned in the manual as:</p> <p align=left></p><font size=2> <p><font face="Courier New">CHARMs Smart Logic Solver proof test and power up successful.</font> </p> <p>&nbsp;</p> <p>Please find attached the Historical Review Data.</p></font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Documentation | The documentation needs to be updated. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U4 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Perform Reboot operation on the CSLS or configure Proof test on one of the CSLS.</p> <p>2. Open Historical Review application and check for SIS Events in SIS tab.</p> |  | U4 |  |  | FINDING | [6 empty] | 111018
36004 | FINDING | In Historical review, Operator events are appearing inconsistently . | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-04-20 22:48 | [11 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-04-20 22:48 |  |  |  | 2016-04-20 22:48 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-03-30 04:45 |  | In Historical review, Operator events are appearing inconsistently . |  |  |  |  | 0 |  |  |  | <p>GA:- </p><p><br></p><p>Date:- 4/21/2016</p><p>Used Build:- Ov 3.6.0_U6</p><p><br></p><p>Operator events are appearing consistently. Hence finding is closed.</p> | 0 |  | Ovation for Windows/Operator Station/Historical Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Contento, James AUTOSOL PWS PITT | [9 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation Release: - Ov 3.6.0</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Used build:- OV 3.6.0_U4</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Network: - Net#36</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>DBS Drop: - Drop100</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>OPH server Drop:- drop180</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>OPH :- OPH 3.6.0_U1</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Operator Station/Historical Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | smatreja: Fixed. Check in U5. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- Open the historical review and go to Operator Event tab.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Set the following filter:-</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;text-indent:0.25in;"><font size=3><font face=Calibri>Start time:- 03/30/2016 06:00:00<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;text-indent:13.5pt;"><font face=Calibri><span style=""><font size=3>&nbsp; </font></span><font size=3>End time:- 03/30/2016 12:00:00</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Historian:- drop180</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Network/Unit:- </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Originating Drop: All Drops</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Domain/UserName:</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Reason:</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Filter Criteria:- All Subtypes</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- Press start button.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>“0 operator events reviewed” Message are appearing. See screen shots” Operator events are not </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>appearing.jpg”</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><font size=3>4. <span style="">&nbsp;</span></font><font size=3>In excel addin, we are able to see Operator events in the same time stamps. see </font><span style=""><font size=3>&nbsp;</font></span><font size=3>screenshots” </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font size=3>Operator events appearing in excel addin.jpg”</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><b style=""><font size=3>Note:-</font></b><font size=3> 1:-</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- it is inconsistent behavior. Sometimes we are able to see the events. But most of the times we are not able to see operator events in Historical review.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Attached the SYSREQUESTS file from drop180 and also attached the screen shots “SYSREQUESTS file.jpg” , marked the log when operator events stopped.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>A remote login detail of drop180 is attached with this finding.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 95342
36005 | FINDING | ATREND algorithm is not behaving as desired for indicating trended point or scaling change. | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-03-30 04:48 | [11 empty] | USPITTFSService | 2016-03-30 04:48 | [7 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-03-30 04:48 |  | <p>As per Algorithm manual for ATREND &quot;The output to the recorder is set to zero percent for five seconds and then to 100 percent for 10 seconds to indicate that the point being trended or its scaling has been changed.&quot; </p><p>However whenever point being trended or scaling is changed for this algorithm, the recorder is set to zero percent, 4.00 mA for 10 seconds (instead of 5 seconds) and then 1 percent, 4.16mA (instead of 100 percent) for 10 seconds. <br></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U4, OCR1100 Drop27/77 |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps followed to reproduce this issue:</p><p>1. Create a sheet with ATREND algorithm in control builder. Assign point ‘D27-ATTREND-CARD’ to ATREND’s “CARD” output. </p><p>2. Defined &quot;D27-ATTREND-CARD&quot; in channel 1 of Analog Output (4-20mA) Module.</p><p>3. Kept default TPSC and BTSC as 100 and -100 for ATREND. Load controller.</p><p>4. Enter a continuously changing Point &quot;D27-SINEGEN-OUT&quot; (to be trended) in ATREND algorithm through Advanced tuning window. ATREND is recording the &quot;D27-SINEGEN-OUT&quot; point.</p><p>5. Change ATREND BTSC from -100 to 0 in signal Diagram.</p><p>It is observed that the recorder point &quot;D27-ATTREND-CARD&quot; is set to zero percent, 4.00 mA for 10 seconds (instead of 5 seconds) and then 1 percent, 4.16mA (instead of 100 percent, 20mA) for 10 seconds.</p> |  | U4 |  |  | FINDING | [6 empty] | 94033
36006 | FINDING | In NCV readout tab of HPCR analog indicator, horz alignment is not working properly. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Johnson, Kathy EMR SYSS PWS PITT | 2016-03-30 08:58 | [11 empty] | Johnson, Kathy EMR SYSS PWS PITT | 2016-03-30 08:58 |  |  |  | 2016-03-30 08:58 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-03-30 06:38 |  | In NCV readout tab of HPCR analog indicator, horz alignment is not working properly. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ovation Release: - Ov 3.6.0</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Used build:- OV 3.6.0_U4</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Network: - Net#36</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>DBS Drop: - Drop100</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | <p>I don't think you understand how left and right and center alignment works. The overall NCV display &nbsp;is left justified with the overall indicator shape/DOC arrow pair when the horizontal alignment is set to left. That means that the left side of the NCV display lines up with the left side of the shape+DOC pair.&nbsp; When right horizontal alignment is specified, that means that the right side of the NCV display lines up with the right side of the shape+DOC pair. When centered horizontal alignment is specified, that&nbsp; means that the center of the NCV display lines up with the center of the shape+DOC pair. Note that when left or right alignment is specified, the left or the right sides will line up no matter whether the NCV display is larger, smaller, or same size as the shape+DOC pair.&nbsp; Imagine an outlining rectangle being drawn around the NCV display and the shape+DOC pair. When left alignment is specified, the left sides of the outlining rectangles will be aligned; when right alignment is specified, the right sides of the outlining rectangles will be aligned. This is consistent with how the Align edit function works in GB. The attachments you sent show that GB is working correctly.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- In Graphic Builder configured the HPCR Analog indicator.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Configured the Numeric Current Value (NCV).</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font size=3><font face=Calibri>3:- <span style="color:black;">NCV are appearing in the High performance analog indicator.</span></font></font></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>4:- Select Pos (e.g.:- above indicator shape/doc).</font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>5:- In following scenarios behavior of horz alignment position is: </font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">a. 0&lt;Char w&lt;=45<span style="">&nbsp; </span></span><span style="color:black;font-family:Wingdings;"><span style="">à</span></span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Horz alignment position is moving properly. See screen shot</span></font></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><span style=""><font size=3>&nbsp;</font></span><font size=3>&quot;Correct NCV postions.jpg&quot;</font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">b. 46&lt;=Char w&lt;=58 </span><span style="color:black;font-family:Wingdings;"><span style="">à</span></span></font><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><span style=""><font size=3>&nbsp; </font></span><font size=3>Horz alignment position is not moving at all. See screen shot &quot;</font></span><font face="Times New Roman" size=3> </font></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>NCV is not moving.jpg&quot;.</font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">c. 59&lt;=Char w </span><span style="color:black;font-family:Wingdings;"><span style="">à</span></span><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"> Horz alignment position is moving incorrectely, e.g. Left position</span></font></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><span style=""><font size=3>&nbsp;</font></span><font size=3>Moved to right and right position moved to left. See screen shot &quot;InCorrect NCV</font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;text-indent:0.5in;"><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><span style=""><font size=3>&nbsp;</font></span><font size=3>postions.jpg&quot;</font></span></p><font face="Times New Roman" size=3> </font><p style="line-height:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;</span></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 94055
36016 | FINDING | Stoping PrimaryVirtual Controller does not reboot Secondary Dev | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-05 14:38 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-05 14:38 | 66878 |  |  | 2016-04-05 14:38 |  |  |  | Shiferaw, Tedla AUTOSOL PWS PITT | 2016-03-30 14:57 |  | GWS&gt; Duplicate of SDR 35345. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Shiferaw, Tedla AUTOSOL PWS PITT | Development |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U5 |  |  | FINDING | [6 empty] | 94464
36018 | FINDING | Signal diagram functionality is not working for SIS control sheet | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:42 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:42 | 67136 |  |  | 2017-02-24 07:22 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-03-31 00:10 |  | <p>Signal diagram functionality is not working for SIS control sheet&nbsp; &amp; please find below observations;</p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">1. In Signal Diagram,&nbsp;yellow Warning message “Function Executing in Controller Newer than displayed documents” appears. </span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2. In Signal diagram-Sometimes the Event log Warning for LC Record Point “Error (5): Long Point Record Point not updated ”appears. </span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3. In signal diagram- The output of Algorithm is&nbsp; going to BAD quality (Please find attached snapshot of “Signal_diagram_not_updating.jpg” for point 1-3).</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">4. Open ovation error log, error appears for signal diagram (C07C). e.g. “Error registering the module:hwpath….(Please find attached “error_log.jpg”)</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Note: 1. Non SIS Control sheet is&nbsp;not showing yellow warning&nbsp;message and it is in green state &nbsp;&quot; Documents timestamp matches current control&quot;. &nbsp;Also verified the above scenario in OCR1100 SIS setup.</span></p><p><br></p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><font color="#000000" face="Times New Roman" size=3> </font><font color="#666666" face="Times New Roman" size=3>Note: 2. </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>As per&nbsp;Developer suggestion,&nbsp; <strong><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">OvPtSysApi.dll</span></strong></font><font size=3> was replaced in the Ovation\OvationBase folder in DBS drop100&nbsp; for work around of Finding#35853</font></span></p><p><font color="#000000" face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Latest OvPtSysApi.dll (File version-3.6.0.0 &amp; size-1.12MB) file&nbsp; &amp; now able to load the Logic Solver successfully.</font></span></p><p><font color="#000000" face="Times New Roman" size=3> <br></font></p><p><br></p><p><font color="#000000" face="Times New Roman" size=3>Is it all the sheets in the Logic Solver or Control Module?</font></p><p><font color="#000000" face="Times New Roman" size=3>PP:04/05/2016-Yes, I have created control sheet&nbsp;in control module #1 of Logic Solver #5 &amp; loaded Logic Solver Successfully with provided work around.</font></p><font color="#000000" face="Times New Roman" size=3><p><br></p><p>When the logic solver is loaded, are there any SIS Event Messages from that controller / logic solver ?</p><p>PP:04/05/2016-We are not getting any SIS Event Messages for any action performed on SIS controller &amp; Logic Solver. e.g. Load, clear, Reboot, lock/unlock of Logic Solver although the SIS logger is defined.</p><p><br></p><p>Please Attach the SIF Scripts for this SDS.&nbsp; They are found under ...\ControlFunctions\sifs</p><p>PP:04/06/2016-We have&nbsp;created SIS Control sheet under Drop27 (OCR400)-&gt;SDS01-&gt;LS05-&gt;CM01. Please find attached SIF script&nbsp;name as &quot;D27_SDS01_LS05#1.sif&quot;.</p><p>Also, We tried with work around(<font color="#1f497d">“cbdbWindows.dll” &amp;“cbDirect.dll” files&nbsp;)</font> provided by Steve in mail.</p><p>Detailed observation send through mail but issue still exists.</p><span style="color:rgb(31, 73, 125);"><p><br></p><p>PP:04/13/2016-Ov360_U6: We have created SIS Control sheet (&quot;D27_SDS01_LS05_BAD_QUALITY_TEST&quot;) in Ov3.6.0_U6 under Drop27 (OCR400)-&gt;SDS01-&gt;LS05-&gt;CM01. </p><p>Observation: We have found the same above issue as&nbsp;the SIS signal diagram is not updating&nbsp;as well as&nbsp;t<font face=Calibri>he output of Algorithm is&nbsp; going to BAD quality</font>.<font face=Calibri> (Please find attached snapshot of “SIS_Signal_diagram_not_updating_04-13-2016.jpg).</font> <br></p><font face=Calibri><p><br></p><p><br></p><span style="color:rgb(31, 73, 125);"><p>PP:05/02/2016-<font color="#000000" face="Times New Roman"> </font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);">We have verified in Ov3.6.0_U9 &amp; found the Legacy SIS setup is running o.k. except below issues:</span></p><p><font color="#000000" face="Times New Roman"> </font><span style="color:rgb(31, 73, 125);">1. In SIS Signal Diagram, yellow Warning message “Function Executing in Controller Newer than displayed documents” still appears. </span></p><p><font color="#000000" face="Times New Roman"> </font><span style="color:rgb(31, 73, 125);">2. In SIS Signal diagram-Sometimes the Event log Warning for LC Record Point “Error (5): Long Point Record Point not updated ”appears <b>during the load of&nbsp; SIS controller drops</b>. </span></p><p><font color="#000000" face="Times New Roman"> </font><span style="color:rgb(31, 73, 125);">Hence, Finding is partially failed.</span></p><p><font color="#000000" face="Times New Roman"> </font><br></p></span><p><br></p><p><br></p></font><p><br></p></span><p><br></p><p><br></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri>&nbsp;</font></span></p><p> <br></p><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0cm;margin-bottom:0pt;"><font face="Times New Roman" size=3><br></font></p><p><br></p><p><br></p></font></span><p><br></p><p><font face="Times New Roman" size=3> <br></font></p> | <p><font size=3 face="Times New Roman">This is tracked by </font><a href="https://uspit-tfs-v.emrsn.org/tfs/Quality/SDR/_workitems/edit/37997" class=caption>SDR 37997</a></p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | Saklani, Rajnish EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA |  |  | Implementation | 3.6.0_U7 |  | <span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:12pt;">OV3.6.0_U4,DBS Drop100 (192.168.36.100) WS12R2,SIS Controller OCR400 G02, Logic Solver (1508)</span> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 15 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font size=3 face="Times New Roman"> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>1. Inserted a new SIS control sheet in logic solver 03 of SDS01-&gt; SIS Controller 27/77(OCR400).</font></span><font size=3 face="Times New Roman"> </font></p><p><font size=3 face="Times New Roman">2. L </font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>ogic solver loaded successfully.</font></span><font size=3 face="Times New Roman"> </font></p><p><font size=3 face="Times New Roman">3. Opened the SIS control sheet in signal diagram</font></p><p><font size=3 face="Times New Roman">4. Found the &quot;Signal diagram functionality is not working&quot;. Given detail observations in description field.</font></p><p><font size=3 face="Times New Roman"><br></font></p><p><font size=3 face="Times New Roman">This is tracked by </font><a href="https://uspit-tfs-v.emrsn.org/tfs/Quality/SDR/_workitems/edit/37997" class=caption>SDR 37997</a></p> |  | U4 |  |  | FINDING | [6 empty] | 109270
36019 | FINDING | Incorrect Sheet title name displayed in Sheet compile operation confirmation window. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-06 13:03 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-06 13:03 |  |  |  | 2016-04-06 13:03 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-03-31 01:00 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Incorrect Sheet title name displayed in Sheet compile operation confirmation window. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Incorrect Sheet title name displayed in Sheet compile operation confirmation window if Sheet Title contain sign <b style="">Greater Than</b></font><font size=3> OR </font><b style=""><font size=3>Less Than i.e.</font></b><font size=3>“</font><b style=""><font size=3>&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&gt;&lt;</font></b><font size=3>”.</font><span style=""><font size=3>&nbsp; </font></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-1: Create a control sheet with Title name contain sign <b style="">Greater Than</b></font><font size=3> OR </font><b style=""><font size=3>Less Than i.e.</font></b><font size=3>“</font><b style=""><font size=3>&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&gt;&lt;</font></b><font size=3>” .</font><span style=""><font size=3>&nbsp; </font></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-2: Save the sheet.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-3: Perform Compile operation.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-4: Upon compile confirmation window, incorrect control sheet title appears.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>For reference <b style="">Cbeditor_Compile_incorrect title.jpg </b></font><font size=3>is attached.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Example-1: If Control sheet title is <b style="">VP&lt;CTR&lt;TEST&lt;&gt;D37&lt;&gt;CM2. <span style="">&nbsp;</span></b></font><font size=3>While compilation, on confirmation window.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>Incorrect Sheet title name </font><b style=""><font size=3>VPD37CM2 </font></b><font size=3>gets appeared.</font><b style=""><font size=3> </font></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><font size=3>Example-2: If Control sheet title is <b style="">VP&lt;TEST&gt;A1&lt;&gt;B2&lt;C3&gt;D4</b></font><font size=3>.</font><b style=""><font size=3> </font></b><font size=3>On compile confirmation window, incorrect [</font><b style=""><font size=3>VPA1B2D4</font></b><font size=3>] Sheet title name appeared.</font></font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>3.6.0+Control Builder</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-1: Create a control sheet with Title name contain sign <b style="">Greater Than</b></font><font size=3> OR </font><b style=""><font size=3>Less Than i.e.</font></b><font size=3>“</font><b style=""><font size=3>&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&lt;&gt;</font></b><font size=3>” OR “</font><b style=""><font size=3>&gt;&lt;</font></b><font size=3>” .</font><span style=""><font size=3>&nbsp; </font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-2: Save the sheet.</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-3: Perform Compile operation.</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-4: Upon compile confirmation window, incorrect control sheet title appears.</font></p> |  | U4 |  |  | FINDING | [6 empty] | 94515
36024 | FINDING | Ov3.6.0_U4 Virtual Controller manual OW352_57 needs to be updated for few changes. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 06:05 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 06:05 | 3.6.0_U5 |  |  | 2016-04-14 06:05 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-01 00:40 |  | <p>Ov3.6.0_U4 Virtual Controller manual OW352_57 needs to be updated for few changes in section 4.2.4 ,section 4.2.9 and section 4.3.4.</p><p><br></p> | AA (04/01/2016): The issue related to the Finding has been resolved. Sections 4.2.4, 4.2.9, and 2.3.4&nbsp;have been modified. This will be available in the online help file for 3.6.0_U5 Build.&nbsp;The latest Virtual Controller User Guide OW360_57.pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | AA (04/01/2016): The issue related to the Finding has been resolved. Sections 4.2.4, 4.2.9, and 2.3.4&nbsp;have been modified. This will be available in the online help file for 3.6.0_U5 Build.&nbsp;The latest Virtual Controller User Guide OW360_57.pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>AA (04/01/2016): The issue related to the Finding has been resolved. Sections 4.2.4, 4.2.9, and 2.3.4&nbsp;have been modified. This will be available in the online help file for 3.6.0_U5 Build.&nbsp;The latest Virtual Controller User Guide OW360_57.pdf is kept at: <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a></p><p><br></p><p>SS: Verified and found the changes are updated in the manual OW360_57</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1.Section 4.2.4 step 11 &quot;show runn&quot; should be replaced with &quot;show run&quot;.</p><p>2.Section 4.2.9 step 3 &quot;Run wrtap32&quot; should be replaced with &quot;Type wrtap32 and press Enter&quot; or &quot;Run wrtap32&quot; should be replaced with &quot;Type wrtap32 and press Enter&quot;.</p><p>3.Section 4.3.4 step 7&nbsp;&quot;Select&quot; should be replaced with &quot;Press&quot;.</p> |  | U4 |  |  | FINDING | [6 empty] | 94915
36025 | FINDING | Ov3.6.0_U4_Virtual controller Host and Virtual controlller default port values are not same as mentioned in the manual. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 06:20 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 06:20 | 3.6.0_U5 |  |  | 2016-04-14 06:20 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-01 00:50 |  | <p>Ov3.6.0_U4_Virtual controller Host and Virtual controller default port values are not same as mentioned in the manual.</p><p>Default Port value for Virtual controller Host as mentioned in the manual (OW352_57)is 6010 (Section 4.2.6 step8 Virtual Controller Host section) but the actual default port value for VCH is 6001.</p><p>Default Port value for Virtual Controller as mentioned in the manual (OW352_57) is 6001 (Section 4.2.6 step8 Virtual Controller section ) but the actual default port value for VC is 6010.</p><p><br></p><p>SS: Verified in U6 build.</p> | AA (04/01/2016): The issue related to the Finding has been resolved. Section 4.2.6 has been modified. The latest OW360_57.pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | AA (04/01/2016): The issue related to the Finding has been resolved. Section 4.2.6 has been modified. The latest OW360_57.pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>AA (04/01/2016): The issue related to the Finding has been resolved. Section 4.2.6 has been modified. This will be available in the online help file for 3.6.0_U5 Build.&nbsp;The latest Virtual Controller User Guide OW360_57.pdf is kept at: <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a></p><p><br></p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1.Open Developer studio.</p><p>2.Navigate to any Virtual controller Host Drop in the hardware tab.</p><p>3.Right click on the Virtual Controller Host drop and select open.<br>4.Go to the Virtual Controller host section.</p><p>5.Verify the port number</p><p>6.Verify the port numbers for Virtual Controllers also.<br><br></p><p><br></p> |  | U4 |  |  | FINDING | [6 empty] | 94925
36026 | FINDING | Default value of BTSC parameter for Squareroot algorithm is incorrect | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-15 05:21 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-15 05:21 | 67022 |  |  | 2016-04-15 05:21 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-01 03:03 |  | As per SRF2137 SVTP default BTSC value of squareroot algorithm should be 0&nbsp;, But instead default value of BTSC for Squareroot algorithm is -1E+09.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U5 |  | <p>OV3.6.0_U4 NET#36</p><p>EWS Drop154 </p><p><br></p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | Changed BTSC default value to 0.0 in template.tft. | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open control builder.</p><p>2. Add squareroot algorithm .</p><p>3. See the BTSC value of squareroot algorithm in the property editor window.</p> |  | U4 |  |  | FINDING | [6 empty] | 95028
36027 | FINDING | In SIS Security disabled scenario, Reboot of Charms can be performed. | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-20 02:03 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-20 02:03 | 67055 |  |  | 2016-04-20 02:02 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-01 03:53 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>In SIS Security disabled scenario, Reboot of Charms can be performed.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Steps and observation: </font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-1: Via Ovation Security Manager, Disabled SIS security rights for a User.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-2: User (SIS Security disabled in step-1) logged in. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-3: In Studio, Goto- <b style="">Local Safety Network</b></font><font size=3> [</font><b style=""><font size=3>LSN1</font></b><font size=3>]-</font><b style=""><font size=3>SIS CHARM LOGIC SOLVER</font></b><font size=3>-</font><b style=""><font size=3>SIS I/O CHARMS</font></b><font size=3>.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;text-indent:0.5in;"><font face=Calibri size=3>Select and Right click on a configured SIS Charms I/O.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-4: <b style="">Reboot</b></font><font size=3> option is active, Perform Reboot of Charm operation. </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Observation: </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>In SIS Security disabled scenario,</font><font face=Calibri size=3>&nbsp;Reboot option for SIS charms IO is still active and user can perform reboot of charms IO. For reference screenshot is attached.</font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font></p> |  |  |  | After updating to U5, retest against Steps to Reproduce above. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U5 |  | 3.6.0+ |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Found Issue fixed in&nbsp;3.6.0_U6. Finding is closed&nbsp;&nbsp; | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-1: Via Ovation Security Manager, Disabled SIS security rights for a User.</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Step-2: User (SIS Security disabled) logged in. </font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-3: In Studio, Goto- <b style="">Local Safety Network</b></font><font size=3> [</font><b style=""><font size=3>LSN1</font></b><font size=3>]-</font><b style=""><font size=3>SIS CHARM LOGIC SOLVER</font></b><font size=3>-</font><b style=""><font size=3>SIS I/O CHARMS</font></b><font size=3>.</font></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;text-indent:0.5in;"><font face=Calibri size=3>Select and Right click on a configured SIS Charms I/O.</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Step-4: <b style="">Reboot</b></font><font size=3> option is active, Perform Reboot of Charm operation. </font></font></p> |  | U4 |  |  | FINDING | [6 empty] | 95274
36029 | FINDING | LSBDE and LSPDE algorithms does not give output for all input triggers | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 9 | Konkol, Marek AUTOSOL PWS WRSW | 2017-04-20 10:39 | [11 empty] | Konkol, Marek AUTOSOL PWS WRSW | 2017-04-20 10:39 |  |  |  | 2017-04-20 10:39 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-01 07:16 |  | <p>Found that the output of LSBDE and LSPDE algorithms is not as expected.</p> <ol> <li>Sometimes&nbsp;it was observed that neither LSBDE nor LSBDE was giving any output and few times LSBDE was giving output at positive transition of input. Few instances were also observed when LSBDE was giving output at negative transition of input.</li> <li>When same operation was tried again,&nbsp;it is observed that&nbsp; LSBDE and LSBDE both give output at positive input edge.<br>But this behavior is also not consistent i.e. we do not always get the output of all instances of change in input (Output_1.png and Output_2.png).</li> <li>In Output_1.png, when LSBDE and LSPDE&nbsp; were giving output, it was observed that LSBDE and LSPDE does not give output for all the input instance i.e. they give output only at an regular intervals.<br>Sometimes there was a change in the time interval gap between the outputs.</li> <li>A delay of about 3 seconds was observed between change in input and the change in output of LSBDE algorithm (TimeAnalysis.png)</li> <li>We tried by using the SIS Force to change the value of input pin of LSBDE algorithm, but the observations were the same.</li> <li>Tried by changing the CSLS scan rate between 50 msec. and 200 msec. and also I/O Data Update Time, but the behavior was still the same. CSLS shadow block is configured for control task 2.</li></ol> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  | Implementation |  |  | <p>Ovation 3.6.0_U4</p> <p>Net#36 EWS Drop155 (W7-SP1 64-bit)</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | In Validation | 3.6.0 |  |  | User Error | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | Algorithms work as per design.<br><span id=result_box class=short_text lang=en><span class="">The connected external relay reacted correctly during input </span></span>transitions.<br>Ovation software points could have few seconds delay and trend with 1sec resolution may not register a 50-200msec peak.<br> | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Created a simple logic in Control Task 2 of Drop30/80 to change the value of digital point between 0 and 1 at a time gap of 10 seconds (LSBDE_LDSPDE_Input_Logic.png)</li> <li>Created a simple logic in Control Module 1 of CSLS05 of Drop30/80 to for LSBDE (LSBDE_Logic.png)</li> <li>Created a simple logic in Control Module 2 of CSLS05 of Drop30/80 to for LSPDE (LSPDE_Logic.png)<br></li></ol> | EPM Validation | U4 |  |  | FINDING | [6 empty] | 111462
36036 | FINDING | SVTP issue:SVTP "3.6.0_CB_SVTP_rev_2.8_xx.doc", Testcase 5.8.1 to TestCase 5.8.4 need to be modified | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-02 04:26 | [11 empty] | USPITTFSService | 2016-04-02 04:26 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-02 04:26 |  | <p>SVTP issue:SVTP &quot;3.6.0_CB_SVTP_rev_2.8_xx.doc&quot;, Testcase 5.8.1 to TestCase 5.8.4 need to be modified.</p> <p>Test Case 5.8.1.d and Test Case 5.8.3.d says &quot;<span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font color="#000000">Verify selected Symbols exist under selected directory with both ‘.svg’ and “.png” extensions when new (custom)Algorithm symbols are inserted.&quot; and &quot;<span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">Verify selected Macros exist under selected directory with ‘.svg’, ‘.mcr’, <span style="">&nbsp;</span>and<span style="">&nbsp; </span>‘.tft’ file extensions.&quot; respectively. However, when the Algorithm symbol and Control macro are exported, .png, .mcr and .tft files are not created in the folder in which Symbol and Control Macro are exported. Only svg files are exported.</span></font></span></p> <p><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font color="#000000"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"></span></font></span>&nbsp;</p> <p><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font color="#000000"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">One Step needs to be added in Test Case 5.8.2 that &quot;d) Verify if the png file of the symbol is created upon using that Control macro in any Control Sheet after the Import operation&quot;.</span></font></span></p> <p><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;"><font color="#000000"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">One Step needs to be added in Test Case 5.8.4 that &quot;Verify if after Import Operation, .mcr and .tft files for the Control macro are created automatically in the selected folder&quot;</span></font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94239
36037 | FINDING | ATREND algorithm is trending point values beyond its defined TPSC and BTSC limits. | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-02 05:03 | [11 empty] | USPITTFSService | 2016-04-02 05:03 | [7 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-04-02 05:03 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>In ATREND algorithm, when value of a trended point is beyond defined TPSC and BTSC of ATREND algo, the CARD point still&nbsp;record the value&nbsp;but goes to BAD </font><font size=3>quality.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>However, many algorithms do not allow point values to go beyond the defined TPSC and BTSC values. In this regard ATREND is behaving differently.</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U4 |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">1. Create a sheet with ATREND algorithm in control builder. Assign point ‘D27-ATTREND-CARD’ to ATREND’s “CARD” output. </font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">2. Defined &quot;D27-ATTREND-CARD&quot; in channel 1 of Analog Output (4-20mA) Module.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">3. Kept default TPSC and BTSC as&nbsp;90 and 10 for ATREND. Load controller.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">4. Enter a continuously changing Point &quot;D27-SINEGEN-OUT&quot; (to be trended) in ATREND algorithm through Advanced tuning window. ATREND is recording the &quot;D27-SINEGEN-OUT&quot; point.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">5.Value of &quot;D27-SINEGEN-OUT&quot;&nbsp; is changing&nbsp;from 0-100. </font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">6. Accordingly &quot;D27-ATTREND-CARD&quot; value is also changing to record the trendedpoint &nbsp;&quot;D27-SINEGEN-OUT&quot;&nbsp; value.</font></span></p><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">7. Whenever the trended point value go below 10 or above 90, the &quot;D27-ATTREND-CARD&quot;&nbsp;point is displaying that value&nbsp;with BAD quality.</font></span></p><p><font size=3> </font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">It is not limiting trended value to the defined TPSC and BTSC.</span></p> |  | U4 |  |  | FINDING | [6 empty] | 94241
36038 | FINDING | Ov3.6.0_U4 online help should be updated for Divide,Gainbias,Hiselect,Leadlag,Loselect,Multiply,Ratelimit,,Squareroot,Sum,Transfer algorithms for the default scale values. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 05:53 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-14 05:53 |  |  |  | 2016-04-14 05:53 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-02 06:37 |  | <p>Ov3.6.0_U4 online help should be updated for Divide,Gainbias,Hiselect,Leadlag,Loselect,Multiply,Ratelimit,Squareroot,Sum,Transfer algorithms.</p><p>The new default scale values TPSC and BTSC are 1E+09 and -1E+09 respectively. Earlier the default TPSC and BTSC values were 100 and 0 respectively.</p><p>For the Squareroot algorithm the new TPSC and BTSC default values are 1E+09 and 0 respectively.</p> | Updated the Divide,Gainbias,Hiselect,Leadlag,Loselect,Multiply,Ratelimit,Squareroot,Sum,Transfer algorithms to show the new values for the TPSC (top of scale) and BTSC (bottom of scale) parameters. |  |  | Check the Divide,Gainbias,Hiselect,Leadlag,Loselect,Multiply,Ratelimit,Squareroot,Sum,Transfer algorithms. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | U5 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | LC 04/08/2016: Updated the Divide,Gainbias,Hiselect,Leadlag,Loselect,Multiply,Ratelimit,Squareroot,Sum,Transfer algorithms.<p>The new default scale values for TPSC and BTSC are 1E+09 and -1E+09.&nbsp; Since this is binary, I also added the regular numbers as well (999999999 and -999999999).</p><p>For the Squareroot algorithm the new TPSC and BTSC default values are 1E+09 and 0 respectively.</p><p><br></p><p>SS: Verified the finding successfully in U6 build.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1.Open any control sheet.</p><p>2.Go to help menu.</p><p>3.Select Algorithm guide.</p><p>4.Open the algorithms mentioned above.</p><p>5.Check the TPSC and BTSC values for each of the above mentioned algorithms.</p><p><br></p><p>Please refer attachment for better understanding.</p> |  | U4 |  |  | FINDING | [6 empty] | 94910
36039 | FINDING | "Failed to create OPH message from SIS event" messages appear in sisev.log file created at the Scanner machine | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-19 03:39 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-19 03:39 | 67091 |  |  | 2016-04-19 03:39 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-03 06:43 |  | <p>&quot;Failed to create OPH message from SIS event&quot; messages appear in sisev.log file created at the Scanner machine.</p> <p><font face="Courier New">&nbsp;OvSisEvents.Service.exe Warning: 0 : Failed to create OPH message from SIS event: Index (zero based) must be greater than or equal to zero and less than the size of the argument list.&nbsp;&nbsp; at System.Text.StringBuilder.AppendFormat(IFormatProvider provider, String format, Object[] args)<br>&nbsp;&nbsp;&nbsp; at System.String.Format(IFormatProvider provider, String format, Object[] args)<br>&nbsp;&nbsp;&nbsp; at System.String.Format(String format, Object arg0, Object arg1)<br>&nbsp;&nbsp;&nbsp; at Emerson.OvSisEvents.Core.Activities.ActivityEntry.GetMessageTemplate()<br>&nbsp;&nbsp;&nbsp; at Emerson.OvSisEvents.Core.Activities.ActivityEntry.GetMessage()<br>&nbsp;&nbsp;&nbsp; at Emerson.OvSisEvents.Core.Activities.ActivityEntry.get_Message()<br>&nbsp;&nbsp;&nbsp; at Emerson.OvSisEvents.Data.DataProcessing.HistorianMessage.OphMessage.FromActivityEntry(ActivityEntry sisEvent)</font><br></p> <p>Please find attached <em>sisev.log</em> file.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [7 empty] | Implementation | U5 |  | <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on DBS Drop100 (OS: Windows Server 2012 R2)&nbsp;</span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U4 on&nbsp;Scanner Drop159 (OS: Win 7)&nbsp;</span></span></p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | PA 04/19/2016: &quot;Failed to create OPH message from SIS Event&quot; messages are no more observed in sisev.log file on Ovation3.6.0_U6. Closing the Finding. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1. Perform any operation on CSLS to generate <em>sisev.log</em> file. |  | U4 |  |  | FINDING | [6 empty] | 95206
36043 | FINDING | The alarm shelve field of Alarm tab in point information window shows wrong sequence when shelve any alarm limit. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:44 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:44 | 67140 |  |  | 2016-04-17 06:44 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-04 03:47 |  | <p><font face="Times New Roman" size=3> </font><font face=Calibri><font size=3>If we shelve alarm limit e.g. High 4 the alarm shelve field of Alarm tab in point information window displays as </font><b><font size=3>High 1 2 3 4 HUDA</font></b><font size=3>&nbsp;instead of <b><font size=3>High&nbsp;4&nbsp;3&nbsp;2&nbsp;1 HUDA.</font></b><font size=3> </font></font></font></p><p><font face=Calibri><font size=3> The same observation is true for all the alarm limits (Please find attached snapshot “Shelve field with wrong sequence.jpg”).</font></font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>PP: 04/17/2016-Verified in Ov3.6.0_U6: When <font color="#000000">shelved alarm limit e.g. High 4 the alarm shelve field of Alarm tab in point information window displays&nbsp;</font><font color="#000000"><font size=3> <b><font size=3>High&nbsp;4&nbsp;3&nbsp;2&nbsp;1 HUDA.</font></b></font></font></font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Hence issue is resolved.</font></span><font face="Times New Roman" size=3> </font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">1. Create an analog point</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">2. Define all alarm limits</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">3. Open Point in Ovation Point Information window</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">4. Put the point into Alarm</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">5. Open Alarm window </span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">6. Right click on the point &amp; shelve the High 4 limit</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">7. Alarm shelve value shows HIGH 1 2 3 4 HUDA instead of HIGH 4 3 2 1 HUDA</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">8. Same for all alarm limits</span></p> |  | U4 |  |  | FINDING | [6 empty] | 95099
36044 | FINDING | Test case 5.2.13/d, i & 5.2.15/k & l should be removed from SVTP “3.6.0_SRF2048_SVTP_rev1.13_XX.doc”. | Joshi, Parmesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:17 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:17 |  |  |  | 2018-12-15 04:17 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-04 03:52 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Test case 5.2.13/d, i &amp; 5.2.15/k &amp; l should be removed from SVTP “3.6.0_SRF2048_SVTP_rev1.13_XX.doc” as per developers comments&nbsp; in e-mail conversation.</span></p><p><span style="color:black;line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">&quot;The UDA limits cannot be shelved separately.&nbsp;This is how the software was design.&nbsp;When you shelve the low or high limits it will also shelve the corresponding UDA limit.&quot; </span><font face="Times New Roman" size=3> </font></p> |  |  |  |  | 0 |  |  |  | <p>PP-12/15/2018: Verified in Attached TR of &nbsp;&quot;SRF2048_SVTP_rev1.14.doc&quot; &amp; found the issue is fixed.</p><p>Hence, it is closed validation.</p> | 0 |  | Ovation for Windows/Operator Station/Alarms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Operator Station/Alarms | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | PJ 12/11/2018&gt; Attached Rev 1.14 addresses the issue. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 135729
36065 | FINDING | In Ovation Security manager- Description for SIS security configuration needs to be updated with Charms related fateures | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Morris, Gilbert L AUTOSOL PWS PITT | 2016-04-05 14:44 | [11 empty] | Morris, Gilbert L AUTOSOL PWS PITT | 2016-04-05 14:44 |  |  |  | 2016-04-05 14:44 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-04 11:51 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>In Ovation Security manager- Description for SIS security configuration contains only sis Legacy feature. This needs to be included Charms features also</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><font size=3>Steps: Launch <b style="">Ovation Security Manager</b></font><font size=3>- </font><b style=""><font size=3>Manage Ovation Roles</font></b><font size=3>- Select </font><b style=""><font size=3>Allow- Full access to Ovation SIS configurations</font></b><font size=3>. </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Description for SIS security configuration:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><i style=""><font face=Calibri size=3>Permits users to create, modify and delete configuration information pertaining to Ovation Safety Instrumented System (SIS). </font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><i style=""><font face=Calibri size=3>This includes the ability to build SIS control sheets, define SIS points, IOs and perform operations like loading, locking and unlocking the logic solvers.</font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><i style=""><font face=Calibri size=3>&nbsp;For Reference screenshot of SIS Security configuration window is attached.</font></i></p><p style="margin:0in 0in 0pt;">&nbsp;</p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Description may be modified as following:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><i style=""><font face=Calibri size=3>Permits users to create, modify and delete configuration information pertaining to Ovation Safety Instrumented System (SIS). </font></i></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><strong><em><font size=3>This includes the ability to build <span style="background:yellow;">LSN</span></font><font size=3>, </font><span style="background:yellow;"><font size=3>CSLS/Logic Solver</font></span><font size=3>, SIS control sheets, define SIS points, IOs and perform operations like loading, locking and unlocking the </font></em></strong><span style="background:yellow;"><font size=3><strong><em>CSLS/</em></strong><strong><em>logic solvers</em></strong></font></span><font size=3><strong><em>.</em></strong></font></font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software | <p>If the current description called out 1508 specifically (old SIS implementation) then there might be a need to include&nbsp;LSN &amp; CSLS indications.&nbsp; Generally speaking SIS is SIS whether it is the old 1508 implementation or the new CSLS implementation.&nbsp; The description is meant to be generic.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0+Ovation Security Manager |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p><font face=Calibri>Steps: Launch <b style="">Ovation Security Manager</b><font size=3>- </font><b style=""><font size=3>Manage Ovation Roles</font></b><font size=3>- Select </font><b style=""><font size=3>Allow- Full access to Ovation SIS configurations</font></b><font size=3>. </font></font></p><p><font face=Calibri size=3><br></font></p><font face=Calibri size=3><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Description for SIS security configuration:</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><i style=""><font face=Calibri size=3>Permits users to create, modify and delete configuration information pertaining to Ovation Safety Instrumented System (SIS). </font></i></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><i style=""><font face=Calibri size=3>This includes the ability to build SIS control sheets, define SIS points, IOs and perform operations like loading, locking and unlocking the logic solvers.</font></i></p></font><p><br></p> |  | U4 |  |  | FINDING | [6 empty] | 94465
36077 | FINDING | Point toggles when performed Cutout operation by Packed point or by Digital point. | Cooper, David External Self Employed | Open | [10 empty] | 35 | FINDING |  |  |  |  | 7 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-05-27 04:53 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-05-27 04:53 | [7 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-05 03:04 |  | <p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Point toggles when performed Cutout operation by Packed point or by Digital point.</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">There are&nbsp;2 scenarios:</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">1. Cutout performed by Packed point as bit mask.</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2. Cutout performed by Digital point.</span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">&nbsp;</span></p><p><font face="Times New Roman" size=3> </font></p><p><strong><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u>Cutout performed by Packed point as&nbsp;bit mask</u></span></strong></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>1.Performing Alarm Cut-Out operation of individual alarm limits of an analog point by packed point bits we observe that <b>HUDA</b></font><font size=3> limit is not getting cutout by A2 bit 4 of packed point, however the analog point “</font><b><font size=3>Cutout&nbsp;Status</font></b><font size=3> ” field in the Alarm tab of Point Information Window shows </font><b><font size=3>HUDA</font></b><font size=3> but “</font><b><font size=3>Suppressed Alarm Status</font></b><font size=3>” field is blank and the point is still in alarm, please refer to snapshot 1.jpg. </font></font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.Also the lower alarm limits like High4, High3, High2,High1 are not getting suppressed by performing cutout of &nbsp;High User Defined Alarm, please refer to snapshot 1.jpg and 2.jpg .</font></span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><br></font></span></p><p><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>We have similar observation for LUDA alarm limit when we cutout it with A2 bit 9,please refer to snapshot 3.jpg .&nbsp;&nbsp;&nbsp;&nbsp; </font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Please refer to snapshot 4.jpg for defined alarm limits.</font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><br></font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>All the points are created in controller.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><font face="Times New Roman" size=3><p><strong><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u>Cutout performed by Digital point</u></span></strong></p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><span style="color:rgb(31, 73, 125);"><br></span></p><p><span style="color:rgb(31, 73, 125);">When we Cutout any analog point with a digital point, then &quot;<b><span style="background:yellow;">Suppressed Alarm Status&quot; field</span></b> in <b><span style="background:yellow;">the Alarm parameter section of Alarm tab in Point Information window</span></b> keeps blinking , Alarm sequence Number field keeps updating it’s value and &quot;<b><span style="background:yellow;">Time of Last Event (sec)&quot;</span></b> field (5.jpg) in Alarm Times section of Alarm tab in Point Information is also updated continuously.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><br></span></p><p><span style="color:rgb(31, 73, 125);">Following 1W Bits are also blinking (6.jpg) .</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">Bit 1, Bit 3, Bit 16.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">The same point is also toggling in Alarm Suppressed tab of Alarm window (7.jpg) .</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">This observation is same for all alarm limits.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">Points are created in controller and Ovation build is U4.</span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><br></span></p><p><span style="color:rgb(31, 73, 125);">Please refer to snapshots.</span></p><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p><p> <br></p></font><p><br></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  | <p>The problem of toggling is resolved but now have few other observations</p><p>1. If L1,L2,L3 or L4 are cutout, then LUDA is cutout also, but if I cutout any higher limit say L3 then L1,L2,L3,LUDA along with <strong>L4 is also cutout which should not happen.</strong></p><p>2. If H1,H2,H3 or H4 are cutout, then HUDA is cutout also, but if I cutout any higher limit say H3 then H1,H2,H3,HUDA along with <strong>H4 is also cutout which should not happen.</strong></p><p>3. If only LUDA is cutout then all the other alarm limits <strong>L1,L2,L3,L4&nbsp;are also cutout in the Point Information window which is not expected, but only PW bit 20 is high.</strong></p><p>4. If only HUDA is cutout then all the other alarm limits <strong>H1,H2,H3,H4&nbsp;are also cutout in the Point Information which is not expected, but only PW bit21 is high.&nbsp;</strong></p><p>5. <strong>Alarm sequence number,U4,U5,U6,U7</strong> field in the alarm tab of Point Information window are updating themselves continuously after every 3 seconds.</p><p>6. Performing cutout of&nbsp;LUDA is cutting all the lower alarm limits as well as higher alarm limits.</p><p>7. Performing cutout of HUDA is cutting all the&nbsp;higher alarm limits as well as lower alarm limits.&nbsp;</p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Augustine, Lisa EMR SYSS PWS PITT | Prasad, Parmatma EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <p>Windows7 64 Bit + Ov3.6.0</p><p>Windows Server 2012 R2 + Ov3.6.0</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u><strong>Cutout performed by Packed Point as bit mask</strong></u></span></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><strong><u></u></strong></span><br></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.Create any analog point and define alarm limits.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>2.Define a Packed Point at the “<b>Alarm cutout name”</b></font><font size=3> field ,check the “</font><b><font size=3>Treat packed alarm cutout as a bit mask</font></b><font size=3>” and check the </font><b><font size=3>Alarm cutout on zero</font></b><font size=3> field in the point record of analog point in Developer studio.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.Save the changes and load the controller where point is created.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>4.Open the analog point in&nbsp; Point Information window.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>5.Take the point in High User Define Alarm state.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>6.Open the Packed point which was defined in the point record of analog point in Point Information Window.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>7.Select A2 bit 4 of packed point set the value to zero.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>8.Verify in the Point Information window that analog point is still in alarm.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>9.Verify that “<b>Cutout Status</b></font><font size=3> ” field in the Alarm tab of Point Information Window shows </font><b><font size=3>HUDA</font></b><font size=3> but “</font><b><font size=3>Suppressed Alarm Status</font></b><font size=3>” field is blank and the point is still in alarm.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>10.Verify the lower alarm limits like High4, High3, High2, High1 are not getting cutout.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Perform similar operation for Low user defined Alarm limit.</font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><br></font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u><strong>Cutout performed by Digital Point</strong></u></span></font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><strong><u><br></u></strong></span></font></span></p><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.Create any analog point and define alarm limits.</font></span></p><font face="Times New Roman" size=3></font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>2.Define a&nbsp;Digital Point at the “<b>Alarm cutout name”</b></font><font size=3> field </font><font size=3>and check the </font><b><font size=3>Alarm cutout on zero</font></b><font size=3> field in the point record of analog point in Developer studio.</font></font></span></p><font face="Times New Roman" size=3></font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.Save the changes and load the controller where point is created.</font></span></p><font face="Times New Roman" size=3></font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>4.Open the analog point in&nbsp; Point Information window.</font></span></p></span><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>5.Take the point into any Alarm state.</font></span></p></font><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">6. Cutout the point with digital point.</span></p><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">7.Verify the point blinks for all alarm limits.</span></p><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman" size=3> </font></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">8.Verify the</span></p><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman" size=3> </font> <span style="background:yellow;color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><strong>Suppressed Alarm Status field</strong></span><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"> in <b><span style="background:yellow;">the Alarm parameter section of Alarm tab in Point Information window</span></b> keeps blinking , Alarm sequence Number field &nbsp;keeps updating it’s value and <b><span style="background:yellow;">Time of Last Event (sec)</span></b> field in Alarm Times section of Alarm tab in Point Information is also updated continuously.</span></p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p style="margin:0cm 0cm 0pt;">9.Verify the f<span style="color:rgb(31, 73, 125);">ollowing 1W Bits are also blinking .</span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"></span><span style="color:rgb(31, 73, 125);">Bit 1, Bit 3, Bit 16.</span></p><p style="margin:0cm 0cm 0pt;"><font color="#000000" face="Times New Roman" size=3><strong> </strong><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">10.The same point is also toggling in Alarm Suppressed tab of Alarm window </span></font></p></span><p style="margin:0cm 0cm 0pt;"><br></p></span><p style="margin:0cm 0cm 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 97913
36079 | FINDING | X3STEP algorithm on-line help needs changes | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2016-04-16 05:38 | [11 empty] | Lal, Ramesh External | 2016-04-16 05:38 |  |  |  | 2016-04-16 05:38 |  |  |  | Lal, Ramesh External | 2016-04-05 04:08 |  | <p>Ref: SDR#34259: X3STEP algorithm manual and on-line help changes</p><p>4/04/16: Checked OW_360_1100 Manual on Val\Tests\3.6.0\DOCS_for_Validation and found O.K.. However, there is following discrepancy in on-line help:</p><p>All the bullet points should be replaced by numbers e.g.&nbsp;1, 2, 3 .... in sections Operation, Algorithm Configuration, Tuning Parameters.&nbsp;&nbsp;</p><p>Table 11 is repeated. The last occurrence should be changed to Table 12.</p><p>Table 7: Fine pulsing : &lt; ON2 and &lt; FNE2 should be changed to&nbsp;&gt; ON2 and &lt; FNE2 </p><p>Table &quot;11&quot; is repeated. The last occurrence should be changed to Table &quot;12&quot;.</p><p>Table 15&nbsp;:&nbsp;Coarse pulsing:&gt;COR2 should be changed to &lt;COR2</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;Fine pulsing :&nbsp;&gt;FNE2&nbsp; and &lt;COR2 should be changed to&nbsp;&gt;COR2&nbsp; and &lt;FNE2 </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;OFF: &gt;0 and &lt;FNE2 should be changed to &gt;FNE2 and &lt;0</p><p>Table 16: Example DIG1......... should be changed to DIG2 ......</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Column headers DIG1, FNE1, COR1, ON1 should be changed to DIG2, FNE2, COR2, ON2 <br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; respectively&nbsp;.</p><p>&quot;Algorithm Definition&quot;&nbsp;is repeated. The last occurrence should be deleted.&nbsp;</p><p><br></p><p><br></p> | Corrected miscellaneous formatting errors for the X3STEP algorithm. |  |  | Test the X3STEP algorithm. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U5 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>LC 04/08/2016: Updated the X3STEP algorithm.&nbsp; Online help will be updated in the U5 build of 3.6.&nbsp;&nbsp; Print manual available at V:\Tests\3.6.0\DOCS_for_Validation (OW360_R1100).</p><p>The changes are as follows:</p><p>&nbsp;&nbsp;All table numbers were removed per the Documentation standards in our department. </p><p><br></p><p><br></p><p>&quot;Table 7&quot;&nbsp; Changed to ON2 and &lt; FNE2 for Fine pulsing&nbsp; </p><p>&quot;Table 15&quot;&nbsp;For&nbsp;Coarse pulsing, changed to &lt;COR2</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; For Fine pulsing :&nbsp; changed to&nbsp;&gt;COR2&nbsp; and &lt;FNE2 </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; For OFF: changed to &gt;FNE2 and &lt;0</p><p>&quot;Table 16&quot; &nbsp;Example DIG1......... was changed to DIG2 ......</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Column headers DIG1, FNE1, COR1, ON1 were changed to DIG2, FNE2, COR2, ON2&nbsp;<br></p><p>&quot;Algorithm Definition&quot;&nbsp;is no longer repeated. </p><p>All the bullet points&nbsp;remain in sections Operation, Algorithm Configuration, Tuning Parameters.&nbsp; No need to make numbers because items are not sequential. The use of bullets is correct.</p><p><br></p><p>4/16/16: Rechecked in 3.6.0_U6 and found O.K. Finding closed.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U6 |  |  | FINDING | [6 empty] | 95090
36080 | FINDING | No information available about FY record field in online help | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Swati EMR SYSS PWS NOIDA | 2016-04-29 06:00 | [11 empty] | Jain, Swati EMR SYSS PWS NOIDA | 2016-04-29 06:00 | 3.6.0_U6 |  |  | 2016-04-29 06:00 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-05 04:52 |  | The online help for record type does not contain any details of 'FY' record field. This field was added for Ovation &gt;= 3.3.1<br>Also, could not find any details of this field in older version of Ovation Record Types Reference Manual (example-OW351_R1140). | SJ April 12, 2016: No changes required to the manual. |  |  | SJ April 29, 2016: Changing the State reason to Way it Works (No plans to fix) as asked by development and validation. | 0 |  |  |  | SJ April 29, 2016: Changing the State reason to Way it Works (No plans to fix) as asked by development and validation. | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation | <p>SJ April 12, 2016: As per the developer, this <span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:11pt;">SDR is an internally written SDR. It is not required to be mentioned in the Record Types manual.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000">SJ April 29, 2016: Changing the State reason to Way it Works (No plans to fix) as asked by development and validation.</font></span></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U4 |  | Ovation 3.6.0_U4<br>Net#36 DBS Drop100 (Windows Server 2012) |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | In Validation | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | SJ April 12, 2016: No changes required to the manual. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U4 |  |  | FINDING | [6 empty] | 95933
36081 | FINDING | Test Case 5.2.15/c,d,e,f,g,h,i,j of SVTP "3.6.0_SRF2048_SVTP_rev1.13_XX.doc" need modification. | Joshi, Parmesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:18 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:18 |  |  |  | 2018-12-15 04:18 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-05 06:43 |  | <font face="Times New Roman" size=3> </font><p><font face="Times New Roman" size=3> As suggested by the developer&nbsp;via&nbsp;&nbsp;E-mail, the test Case 5.2.15/c,d,e,f,g,h,i,j&nbsp; of SVTP&nbsp; &quot;3.6.0_SRF2048_SVTP_rev1.13_XX.doc&quot; need&nbsp;modification.</font></p><p><font face="Times New Roman" size=3>Please add the text mentioned in black bold color below.<br></font><font face="Times New Roman" size=3><br></font></p><font face="Times New Roman" size=3><p><br></p><table align=left style="margin:auto 6.75pt;border-collapse:collapse;" border=0 cellspacing=0 cellpadding=0> <tbody><tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="padding:0cm;border:1pt solid windowtext;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>c) Verify if Low1 limit is shelved then 1W 26 bit=1 and PW bit0 =1 <strong>&amp; PW bit8=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:1pt 1pt 1pt 0px;border-style:solid solid solid none;border-color:windowtext windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:1pt 1pt 1pt 0px;border-style:solid solid solid none;border-color:windowtext windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>d) Verify if Low2 limit is shelved then 1W 26 bit=1 and PW bit1=1<strong>,PW bit0=1 &amp; PW bit8=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>e) Verify if Low3 limit is shelved then 1W 26 bit=1 and PW bit2=1<strong>,PW bit0=1,PW bit1=1&nbsp;&amp; PW bit8=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>f)Verify if Low4 limit is shelved then 1W 26 bit=1 and PW bit3=1, <strong>PW bit0=1,PW bit1=1,PW bit2=1&nbsp;&amp; PW bit8=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>g) Verify if High1 limit is shelved then 1W 26=1 and PW bit4=1<strong>,&nbsp;&amp; PW bit9=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>h) Verify if High2 limit is shelved then 1W 26 bit=1 and PW bit5=1, <strong>PW bit4=1&nbsp;&amp; PW bit9=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>i) Verify if High3<span style="">&nbsp; </span>limit is shelved then 1W 26 bit=1 and PW bit6=1, <strong>PW bit4=1,&nbsp;PW bit5=1&nbsp;&amp; PW bit9=1</strong>.</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> <tr style="height:15.8pt;page-break-inside:avoid;"> <td width=426 valign=top style="border-width:0px 1pt 1pt;border-style:none solid solid;border-color:rgb(0, 0, 0) windowtext windowtext;padding:0cm;width:319.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US style=""><font face=Times>j) Verify if High4 limit is shelved then 1W 26 bit=1 and PW bit7=1, <strong>PW bit4=1,&nbsp;PW bit5=1, PW bit6=1&nbsp;&amp; PW bit9=1</strong>..</font></span></p> </td> <td width=114 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:85.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>P/F/F#:</font></span></p> </td> <td width=90 valign=top style="border-width:0px 1pt 1pt 0px;border-style:none solid solid none;border-color:rgb(0, 0, 0) windowtext windowtext rgb(0, 0, 0);padding:0cm;width:67.5pt;height:15.8pt;background-color:transparent;"> <p style="margin:0cm 0cm 0pt;"><span lang=EN-US><font face=Times>Date:</font></span></p> </td> </tr> </tbody></table><p><br></p></font><p><br></p><font face="Times New Roman" size=3><p><br></p><p><br></p></font><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3><br></font></p> |  |  |  |  | 0 |  |  |  | <p>PP-12/15/2018: Verified in Attached TR of &nbsp;&quot;SRF2048_SVTP_rev1.14.doc&quot; &amp; found the issue is fixed.</p><p>Hence, it is closed validation.</p> | 0 |  | Ovation for Windows/Operator Station/Alarms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Operator Station/Alarms | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | PJ 12/11/2018&gt; Attached Rev 1.14 addresses the issue. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 135730
36082 | FINDING | Alarm status of User Defined Low Alarm Limit is not showing correctly at specific scenario. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-04-05 12:14 | [11 empty] | USPITTFSService | 2016-04-05 12:14 | [7 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-04-05 07:35 |  | When a point is in any alarm state other than user defined low alarm limit and we change the User defined low alarm limit value from PI (Limit tab) and create the alarm for the same : The observation in this case is that Alarm Status field displaying as LW/LUDA instead L4/LUDA. <br>Please note :<br>- To bring back point to show correct alarm status (L4/LUDA), we have to make the point alarm free.<br>- Same observation is not true for HIGH alarm cases.<br>- Checked&nbsp; in Lower Ovation level (OV 3.5.1) and found the same observation. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | OV 3.6.0_U4&nbsp; EWS |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Create a point with all high/low/user defined alarm limits configured and load the drop.<br>2. Open the point in PI window and generate any alarm except User Defined LOW alarm.<br>3. Change the value of &quot;User Defined Low Alarm Limit&quot; field from &quot;Limit&quot; tab of PI.<br>4. Create the User Defined Low limit alarm by entering correcponding limit value and check the alarm status <br>Observation : Alarm Status field displays LW/LUDA as seen in attached snapshot.<br>5. Take out the point from any alarm and then create the User Defined Low limit alarm again as mentioend in step-4<br>Observation: Alarm Status window field displays L4/LUDA.<br>6. Repeat all above steps for &quot;User Defined High Alarm Limit&quot;.<br>Observation: For any case (step4 &amp; 5) the Alarm Status is showing same as H4/HUDA. |  | 3.6.0_U4 |  |  | FINDING | [6 empty] | 94455
36088 | FINDING | Online Studio help, there is no information for topic "SIS Alarming with CHARMS Smart Logic Solver timestamp" | Maggu, Mukesh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:35 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:35 | 3.6.0_U7 | [6 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-05 10:03 |  | <p><font face=Calibri size=3>In Studio online help, on selection of&nbsp;topic <strong>SIS Alarming with CHARMS Smart Logic Solver timestamp&nbsp;</strong>a<strong> </strong>page gets displayed&nbsp;with&nbsp;following&nbsp;title but there is no information related to topic selected.&nbsp;</font></p><font face=Calibri size=3><p><font face=Calibri><em>The following sections describe how to configure SIS digital points for alarming with CHARMS Smart Logic Solver timestamps.</em></font></p></font><p><font face=Calibri size=3>For reference screenshot attached.</font></p><p><font face=Calibri size=3>Description/&nbsp;Information for the topic <strong>SIS Alarming with CHARMS Smart Logic Solver timestamp </strong>needs to be&nbsp;updated in online help.</font></p><p><font face=Calibri size=3><br></font></p><p><strong><font face=Calibri size=3><br></font></strong></p> |  |  |  | MM(4/27/16):&nbsp;Check the online help&nbsp;in U7 built. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation | MM(4/27/16):&nbsp;Check the online help&nbsp;in U7 built. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>MM(4/27/16): Fixed in U7 built.</p><p>Verified in U8, More than required links are available on the page. Though not related to SIS Alarming,&nbsp; topics are available on page. &nbsp;</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face=Calibri>In Studio online help, select topic <strong>SIS Alarming with CHARMS Smart Logic Solver timestamp. </strong>Page with Title&nbsp;&nbsp;<em>T</em></font><font face=Calibri><em>he following sections describe how to configure SIS digital points for alarming with CHARMS Smart Logic Solver timestamps appeared , but there is no information related to selected topic.</em></font></p> |  | U4 |  |  | FINDING | [6 empty] | 97333
36098 | FINDING | PWTTS - Controller failed during wekend soak test | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Phan, Quang EMR ENT TECH AUS | 2016-04-06 11:31 | [11 empty] | Phan, Quang EMR ENT TECH AUS | 2016-04-06 11:31 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-04-06 09:06 |  | <p>System was set up for weekend soak test with no configuration activity.</p><p>Secondary controller was in active mode, went into BAD status and couldn't recover on its own.&nbsp; Switchover to Primary controller occurred.</p><p><br></p><p>See attached for Error log capture and screenshot.</p><p><br></p><p>UPDATE: Perform a download/clear/load on Primary controller (DROP2) and note that Secondary controller (DROP52) recovered out of FAIL mode on its own.&nbsp; See attached : &quot;Error_Log_Drop52 Recoverred.xlsx&quot; file for details</p><p><br></p><p>System info:</p><p>PWTTS Test system 1</p><p>Ovation 3.6.0 build U4 with AMS 13.0</p><p>OCR400 controller</p><p>DBS w/Win Server 2012 R2 Std</p><p>OPS w/Win 7</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Ritchie, Mark AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | N/a |  | U4 |  |  | FINDING | [6 empty] | 94511
36100 | FINDING | Next button click has no effect if no switch is selected on verification page of SisSwitchConfigTool wizard. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-06 10:32 | [11 empty] | USPITTFSService | 2016-04-06 10:32 | [7 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-04-06 10:32 |  | <p>When going through the OvSis Switch Configuration Tool wizard, the next button on verification page is enabled, but clicking it has no effect until any switch is selected.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Zochowski, Michal AUTOSOL DX WRSW | Development |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94507
36103 | FINDING | PWTTS - Standby FF module report "Problem detected..." on segment while macrocycle is set within limit | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2016-04-06 14:59 | [11 empty] | USPITTFSService | 2016-04-06 14:59 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-04-06 14:59 |  | <p>A redundant FF is configured with 15 devices on port 1 and 8 devices on port 2.&nbsp; Some function blocks from some devices are configures on control module.&nbsp; See attached for details.</p><p>Macro-cycle is configured to meet requirement for port 1 (1 second) and port 2 (2 second).</p><p>Standby module kept report problem detected on port 2 every 1-3 minutes.</p><p>Problem went away after macro-cycle on port 2 change to 5 seconds from 2 seconds.</p><p><br></p><p><br></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Firmware/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Wood, Thomas T AUTOSOL PWS PITT | Plymire, Alvan AUTOSOL PWS PITT | Ritchie, Mark AUTOSOL PWS PITT | [6 empty] | Implementation |  |  | <p>System info:</p><p>PWTTS Test System 1</p><p>OCR400 controller</p><p>DBS - WinServer 2012 R2 with Ovation 3.6 build U4 and AMS 13.0</p><p>OPS - Win7</p> |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Set macro-cycle to minimum requirement.&nbsp; Will or will not reproduce issue. |  | U4 |  |  | FINDING | [6 empty] | 94522
36105 | FINDING | Conversion Type in Instrument Tab should be on the list of attributes for default Analog and Deluxe Analog points, The benefit is Conversion Type would be copied to a new LA/DA point. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-18 23:55 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-18 23:55 | 67224 |  |  | 2016-04-18 23:55 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-07 03:19 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Observation for Analog (LA Type) and Deluxe Analog(DA) point:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);">Performed Copy operation for Analog&nbsp;/&nbsp;Deluxe Analog point. Conversion Type in Instrumentation Tab not copied to new point.</span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>If the object to be copied has a corresponding default object type, then the list of attributes which are copied from the source object is based on the list of attributes in the default object type.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>In Default Analog Point, there are a number of attributes on the Instrument Tab.&nbsp; However, Conversion Type is not one of them.&nbsp; As a result, the copy operation is not including this attribute when it takes values from the source object to the new copy.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Conversion Type in Instrument Tab should be on the list of attributes for default Analog and Deluxe Analog points, The benefit is Conversion Type would be copied to a new LA/DA point.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>The affected area is in the list of attributes applicable to the default analog and default deluxe analog point objects.&nbsp; The Conversion Type will now be included.&nbsp; This will also enable the attribute to be included during a copy operation.</p><p>Recommended testing for the issue itself should be obvious.&nbsp; In addition, the value of the Conversion Type attribute should be changed in the default objects to verify that a newly created point (of the corresponding type) will initial have the value as defined in the default object.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | 3.6.0+ Ovation Developer Studio |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>As stated in the Description, the issue is that the Conversion Type is not in the list of attributes applicable for default analog and default deluxe analog point objects.&nbsp; This attribute will be included in the default objects.</p><p>VP 04/19- Verified 3.6.0_U6,&nbsp; the Conversion Type&nbsp;attribute included during a copy operation of &nbsp;analog and default deluxe analog point. Finding is closed.</p> | 6 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U4 |  |  | FINDING | [6 empty] | 95188
36107 | FINDING | Incorrect help links are opening for FG,FH,FI fields on point information window. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:28 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:28 | 3.6.0_U7 |  |  | 2016-05-13 04:28 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-07 05:36 |  | <p>Incorrect help links are opening for FG,FH,FI fields on point information window.</p> | <p>SJ April 12, 2016: Added help ids to FG, FH, and FI record fields topics.</p><p>SJ April 25, 2016: Added help ids to FG, FH, and FI record fields topics.</p> |  |  | <p>SJ April 12, 2016: Added help ids to FG, FH, and FI record fields topics. Check OvationApplications online help in Ovation 3.6.0 U5 build.</p><p>SJ April 25, 2016: Latest online help was not picked in U5/U6. Kindly check&nbsp;OvationApplications online help in Ovation 3.6.0 U7 build.</p> | 0 |  |  |  | <p>LB 05/13/16-Verified on Ovation3.6.0_U7 and observed that correct help links are opening for FG,FH,FI fields on point information window. Hence this finding is closed by validation<br></p> | 0 |  | Ovation for Windows/Operator Station/Point Information/Documentation | <p>SJ April 12, 2016: Added help ids to FG, FH, and FI record fields topics. Check OvationApplications online help in Ovation 3.6.0 U5 build.</p><p>SJ April 25, 2016: Latest online help was not picked in U5/U6. Kindly check&nbsp;OvationApplications online help in Ovation 3.6.0 U7 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>Ovation 3.6.0_U4</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>SJ April 12, 2016: Check Ovation 3.6.0 U5 build.</p><p>SJ April 25, 2016: Check Ovation 3.6.0 U7 build.</p><p><br></p><p><br></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open&nbsp; a drop point&nbsp;using point information.</p><p>2)Select status Tab.</p><p>3)Under faults; try to open the help file of FG,FH,FI field.</p><p>Observation: Click on any of the above mentioned fields open help for FO field only.</p> |  | U4 |  |  | FINDING | [6 empty] | 96771
36119 | FINDING | When shelve a point which is in sensor alarm then the value of “Suppressed alarm status’ (bit27) of 1W field is 0 instead of 1. | Cooper, David External Self Employed | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Cooper, David External Self Employed | 2019-03-20 05:42 | [11 empty] | Cooper, David External Self Employed | 2019-03-20 05:42 | [7 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-08 00:16 |  | <font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>As&nbsp;suggested by developer via E-mail conversation.</font></span><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>When shelve a point <b>which is in sensor alarm</b></font><font size=3> then the value of “Suppressed alarm status’ (bit27) of 1W in point information window in alarm tab is showing 0 value instead of 1.</font></span><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;line-height:18pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>&nbsp;</font></span></p><p><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>Note: As per developer When shelve a point <b>which is in sensor alarm</b></font><font size=3> then the below filed bits should be as below:</font></span><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3><span>&nbsp; </span></font><font size=3>PW = 0</font></span><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>&nbsp;1W bit 26 = 1 </font></span><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 10pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3><span>&nbsp;</span></font><font size=3>1W 27 = 1 </font></span></p><p style="margin:0cm 0cm 10pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"></span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>1W 7 = 0&nbsp; </font></span></p><p style="margin:0cm 0cm 10pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"></span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>1W 5 = 0&nbsp;&nbsp; </font></span></p><p style="margin:0cm 0cm 10pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>PP:04/11/2016- Same issue is observed for Sensor alarm when CutOut either with digital point or packed point bit.</font></span></p><p style="margin:0cm 0cm 10pt;"><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">PP:05/24/2016-The above issues are verified in Ov3.6.0_U9 but the problems still persists.</font></span></font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | Added code to set bit 27 when in sensor alarm and cutout or shelved. Cutout sensor alarm option must be enabled. Also had to clear bit 27 when in sensor alarm and NOT cutout or shelved. Had to tweak the code to issue alarm messages. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Augustine, Lisa EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | Minor code changes to set bit 27 when in sensor alarm and cutout or shelved. | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">1. Create a hardware point e.g&nbsp;analog point</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">2. Define all alarm limits</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">3. Open Point in Ovation Point Information window</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">4. Remove the Modules</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">5. Now point&nbsp;is in&nbsp;Sensor alarm</span></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">6. Right click on the point &amp; shelve the whole point</span></p><p></p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><p>7. The Value of&nbsp;&quot;Suppressed alarm status (Bit27) of 1W is showing 0&quot;&nbsp;&nbsp;<font size=3> </font></p><p style="margin:0cm 0cm 10pt 36pt;line-height:18pt;"><br></p></span><p style="margin:0cm 0cm 10pt 36pt;line-height:18pt;"><br></p><p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><br></span></p> |  | U4 |  |  | FINDING | [6 empty] | 139634
36120 | FINDING | For "Alarm Shelve Shift configuration" When shelved the point in point information window from ribbon bar shelve button then no display warning message is displayed. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-13 04:15 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-13 04:15 | 67513 |  |  | 2016-05-13 04:15 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-08 00:22 |  | <p><font face="Times New Roman" size=3> </font><font face=Calibri><font size=3><strong>For Display Warning</strong>: Configured “Action For Shelve Operation that Cross Shift” for <b>Display Warning</b></font><font size=3> option &amp; Downloaded , rebooted the concerned drop.</font></font><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri><b><font size=3>Observation</font></b><font size=3>: 1. When we shelve via right click on point information window then we got a popup message window as “Display_Warning.jpg”. Please find attached snapshot of “Display_Warning.jpg”.</font></font><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt 36pt;"><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 2. When we shelve the point in point information window from ribbon bar shelve button then no display warning message is display.</font></p><p><font face=Calibri size=3><br></font></p><font face=Calibri size=3><font face=Calibri size=3><p style="margin:0cm 0cm 0pt 36pt;"><strong>For Display Error</strong>: We configured “Action For Shelve Operation that Cross Shift” for <b>Display Error</b> option &amp; Downloaded ,rebooted the concerned drop.</p><p style="margin:0cm 0cm 0pt 36pt;"><font face="Times New Roman"></font><b>Observation</b>: 1. When we shelved via right click on point information window then we got a popup message window as “Display_Error.jpg”. Please find attached snapshot of “Display_Error.jpg”.</p><p style="margin:0cm 0cm 0pt 36pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 2. When we shelved the point in point information window from ribbon bar shelve button then no display Error message is displayed.</p><p style="margin:0cm 0cm 0pt 36pt;"><br></p><p style="margin:0cm 0cm 0pt 36pt;">PP:05/13/2016- The above issues are verified in Ov3.6.0_U7 &amp; found the issues are fixed.</p></font><p><br></p></font><p><br></p><font face=Calibri size=3><p><br></p><p style="margin:0cm 0cm 0pt 36pt;"><br></p></font><font face=Calibri size=3><p style="margin:0cm 0cm 0pt 36pt;"><br></p><p style="margin:0cm 0cm 0pt 36pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0cm 0cm 0pt 36pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | [6 empty] | Implementation | 3.6.0_U7 |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. C<span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">onfigured “Action For Shelve Operation that Cross Shift” for <b>Display Warning</b> option under network level.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2. Inserted New Shift Time &amp; Configured &quot;Shift Number&quot;&nbsp;, &quot;Shift Time&quot;&nbsp;.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3. Press O.K. button.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">4. Download &amp; Rebooted the concern drop.</span></p><p>5. Shelve the point vi ribbon bar shelve button then <font face=Calibri size=3>no display warning message is displayed.</font></p><p><font face=Calibri size=3>6. <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">When&nbsp; shelve via right click on point information window then we got a popup window for warning message</span></font></p><p><font face=Calibri size=3><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></font></p><p><font face=Calibri size=3><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Note: The above steps also performed for <strong>Display Error</strong>.</span></font></p><p><font face="Times New Roman" size=3> <br></font></p> |  | U4 |  |  | FINDING | [6 empty] | 96767
36121 | FINDING | For "Alarm Shelve Shift configuration" time Shift window under Network Level, if shift time is changed, there is no download file in download/query window. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-13 04:16 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-13 04:16 | 67515 |  |  | 2016-05-13 04:16 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-08 00:30 |  | <p>There is no download file in download/query window if&nbsp;the shift time&nbsp;is changed&nbsp;for &quot;Alarm Shelve Shift configuration&quot; of&nbsp; time Shift window under Network Level.</p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Also, no prompt window appears when we shelve the point before end of the shift.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">PP:05/13/2016- The above issue&nbsp;is verified in Ov3.6.0_U7 &amp; found the issue&nbsp;is fixed.</span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | [6 empty] | Implementation | 3.6.0_U7 |  | Ov3.6.0_U4,Ws12R2,OCR400G02 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. C<span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">onfigured “Action For Shelve Operation that Cross Shift” for <b>Display Warning</b> option under network level.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2. Inserted New Shift Time &amp; Configured &quot;Shift Number&quot;&nbsp;, &quot;Shift Time&quot;&nbsp;.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3. Press O.K. button.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">4. Download &amp; Rebooted the concern drop.</span></p><p>5. Again changed the Shift time only </p><p><font face=Calibri size=3>6. <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">There is no download file in download/query window &amp; also no prompt window appeared when we shelve the point before end of the shift.</span></font></p> |  | U4 |  |  | FINDING | [6 empty] | 96768
36122 | FINDING | Help file is showing incorrect data for compact flash memory. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-18 05:37 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-18 05:37 | 67256 |  |  | 2016-04-18 05:37 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-08 03:15 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;page-break-after:avoid;"><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;">As per the controller enhancements SRF2137&nbsp;on ovation 3.6.0.</span>.</span></font></font></span></p><p style="margin:0in 0in 0pt;page-break-after:avoid;"><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;"></span>Ovation Controller’s in Ovation 3.6.0 shall be upgraded to use 1 Gigabyte Compact Flash Cards.<span style="">&nbsp; </span></font><font size=3>The previous capacity was 128 Megabytes.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>The increased capacity shall permit future enhancements regarding increased point count, oscillography, and new IO module firmware.</font></font></span></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>MG 18/04/2016: According to this finding, updated the <strong>Section 1.5 Features and&nbsp;specifications of the OCR 1100 controllers</strong> of the Controller (OCR 1100) user guide for Ovation 3.6. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp; <a href="file://uspit-fp05/Ohara/Communication/TechComm/Share/For">\\USPIT-FP05\Ohara\Communication\TechComm\Share\For</a> Megha Ovation 3.6.0 manuals\Manuals\OW360_58\OW360_58.pdf</p><p>Online help: <a href="file://uspit-fp04/SourceIntegrity/TechWriters/3.6.0CHMs/OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a></p> | 0 |  |  |  | Verified on Ovation3.6.0_U6 and observed that compact flash memory details are&nbsp;described as per the SRF2137 on OvPtStudio360 help file. Hence this finding is closed by validation | 0 |  | Ovation for Windows/Engineering Tools/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | Ovation3.6.0_U4 |  | Ovation for Windows | Ovation | Engineering Tools/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | MG 18/04/2016: This finding has been fixed and is available in U6 build. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio help file and verify the&nbsp;compact flash memory details.</p><p>Screenshot is also attached for your reference</p> |  | U4 |  |  | FINDING | [6 empty] | 95119
36123 | FINDING | Help file is showing incorrect data for DDBs. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-18 03:23 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-18 03:23 | 67256 |  |  | 2016-04-18 03:23 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-08 03:16 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;page-break-after:avoid;"><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;">As per the controller enhancements SRF2137 on ovation 3.6.0.</span></font></font></span></font></font></span></p><p style="margin:0in 0in 0pt;page-break-after:avoid;"><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;"><font face="Times New Roman"><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;"></span></font></font></span>The maximum of DDBs shall be increased in Ovation Developer’s Studio from 3072 to 4000.<span style="">&nbsp; </span></font><font size=3>It shall be recommended that the user not increase the number of DDBs above 3072 for networks containing OCR400 type controllers.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>The default setting for this will be changed from 1024 to 3072.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;page-break-after:avoid;"><span style="color:black;"><font face="Times New Roman" size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>MG 18/04/2016: According to this finding, updated the description of the field Maximum Number of DDBs in&nbsp;<strong>Section 5.3.1 To modify the network DDB configuration</strong>&nbsp;of the Developer Studio User Guide for 3.6.0. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp; <a href="file://uspit-fp05/Ohara/Communication/TechComm/Share/For">\\USPIT-FP05\Ohara\Communication\TechComm\Share\For</a> Megha Ovation 3.6.0 manuals\Manuals\Developer Studio User Guide (OW360_60)\OW360_60.pdf</p><p>Online help: <a href="file://uspit-fp04/SourceIntegrity/TechWriters/3.6.0CHMs/OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a></p> | 0 |  |  |  | Verified on Ovation3.6.0_U6 and observed that DDB configuration details are&nbsp;described as per the SRF2137 on OvPtStudio360 help file. Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Engineering Tools/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | <blockquote style="margin-right:0px;" dir=ltr><p>Ovation3.6.0_U4</p></blockquote> |  | Ovation for Windows | Ovation | Engineering Tools/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | MG 18/04/2016: This finding has been fixed and is available in U6 build. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio help file and verify the&nbsp;DDB Configuration&nbsp;details.</p><p>Screenshot is also attached for your reference</p> |  | U4 |  |  | FINDING | [6 empty] | 95112
36124 | FINDING | Alarm Tab field desciption table is missing on help file | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 03:31 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 03:31 | 3.6.0_U8 |  |  | 2016-05-23 03:31 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-08 03:16 |  | Alarm Tab field description table is missing on help file |  |  |  | <p>MG 19/04/2016: According to this finding, added the&nbsp;hyperlink to the topic Alarm tab fields for Long Packed and Deluxe Packed points in the <strong>Section&nbsp;8.6.6 Configuring Deluxe Packed (DP) point types&nbsp;</strong>of the&nbsp;Developer Studio&nbsp;User Guide for 3.6.0. This is available in online help for U6 build.</p><p>The updated Online help is placed at: <a href="file://\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio">\\USPIT-FP04\SourceIntegrity\TechWriters\3.6.0CHMs\OvptStudio</a></p><p><br></p><p>LC 04/22/2016: Added cross-reference links to jump to other tables. Will be available in 3.6.0_U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 0 |  |  |  | <p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that alarm tab field description table contains hyperlinks for LA,DA,LD,DD,LP,DP,DU,RM,RN points. Hence this finding is closed by validation.</p> | 0 |  | Ovation for Windows/Engineering Tools/General/Documentation | Assigning it to Megha as it is related to cross reference mismatch in Dev studio book. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | Ovation3.6.0_U4 |  | Ovation for Windows | Ovation | Engineering Tools/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG 19/04/2016: This finding has been fixed and is available in U6 build.</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio help file and verify the&nbsp;Alarm Tab field description table.</p><p>Screenshot is also attached for your reference</p> |  | U4 |  |  | FINDING | [6 empty] | 97455
36125 | FINDING | Help file is showing incorrect data for OCR1100 maximum point limit. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 01:41 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 01:41 | 67256 |  |  | 2016-05-17 01:41 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-08 03:17 |  | <font face="Times New Roman"><font size=3><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;">As per the controller enhancements SRF2137 on ovation 3.6.0&nbsp;&nbsp;.</span><p style="margin:0in 0in 0pt;"> <span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">The OCR 1100 Controller shall be configured with maximum point and memory values by default.<span style="">&nbsp; </span>Developer Studio options will be removed for the following:</span></p><p style="margin:0in 0in 0pt;"> <span style="font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:12pt;">1)Maximum Point Limit (Normal, Expanded, 32000)</span> </p><p style="margin:0in 0in 0pt;">2)&nbsp;<span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configuration/Controller/System Memory (Normal, Expanded)</span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">3)</span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configuration/Controller/Shared Memory Size MB</span> </p><p style="margin:0in 0in 0pt;"> <br></p><p style="margin:0in 0in 10pt;"><span style="line-height:115%;font-size:12pt;"><font face=Calibri>&nbsp;</font></span></p><p style="margin:0in 0in 0pt;"> <br></p></font><p style="margin:0in 0in 0pt;"><br></p></font><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>MG (April 25, 2016): According to this finding, updated the screenshot and&nbsp;the field description in the&nbsp;<strong>Section 5.4.1 To insert the new Controller drop </strong>of the Controller (OCR 1100) user guide for Ovation 3.6. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U6 build.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Documentation | <p>MG (April 25, 2016): According to this finding, updated the screenshot and&nbsp;the field description in the&nbsp;<strong>Section 5.4.1 To insert the new Controller drop </strong>of the Controller (OCR 1100) user guide for Ovation 3.6. This is available in online help for U6 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U6 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U6 |  | Ovation3.6.0_U4 |  | Ovation for Windows | Ovation | Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 25, 2016): This finding has been fixed and&nbsp;is available in U6 build.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developer studio help file and verify the Maximum point limit details for OCR 1100 Controller.</p><p>Screenshot is also attached for your reference</p> |  | U4 |  |  | FINDING | [6 empty] | 97022
36126 | FINDING | Point Review shows Alarm Shelve as well as Alarm Check ON/OFF ribbon buttons disabled when only "Allow alarm check on-off" is disabled from Ovation Security Manager for a newly created account | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sharma, Satish AUTOSOL PWS NOIDA | 2016-05-13 01:05 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-05-13 01:05 | 67513 |  |  | 2016-05-13 01:05 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-08 03:40 |  | <p>Point Review&nbsp;shows&nbsp;Alarm Shelve&nbsp;as well as Alarm Check ON/OFF ribbon buttons disabled when only &quot;Allow alarm check&nbsp;on-off&quot; is disabled from Ovation Security Manager for a newly created account.</p><p>The Point Review should only disable Alarm Check ON/OFF and not Alarm Shelve/Unshelve button when &quot;Allow alarm check&nbsp;on-off&quot; and &quot;Allow highly managed&nbsp;alarm shelve on-off&quot; is disabled in the Ovation&nbsp;Security Manager for the newly created account.&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U7 |  | <p>Windows 2012 R2 + Ov3.6.0</p><p>Windows7 64 Bit + Ov3.6.0</p> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>The shelve button on the ribbon bar in Point Review should only be disabled when the network is a pre-3.6.0 network or BOTH the shelve and shelve highly managed alarms are disabled.&nbsp; If only the shelve highly managed alarms is disabled, this option should be enabled on the ribbon bar.</p><p><br></p><p>Fix tested and found to function as mentioned in the above comment. Fix is tested in U7 build.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.Create an account from &quot;Manage Ovation Security&quot; and set operator role with &quot;Allow alarm check on-off&quot; and &quot;Allow highly managed&nbsp;alarm shelve on-off&quot; is disabled for local as well as remote console.</p><p>2.Login in with newly created account.</p><p>3.Open Point Review window.</p><p>4.Select any point and verify that both the options (Alarm Check ON/OFF and Alarm Shelve/Unshelve)&nbsp;are disabled in ribbon button.</p><p>5.Please refer to snapshot PointRev.jpg</p> |  | U4 |  |  | FINDING | [6 empty] | 96747
36127 | FINDING | Ovation Error log is getting flooded with DDB errors for SIS & NON SIS controllers after using OvPtSysApi.dll binary. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:37 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-17 06:37 | U5 |  |  | 2016-04-17 06:37 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-08 04:38 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>As per&nbsp;Mikolaj suggestion, we have replaced the OvSisSw.dll (File version-3.6.0.9999 &amp; size-157KB) file in the Ovation\OvationBase folder in DBS drop100 for fix of F#35853</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Steps followed:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><font size=3><span style="color:rgb(31, 73, 125);"><font face=Calibri>1.</font></span><span style="color:rgb(31, 73, 125);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; R</span><span style="color:rgb(31, 73, 125);"><font face=Calibri>ebooted DBS drop100. </font></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><font size=3><span style="color:rgb(31, 73, 125);"><font face=Calibri>2.</font></span><span style="color:rgb(31, 73, 125);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri>Once drop100 is up, tried to load the Logic solver followed by downloaded, </font></span></font></p><p style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><font size=3><span style="color:rgb(31, 73, 125);"><font face=Calibri>3.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Clear &amp; loaded the SIS controller drop27/77. </font></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;line-height:18pt;text-indent:-18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">&nbsp;</span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>We have observed the DDB issue on our Ov3.6.0_U4 build on SIS network. We Tried to investigate this and think that it is due to binary (OvPtSysApi.dll).</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Following steps were done while investigation:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><font size=3><font face=Calibri><b><u><span style="color:rgb(31, 73, 125);">Initial State without binary (</span></u></b><span style="color:rgb(31, 73, 125);">OvPtSysApi.dll<b><u>):</u></b></span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Performed Download, reboot and load operation on OCR400 G02 and OCR1100 G01 successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>We have verified the DDB-largesize=1432 “ddb.cnf.drop27” &amp; “ddb.cnf.drop23”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>After using Binary:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Copied binary and rebooted the DB Server.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Once DB Server came up, performed download reboot and load operation on OCR400 G02 and OCR1100 G01</font></span></p><font face="Times New Roman"><font size=3> </font><font size=3> </font></font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Results:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);font-family:Symbol;"><font size=3>·</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>OCR400 G02,IOIC G03:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Downloaded OCR400 controller successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Rebooted the controller drop27 </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Ping response break time to time &amp; then verified the DDB-largesize=1424 “ddb.cnf.drop27”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);font-family:Symbol;"><font size=3>·</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>OCR1100 G01,IOIC G03:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Downloaded OCR1100 controller successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Rebooted the controller drop23 </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Ping response break time to time &amp; then verified the DDB-largesize=1424 “ddb.cnf.drop27”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>Ovation Error log is getting flooded with DDB errors from both the controller.</font><font size=3> Please find attached Ovation Error log for drop23 as “SIS Controller (Drop23)_DDB_Error.jpg ”.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Please note that it affects NON-SIS controller also.</font></span></p><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>PP:04/17/2016-Verified in Ov3.6.0_U6 &amp; found the Ovation Error log is not flooded with&nbsp;DDB errors for SIS &amp; NON SIS controllers after download &amp; rebooted the controllers but I have a observations which&nbsp;are tracked by F#36018.</font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Hence it is closed.</font></span></p></font><p style="margin:0cm 0cm 10pt;"><br></p></span><p style="margin:0cm 0cm 10pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | [5 empty] | Implementation | U5 |  | Ov3.6.0_U4,DBS drop100 (Ws12R2),SIS Controllers (OCR400G02 IOICG03 &amp; OCR1100G01 IOICG03) |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>We have observed the DDB issue on our Ov3.6.0_U4 build on SIS network. We Tried to investigate this and think that it is due to binary (OvPtSysApi.dll).</font></span><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Following steps were done while investigation:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><font size=3><font face=Calibri><b><u><span style="color:rgb(31, 73, 125);">Initial State without binary (</span></u></b><span style="color:rgb(31, 73, 125);">OvPtSysApi.dll<b><u>):</u></b></span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Performed Download, reboot and load operation on OCR400 G02 and OCR1100 G01 successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>We have verified the DDB-largesize=1432 “ddb.cnf.drop27” &amp; “ddb.cnf.drop23”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>After using Binary:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Copied binary and rebooted the DB Server.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Once DB Server came up, performed download reboot and load operation on OCR400 G02 and OCR1100 G01</font></span></p><font face="Times New Roman"><font size=3> </font><font size=3> </font></font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Results:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);font-family:Symbol;"><font size=3>·</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>OCR400 G02,IOIC G03:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Downloaded OCR400 controller successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Rebooted the controller drop27 </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Ping response break time to time &amp; then verified the DDB-largesize=1424 “ddb.cnf.drop27”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 36pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);font-family:Symbol;"><font size=3>·</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><b><u><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>OCR1100 G01,IOIC G03:</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Downloaded OCR1100 controller successfully.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Rebooted the controller drop23 </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt 72pt;text-indent:-18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3.</font></span><span style="color:rgb(31, 73, 125);line-height:115%;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Ping response break time to time &amp; then verified the DDB-largesize=1424 “ddb.cnf.drop27”.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><font size=3>Ovation Error log is getting flooded with DDB errors from both the controller.</font><font size=3> Please find attached Ovation Error log for drop23 as “SIS Controller (Drop23)_DDB_Error.jpg ”.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Please note that it affects NON-SIS controller also.</font></span></p><font face="Times New Roman" size=3> </font> |  | U4 |  |  | FINDING | [6 empty] | 95098
36128 | FINDING | Reminder to add drop failure for OCR1100 when flash is less than 1Gb | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-25 01:00 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-25 01:00 | 67659 |  |  | 2016-05-25 01:00 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-08 06:19 |  | Add drop failure if OCR1100 controller Compact Flash is less than 1Gb. |  |  |  | If using a compact flash less than 1Gb, controller will not start after it has been downloaded and rebooted. It will fail with the following message in the error log:<div>&quot;The compact flash card size is too small or couldn't be determined&quot;<br></div> | 0 |  |  |  | LB 05/25/16-Verified on Ovation 3.6.0_U9 and observed that error log is throwing a message:&quot;The compact flash card size is too small or couldn't be determined&quot;,If using a compact flash less than 1Gb, state of controller was failed mode after download and reboot. Screenshot is also attached for your reference.<br> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  |  | 7 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U4 |  |  | FINDING | [6 empty] | 97664
36140 | FINDING | The test Case 5.19 (4) should be modified for SVTP “3.6.0_CB_SVTP_rev_2.8_PP.doc”. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-04-09 05:11 | [11 empty] | USPITTFSService | 2016-04-09 05:11 | [7 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-09 05:11 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">The test case 5.19 (4) should be modified for SVTP “3.6.0_CB_SVTP_rev_2.8_PP.doc” as per below:</span><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">In test case 5.19 (4) ,&nbsp;groupshape to be&nbsp; replaced by GraphicShape&nbsp; . Please find attached snapshot of “GraphicShape.jpg”.</span><font face="Times New Roman" size=3> </font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U4,Win764B |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94670
36141 | FINDING | Uninstall Ov-3.6.0 U4 or U5 from a DC (OSS only) fails | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-09 12:56 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-09 12:56 | 67241 |  |  | 2016-05-09 12:56 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-09 08:25 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri>Uninstall Ov-3.6.0 U4 or U5 from a DC (OSS only) fails and must be aborted.</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri>The uninstall is looking for an OvSisEventService directory on the DC and forces an Abort without uninstalling.</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri>Error:</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp; Setup was unable to execute the file</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp; C:\Ovation\OvSisEventService\OvSisEvents.Service.exe -uninstall</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp; Setup will be aborted.</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri></font></font></span>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri>The workaround is to copy that directory from a DBS to the DC, run the uninstall, delete the directory</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri>and then install U5. </font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3><font face=Calibri></font></font></span>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>The problem exists when uninstalling both U4 &amp; U5.</font></span></p><span style="COLOR:#1f497d;"> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="COLOR:#1f497d;"><font size=3 face=Calibri>&nbsp;</font></span><span style="COLOR:#1f497d;"><font size=3 face=Calibri>The problem does not come up on a DBS, &nbsp;DC+DBS or OpSt ( I didn’t try a Base station yet).</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"></span>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software | <p>Events service is installed/uninstalled on dbs and ops only.</p> <p>---</p> <p>msb - 4/19/2016 -</p> <p>Failed in U6 (ChangeSet&nbsp; 67256). </p> <p>The same error still occurs when trying to remove U6 from OSS drop.</p> <p>---</p> <p>msb - 5/09/2016 - </p> <p>OK in U7</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>The issue has been fixed.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U5 |  |  | FINDING | [6 empty] | 96495
36145 | FINDING | SDR 35243 failed | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-04-28 13:39 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-04-28 13:39 |  |  |  | 2016-04-28 13:39 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-10 00:58 |  | <p>As per validation steps of SDR 35243 (<span class=info-text>Slow performance Ovation System Viewer) mouse over information of drop removed but this information still exist in Oation 3.6.0_U4.</span></p><p><span class=info-text>Hence this SDR is failed for Ovation 3.6.0.</span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation : 3.6.0_U4</p><p>OS : WS12-R2 &amp; WIN7-64 bit</p> |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the&nbsp; system viewer from&nbsp; Start menu &gt; Ovation Applications</p><p>2. Expand the hierarchy to reach at drop level</p><p>3. Mouse over to drop , it gives drop&nbsp;information (please refer attached snapshot )</p><p>&nbsp;&nbsp; However as per&nbsp;information (d)&nbsp;available in VALIDATION tab&nbsp;of SDR &quot;mouse over for the drop information no longer exists&quot;</p><p>&nbsp;&nbsp; </p> |  | U4 |  |  | FINDING | [6 empty] | 95908
36146 | FINDING | Profibus and DeviceNet devices are not getting scanned through Ovation Net Device configuration tool in OCR1100 controller | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-25 04:12 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-25 04:12 |  |  |  | 2016-04-25 04:12 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-10 23:29 |  | It has been observed that in case of OCR1100 controller, Profibus and DeviceNet devices are not getting scanned in Ovation Net Device configuration tool. However, these devices are properly getting scanned in Ovation Net device configuration tool in case of OCR400 controller. Please&nbsp;refer the attached snapshot. |  |  |  |  | 0 |  |  |  | ST:04/25&gt; Performed Clear and load operation to the OCR1100 controller, but still DeviceNet devices were not getting scanned. So configured DeviceNet and Profibus modules on another set of OCR1100 controller(G02IOIC) and on this controller pair Profibus and DeviceNet devices are getting properly scanned. So closing this finding. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab, Ov3.6.0_U4, </p><p>OCR1100 (G02_IOIC):Drop27/77</p><p>DBS220</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>This seems to work in the validation lab, however on my 3.5.0 system I can do a scan and nothing shows up in the device assignment list. There is something wrong with my Profibus setup, but the communication between the configuration tool and the controller is working.</p><p><br></p><p><br></p><p>To confirm this attach a USB cable to the controller to get a VxWorks prompt.</p><p>set odm_test_mode = 1</p><p>When I do a scan this is what I see:</p><p>-&gt; odm_test_mode=1<br>odm_test_mode = 0x1154f90: value = 1 = 0x1<br>-&gt; write 104 to the message queue<br>received new connection id 104<br>received 4 byte message on desc 104<br>ODM Board Select Command<br>get hardware list returned 0 addresses of type PROFIBUS<br>failure getting hw list: failed getting device object for device 2.<br>get hardware list returned 0 addresses of type PROFIBUS<br>failure getting hw list: failed getting device object for device 3.<br>get hardware list returned 0 addresses of type PROFIBUS<br>failure getting hw list: failed getting device object for device 4.<br>get hardware list returned 0 addresses of type PROFIBUS<br>failure getting hw list: failed getting device object for device 5.<br>get hardware list returned 0 addresses of type PROFIBUS<br>send response message 1460 bytes<br>connection was broken<br>close the connection</p><p><br></p><p>The scan is working but for some reason no hardware is found.</p><p><br></p><p>ST(04/15/2016): Profibus devices (Segments)&nbsp;are getting properly scanned in OCR1100 controller through Net Device configuration tool&nbsp;but Device Net devices are not.</p><p>Please refer the attached snapshot <strong>(DevicenetScan.jpg), </strong>which shows DeviceNet BusModule is configured at location 1.2.3 and&nbsp;Profibus BusModule is configured at location 1.2.4.</p><p>But Net Device configuration tool is able to scan only Profibus devices (Segments).&nbsp;Please advise if you need more information.<br></p><p><br></p><p>Did you try a clear and load? I just did that on my system and the scans now work.</p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Performed Below&nbsp;steps:</p><p>1. Added an I/O Driver and I/O Device&nbsp;for&nbsp;DeviceNet module.</p><p>2.Added a&nbsp;DeviceNet module to a slot and assigned a module point to it. &amp; assigned&nbsp;node points to its nodes. (P01 &amp; P02)</p><p>3. Clicked <strong>Engineer</strong> option from right click context menu of P01 port of module. SYCON tool opens</p><p>4. Added a WAGO device to the P01 segment and assigned a node point to the device.</p><p>5. Clicked <strong>Configuration&nbsp;</strong>option from right click&nbsp;context menu of DeviceNet master device (P01), net Device configuration tool opens.</p><p>6. Configured Active Scan Range ( IP start Address: <strong>192.168.26.27</strong> &amp; IP END address: <strong>192.168.26.77</strong>) and Scan Time (10000 ms)</p><p>&nbsp;of DeviceNet module P01 port (master) from netDevice-Configuration tool and save the settings. </p><p>7. Configured WAGO device and assigned&nbsp; Ovation points to the inputs and&nbsp;outputs&nbsp;of WAGO device.</p><p>8. Saved settings and performed Download, Clear, Load operation to controller pair.</p><p>9. Reopened SYCON&nbsp;tool for port P01 of DeviceNet Module and Clicked <strong>Configuration&nbsp;</strong>option from right click context context menu of DeviceNet master device, net Device configuration tool opens.</p><p>10. From <strong>Device Assignment</strong> option of the Net Device configuration tool clicked <strong>Scan </strong>option to scan the available Profibus or DeviceNet devices, but none of the devices are getting scanned.</p> |  | U4 |  |  | FINDING | [6 empty] | 95569
36147 | FINDING | Hyper link for Limit tab of Analog Point not available in On-line help | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-20 04:27 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-20 04:27 | 3.6.0_U8 |  |  | 2016-05-20 04:27 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-11 00:42 |  | Hyper link for Limit tab of Analog Point not available in On-line help. Not possible to browse limit tab through Analog point help.<div>(Please refer to attached screenshot for further reference)</div><div><br></div><div>PSH (Apr 15, 2016): Assigning it to Megha as she is&nbsp;assigned with&nbsp;the Ovation Developer Studio manual.</div> | Updated the documentation to include information on the Limit tab for Analog points. |  |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015):</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span> | 0 |  |  |  | Finding is confirmed to be fixed in 3.6.0_U8 | 0 |  |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015):&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0 |  | 3.6.0 + U4;<div>DBS , EWS</div> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | LC 04/22/2016: I checked in Author-it and the Limits tab now has a link. This will be available in the 3.6.0_U7 build of the OvPtStudio.chm.<div><br></div> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Browse an Analog Point.</li><li>Go to help.</li><li>Check the limit tab.</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 97311
36148 | FINDING | Unable to fetch a point in different unit of same network without entering the unit name in Point Name field of Point Information Application | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-17 03:20 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-17 03:20 | 67513 |  |  | 2016-05-17 03:20 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-11 00:42 |  | Unable to fetch a point in different unit of same network without entering the unit name in Point Name field of Point Information Application.<div>According to the help <span style="font-style:italic;">&quot;If the point is not found on the unit, the other units on the network are searched for the point name&quot;.</span></div><div>(Please refer to the attached screenshot of help for reference)</div> |  |  |  |  | 0 |  |  |  | Finding has closed and confirmed to be fixed in 3.6.0_U7 | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0_U7 |  | 3.6.0 + U4 |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Enter a point name of a point in different unit of the same network, without unit name.</li><li>A pop up appears saying&nbsp;<span style="font-style:italic;">&quot;An error&nbsp;occurred&nbsp;loading specified point&quot;.</span></li><li>Enter the point name with unit name and the point is browsed successfully.</li></ol> |  | U4 |  |  | FINDING | [6 empty] | 97028
36149 | FINDING | Ovation Control Builder application shows garbage value in its Version information window | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-11 07:45 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-11 07:45 |  |  |  | 2016-04-11 07:45 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-11 02:02 |  | It has been observed that Ovation Control Builder application version information window shows Control Builder Release as 3.6.0.66666 instead of 3.6.0. However other Ovation applications shows version as 3.6.0. Please refer the attached snapshot. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab, Net26</p><p>EWS Drop195</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | It is the change set number | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Opened Ovation control builder application from Ovation Configuration Studio.</p><p>2. Clicked <strong>About</strong> option from <strong>Help&nbsp;</strong>tab of the application.</p> |  | U4 |  |  | FINDING | [6 empty] | 94720
36150 | FINDING | TR "3.6.0_SRF2137_SVTP_rev1.1" needs some modification | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-11 04:30 | [11 empty] | USPITTFSService | 2016-04-11 04:30 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-11 04:30 |  | <p>It is discussed with Greg via e-mail (3/29)&nbsp;that in case of OCR1100 System Memory is listed but greyed out.</p><p>Hence&nbsp;test case 5.3.1 (b) (<span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">Verify this item is not listed -Configuration/Controller/System Memory (Normal, Expanded)) </span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">of TR&nbsp;</span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">&quot;3.6.0_SRF2137_SVTP_rev1.1&quot;&nbsp;should be updated&nbsp; accordingly</span><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">&nbsp;&nbsp;</span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U4 |  |  | FINDING | [6 empty] | 94709
36151 | FINDING | Ovation Signal Diagram application window's size is observed as fixed. | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:12 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:12 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-11 04:40 |  | <p>It has been observed that below mentioned different type of Ovation Signal Diagram application window's size can not be extended beyond a certain limit (whether Horizontal or Vertical) for any algorithm.</p><p><br></p><p>1. Properties Summary </p><p>2. Event Log</p><p>3. Algorithm Summary</p><p>4. Function Summary</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab,</p><p>EWS195, Net26, OCR400</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>This was in 3.5.0 and following.</p> | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open a signal diagram application containing different algorithms.</p><p>2. select an algorithm for example MASTATION.</p><p>3. If Algorithm control window is located at right side of the signal diagram application, then to&nbsp;access all the control options of this algorithm,&nbsp;user&nbsp;may require&nbsp;to extend the size of this window.</p><p>4. Size of algorithm control window appears as fixed and can not be extended beyond a certain limit.</p><p>5. This behaviour is applicable for all the algorithms.(Function Summary, Algorithm Summary, Event Log, Properties Summary )</p><p>6. Please refer the attached snapshot.</p> |  | U4 |  |  | FINDING | [6 empty] | 95740
36154 | FINDING | In Ovation Online help up and down arrows and See Also option not available for navigation | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:35 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:35 | 3.6.0_U8 |  |  | 2016-05-20 03:35 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-12 04:04 |  | <p>It has been observed that Up and Down arrows for navigating to next or previous pages is not available in Ovation Online help. Also, <strong>See Also</strong> option is not available on all the pages of online help for navigation to different pages of the help as&nbsp;available in previous releases of Ovation.</p><p>This issue has been observed in all the available online helps. Please refer the attached snapshots.</p> | Updated templates so that online help has navigation buttons. |  |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015): This has been fixed.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span> | 0 |  |  |  | <p>ST (05/20/2016): Checked and found <strong>Audit Viewer help</strong> and <strong>Ovation Developer Studio help( OvPtStudio360</strong>) has been updated too in Ov3.6.0_U8 build. So closing this finding.</p> | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>GEC Lab,</p><p>EWS Drop 195</p> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>LC 04/12/2016:&nbsp; Templates were changed in Author-it so that now navigation buttons should work in the U6 build.</p><p>LC 04/13/2016: Assigning this to Megha Gola so she will review the Developer Studio and Audit Viewer help.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): This has been fixed.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open online help of any ovation application.</p><p>2. Navigate randomly to any page&nbsp;from left pane of the help.</p><p>3. Check that up and down arrows are not available on top of that page. (This arrow is available only on the topmost page of online help)</p><p>4. Check that See Also option not available on bottom of that page.</p> |  | U4 |  |  | FINDING | [6 empty] | 97306
36156 | FINDING | Point review not showing filtering of point groups by record types while Enable live data is disabled. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-05-17 07:35 | [11 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-05-17 07:35 | 67513 |  |  | 2016-05-17 07:35 |  |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-04-12 07:56 |  | In point review window, while reviewing point groups , it has been observed that if &quot;Enable Live Data&quot; option is disabled we can not filter points in point groups by &quot;Record Types&quot;. However we can filter the points in the group by their frequencies (S,F,A).<br>Please note that the problem does not exist when we&nbsp;enable &quot;Enable Li*ve Data&quot; option. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | OV 3.6.0_U4 , DBS Drop 220 , WS12_R2 ,Operator/Point review window |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  | PJ 05/17: Checked in U7 build and found the problem resolved. Closed. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a point group in developer studio and assign points of all types (LA,DA, LD, DD, LP, DP) and all frequencies (S,F,A) as point group members. Download the point group.<br>2.Open Point Review window.<br>3. Click on Filter tab and&nbsp; select Point Source as &quot;Configured Point Groups&quot;.<br>4. Select &quot;Point Groups&quot; as defined in step-1.<br>5. Make sure that &quot;Enable live Data&quot; option is disabled. <br>6. Click on &quot;Start Point Review&quot; button to start review .<br>Observation:&nbsp; All Points defined in the group will be populated. This is ok. <br>7. Now filter next by Record Types for example filter only by LA and click on &quot;Start Point Review&quot; .<br>Observation : Still all points populate irrespective of filtering by LA.<br>8. Filter by any one Frequencies (S,F,A) for example filter by SLOW (S) and start point review .<br>Observation: Points are filtering correctly as per frequencies defined. <br>9. Now activate &quot;Enable live Data&quot; option and repeat step-7 &amp; 8.<br>Observation : For step 7: Points are filtering correctly as per Record Types defined.&nbsp; <br>For Step-8: Same behavior.<br>So the problem is with Step-7.</p><p><br></p> |  | U4 |  |  | FINDING | [6 empty] | 97059
36159 | FINDING | Controller Enters Fail Mode upon SSH Login | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-25 03:30 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-25 03:30 | 67271 |  |  | 2016-05-25 03:30 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-04-12 12:26 |  | OCR1100 Controller Enters Fail Mode when logging in Via SSH -<div><br></div><div><div>A workaround exists enter the following in the startup.scr for the controller:</div><div>&nbsp; &nbsp;((short*)&amp;ipcom_priority_map)[2]=150<br></div></div> |  |  |  | <p>Log into a &quot;heavily loaded controller&quot; - i.e. drop32/82 or drop4/54 and verify controller doesn't enter fail mode.</p><p>Logged into via SHC login , controller behavior is ok </p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Brown, Sean EMR SYSS PWS PITT | Durbin, Michael EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | Zochowski, Piotr EMR SYSS RS WRSW | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA |  |  | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Validation |  | Lower the priority of ipssh_server from 50 to 150.<div><br></div><div>A workaround exists enter the following in the startup.scr for the controller:&nbsp;</div><div>&nbsp; &nbsp;((short*)&amp;ipcom_priority_map)[2]=150</div><div><br></div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | The controller may need to be somewhat loaded (control sheets and\or IO points) to demonstrate the failure. |  | U6 |  |  | FINDING | [6 empty] | 97674
36165 | FINDING | On line help for DOC position of HPAI in GBNT needs to be replaced | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-12 00:58 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-12 00:58 |  |  |  | 2016-05-12 00:58 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-13 00:56 |  | The current DOC help for HPAI in GBNT is not giving the right idea of DOC positioning and hence needs to be replaced (For reference the selected portion in the attachment needs to be replaced):<div>Current:</div><div><div><i><br></i></div><div><i>The position of the DOC arrow is always defined as follows:</i></div><div><ul><li><i>DOC arrow is left of the CVI shape for an Up analog indicator bar.</i><br></li><li><i>DOC arrow is right of the CVI shape for a Down analog indicator bar.</i><br></li><li><i>DOC arrow is above the CVI shape for a Left analog indicator bar.&nbsp;</i><br></li><li><i>DOC arrow is below the CVI shape for a Right analog indicator bar.</i></li></ul><div>Needs to b e replaced with:<br></div></div></div><div><i style="line-height:1.5em;"><br></i></div><div><i style="line-height:1.5em;">The DOC arrow position is relative to the CVI shape position. The CVI shape itself can be positioned either above or below the indicator bar for a left/right indicator bar direction, and that the CVI shape can be positioned either left or right of the indicator bar for an up/down indicator bar direction. The DOC arrow will always follow the CVI shape position. &nbsp;For an up or down indicator bar, the DOC arrow can be positioned either left or right of the CVI shape at a user-defined offset from the CVI shape, and the DOC arrow will be centered vertically with the CVI shape center; for a left or right indicator bar, the DOC arrow can be positioned either above or below the CVI shape at a user-defined offset from the CVI shape, and the DOC arrow will be centered&nbsp;horizontally with the CVI shape center.&nbsp;</i><br></div> | <p>Updated the information on positioning DOC arrows.</p> |  |  | Check the topic, <em>To configure a Direction of Change arrow</em> | 0 |  |  |  | Finding is fixed in 3.6.0_U7. Please find the attached screenshot of on-line help after the fix (<span style="font-style:italic;">DOC_Arrow_Fix.png</span>). | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Agarwal, Gaurav EMR SYSS PWS NOIDA | Garg, Amit AUTOSOL PWS NOIDA | [5 empty] | Implementation | 3.6.0_U7 |  | 3.6.0+ U4 + APC 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | LC 04/25/2016: Updated the topic, <em>To configure a Direction of Change arrow</em> to correct the information on how DOC arrows are positioned. The change will be in the online help in the U7 build. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Go to GBNT</li><li>Select a HPAI and go DOC tab.</li><li>Select Help in DOC tab. and check.</li></ol> |  | u4 |  |  | FINDING | [6 empty] | 96672
36166 | FINDING | Deluxe points and assign algorithm help details needs to update as per the SRF2137 | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 01:00 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 01:00 |  |  |  | 2016-05-17 01:00 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-13 01:35 |  | <p>As per the SRF2137.The time that a point’s value has been read from I/O shall be recorded in the U8 and U9 fields of deluxe points.&nbsp; The controller software will store the time when the I/O cycle begins. This time will be copied into every point for every I/O cycle.</p><p>The ASSIGN algorithm shall be updated to transfer U8 &amp; U9 timestamps from the input point to the output point.&nbsp; In this way it will be possible to determine the time at which the control logic had the value from I/O available for computation inside the control task.<br></p> | Updated the ASSIGN algorithm to clarify 3.6 enhancements for timestamping for deluxe points. |  |  | Check the ASSIGN algorithm topic. | 0 |  |  |  | LB 05/17/16-Verified on Ovation3.6.0_U7 and observed that ASSIGN algo help is updated as per the SRF2137.Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Documentation | <p>AA (04-13-2016): Assigning this Finding to Linda. The ASSIGN algorithm is&nbsp;the &nbsp;apart of the Ovation Standard Algorithms Reference Manual that is being done by Linda.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | <p>Ovation 3.6.0_U4</p><p><br></p><p>AA (04-13-2016): Assigning this Finding to Linda. The ASSIGN algorithm is&nbsp; the apart of the Ovation Standard Algorithms Reference Manual that is being done by Linda.</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>AA (04-13-2016): Assigning this Finding to Linda. The ASSIGN algorithm is&nbsp; the apart of the Ovation Standard Algorithms Reference Manual (OW360_R1100)&nbsp;that is being done by Linda.</p><p><br></p><p>LC 04/25/2016: Updated the ASSIGN algorithm to explain enhancements in timestamping for deluxe points.&nbsp; This fix will be available in the U7 build.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the control builder help file and verify the Assign algo. and deluxe point help details.<br> |  | U4 |  |  | FINDING | [6 empty] | 97020
36167 | FINDING | F2 key in the Signal diagram does not works. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-05-25 06:01 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-05-25 06:01 | 3.6.0_U8/68081 |  |  | 2016-05-25 06:01 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-04-13 05:34 |  | <p>F2-Key operation for toggling between viewing the display canvas as part of the signal diagram &amp; viewing it as the entire screen doen not work.</p><p>The same is mentioned under &quot;what is the signal diagram display canvas&quot; title in OW360_80 manual.</p> | <p><br></p><p>AA (04-27-2016): The issue has been resolved. I have removed the Note that stated that ''F2-Key operation for toggling between viewing the display canvas as part of the signal diagram &amp; viewing it as the entire screen does not work.''. Topic 17.6 in the Control Builder (OW360_80) user guide has been modified. The updated pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_80</strong>. This will be available in the U7 online help.</p><p>tn:05/25/16: confirmed the note has been removed from the online help. Thius passing the finding.</p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Documentation | <p><br></p><p>AA (04-27-2016): The issue has been resolved. I have removed the Note that stated that ''F2-Key operation for toggling between viewing the display canvas as part of the signal diagram &amp; viewing it as the entire screen does not work.''. Topic 17.6 in the Control Builder (OW360_80) user guide has been modified. The updated pdf is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_80</strong>. This will be available in the U7 online help.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [8 empty] | Implementation | 3.6.0_U9 |  | All Operator stations of Ov. 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>Functionality deemed not necessary in signal diagram re-write for 3.3.1.&nbsp; Remove comment from documentation.</p><p><br></p><p>AA (04-27-2016): The issue has been resolved. I have removed the Note that stated that ''F2-Key operation for toggling between viewing the display canvas as part of the signal diagram &amp; viewing it as the entire screen does not work.''. Topic 17.6 in the Control Builder (OW360_80) user guide has been modified. The updated pdf is kept at: <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_80</strong>. This will be available in the U7 online help.</p><p><br></p> | 12 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1&gt; Open the signal diagram. </p><p>2&gt; Press F2 key of the keyboard.</p><p>-Observations-No change in the display of the canvas.</p> |  | U5 |  |  | FINDING | [6 empty] | 97692
36169 | FINDING | TT record field help needs modification | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:00 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-16 04:00 | 3.6.0_U7 |  |  | 2016-05-16 04:00 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-13 06:50 |  | TT record field definition explains this is Third-Party I/O Tag having 80 Characters ASCII. On contrary the Developer studio allows entry of only 40 Characters for this in hardware tab. | SJ April 25, 2016: TT record field updated to 40 characters.&nbsp; |  |  | SJ April 25, 2016: TT record field updated to 40 characters.&nbsp;<span style="">Check OvationApplications online help in Ovation 3.6.0_U7 build. </span> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation | SJ April 25, 2016: TT record field updated to 40 characters.&nbsp;<span style="">Check OvationApplications online help in Ovation 3.6.0_U7 build. </span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.6.0 |  | OV360_U6;<br>Online help; |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>SJ April 25, 2016: Check Ovation 3.6.0_U7 build.</p> <p>&nbsp;</p> <p>PS 15May16: Verified the issue in U7build and found fixed. Hence Finding is Closed.</p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1&gt; Go to Dev. Studio -&gt; Create a point with third party IO type hardware specifications. (TT field.jpg)&nbsp;&nbsp;</p> <p>2&gt;&nbsp;The Point Name under the MHI is reflected in TT field. But the entry is limited to 40 Characters.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p> <p>3&gt;&nbsp;Open PI with a point having hardware specifications -&gt; Go to hardware tab -&gt;TT field<br>4&gt; Click on TT field -&gt;online Help opens which explains TT field can have 80 Characters. </p> <p>This needs to be modified.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> |  | U6 |  |  | FINDING | [6 empty] | 96874
36170 | FINDING | FACEPLATE algorithm online help link is incorrect | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 13:55 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 13:55 |  |  |  | 2016-04-22 13:55 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-13 06:58 |  | FACEPLATE algorithm online help link&nbsp; opens MEDIANSEL information from both Control Builder as well as Signal Diagram. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | OV360_U6;<br>Online help; |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>LC 04/22/2016: Closed this finding because it is a software issue (Qt) and not a documentation issue.&nbsp; New finding that addresses the software issue is Finding 36262.</p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1&gt; Open Control Builder diagram with FACEPLATE algorithm -&gt; Select FACEPLATE algorithm&nbsp;-&gt;&nbsp;Right Click -&gt; HELP : </p> <p>This opens&nbsp; MEDIANSEL algoritm help details.</p> <p>2&gt;&nbsp; Open Signal diagram with FACEPLATE algorithm -&gt; Select FACEPLATE algorithm&nbsp;-&gt;&nbsp;Right Click -&gt; FACEPLATE HELP :</p> <p>This also opens&nbsp; MEDIANSEL algoritm help details.&nbsp; .&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> |  | U6 |  |  | FINDING | [6 empty] | 95492
36171 | FINDING | Engineering & Resonability limit behaviour with Soft and hard points are different. | Cooper, David External Self Employed | Documentation to be Updated | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Cooper, David External Self Employed | 2019-03-20 08:22 | [11 empty] | Cooper, David External Self Employed | 2019-03-20 08:22 | [7 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-04-13 07:10 |  | Following are the difference in behavior of Engineering &amp; Reasonability limit.<br>&nbsp; 1. Engineering limit is working for Hard point but for soft point it is not working.<br>2. Reasonability limit is working for both soft and hard point.<br>Please note that document does not state about dependency on hard/soft point and there are no differentiation in the OPP code based on hard or soft points in regards to limit checking |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV 3.6.0, Developer studio, Point info |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | System Deviation Report to be created | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Create a hardware point , configure Engineering limit&nbsp;&amp;&nbsp;load controller.<br>2. Verify the Engineering limit functionality .<br>Observation: Working fine.<br>3. Repeat step 1 &amp; 2 for soft point.<br>Observation: Engineering limit not working.<br>4. Repeat step 1 &amp;2 for Resonability point and for both point types (hard &amp; soft)<br>Observation: Resonability limit working fine for soft as well as hard point. |  | U4 |  |  | FINDING | [6 empty] | 139765
36172 | FINDING | GBNT: GB Quick View Help is not available. | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2016-04-21 10:09 | [11 empty] | McMaster, James External Artech | 2016-04-21 10:09 |  |  |  | 2016-04-21 10:09 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-04-13 23:45 |  | In Graphics Builder, help button is disabled for GB Quick View Option. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov 3.6.0_U4 |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Investigate After Release | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1&gt; Open or Insert New Graphics in Graphics Builder.</p><p>2&gt; Click to open GB Quick View option.</p><p>3&gt; Help button is disabled for this option.</p> |  | U4 |  |  | FINDING | [6 empty] | 95368
36173 | FINDING | Ovation Error Log application: File->Print operation help button is not functional | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | McMaster, James External Artech | 2016-04-19 14:24 | [11 empty] | McMaster, James External Artech | 2016-04-19 14:24 |  |  |  | 2016-04-19 14:24 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-14 00:23 |  | <p>It has been observed that in Ovation Error Log application online help is not opening from File-&gt; Print operation window and File-&gt;Print Setup window.</p><p>Please refer the attached snapshot.</p><p>Remote login details to the drop is attached.</p><p><font face="Times New Roman" size=3> <br></font></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Error Log/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab,</p><p>EWS Drop 195</p> |  | Ovation for Windows | Ovation | Operator Station/Error Log | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open Ovation Error Log application.</p><p>2. Open Print operation window from File-&gt;Print operation, check that available help button is non functional.</p><p>3. Open Page Setup window from File-&gt;Print Setup operation, check that available help button is non functional.</p> |  | U6 |  |  | FINDING | [6 empty] | 95234
36174 | FINDING | Online help to support SRF2227 needs to be updated | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-18 01:05 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-18 01:05 | 3.6.0_U7 |  |  | 2016-05-18 01:05 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-14 00:39 |  | <p>Ovation Online help to support functionality of SRF2227 needs to be updated. Please&nbsp;refer the attached snapshot and SRF document.</p> | SJ April 25, 2016: BIT3 in the 2W field for digital points updated with the text,&nbsp;<b style=""><i style="">Point value From <a name=_GoBack>I/O Scan</a></i></b><span style="">. </span> |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face="Times New Roman">SJ April 25, 2016: BIT3 in the 2W field for digital points updated with the text,&nbsp;<b style=""><i style="">Point value From <a name=_GoBack>I/O Scan</a></i></b><span style="">. Check OvationApplications online help in Ovation 3.6.0_U7 build. </span></font></font></p><font face="Times New Roman" size=3> </font> | 0 |  |  |  | <p>ST May18, 2016: BIT3 in the 2W field for digital points has been&nbsp;updated with the text, <strong><em>Point value From </em></strong><a name=_GoBack><strong><em>I/O Scan</em></strong></a>&nbsp;in Ovation Applications Online help of Ov3.6.0_U7&nbsp; build. So closing this finding.</p> | 0 |  | Ovation for Windows/General/Documentation | SJ April 25, 2016: BIT3 in the 2W field for digital points updated with the text,&nbsp;<b style=""><i style="">Point value From <a name=_GoBack>I/O Scan</a></i></b><span style="">. Check OvationApplications online help in Ovation 3.6.0_U7 build. </span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>GEC Lab,</p><p>Drop195</p> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>SJ April 25, 2016: Check Ovation 3.6.0 U7 build.</p><p><br></p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Go to Point information application for digital input points.</p><p>2. Open help for 2W:3 field.</p><p>3. No information available to support SRF2227.</p> |  | U6 |  |  | FINDING | [6 empty] | 97133
36175 | FINDING | Control Diagnostic application: What's This? option is not working for Process Information tab | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:44 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:44 | 67455 |  |  | 2016-05-20 03:44 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-14 01:02 |  | <p>It has been observed that in Ovation Control Diagnostic application <strong>What's This?</strong> option is working for&nbsp;all the available fields except fields in <strong>Process Information</strong> tab. </p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  | ST(05/20/2016): Checked in Ovation 3.6.0_U8 build, <strong>What's This?</strong> option is now working for&nbsp;<strong>Process Information</strong> also. So closing this finding. | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | <p>GEC lab,</p><p>EWS Drop195</p> |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | &quot;What's This&quot; help info added to the Process Information tab. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open Control Diagnostic application.</p><p>2. Select any controller from the list of available controller.</p><p>3. Open Process Information tab for this controller.</p><p>4. Click <strong>What's This?</strong> option from top of the control diagnostic application and click&nbsp;on&nbsp;any field&nbsp;under Process Information tab.</p><p>5. No information displays.</p> |  | U6 |  |  | FINDING | [6 empty] | 97307
36176 | FINDING | Sensor Calibration application: No option available to open online help from the application | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2016-04-18 08:50 | [11 empty] | McMaster, James External Artech | 2016-04-18 08:50 |  |  |  | 2016-04-18 08:50 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-14 01:46 |  | <p>It has been observed there is no option available to open online help for Sensor Calibration application from the application itself.</p><p>However online help for this application is available when we browse in <strong>Ovation Applications</strong> help under Ovation Utilities option.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab,</p><p>EWS Drop195</p> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open Sensor Calibration application from Start-&gt;All programs-&gt;Ovation Utilities.</p><p>2. Sensor calibration application opens.</p><p>3. Check that no option available in the application to open its online help.</p> |  | U6 |  |  | FINDING | [6 empty] | 95144
36177 | FINDING | SIS Diagnostics tool is not working | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-23 03:21 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-23 03:21 | 67266 |  |  | 2016-05-23 03:21 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-14 03:07 |  | <span style="line-height:18px;">In Ovation 3.6.0 U6, SIS Diagnostics tool is not working.&nbsp;</span><font face="Calibri, sans-serif"><span style="font-size:14.6667px;line-height:22px;">An error Message comes up &quot;Problem contacting diagnostic service&quot; after opening SIS&nbsp;Diagnostics tool.&nbsp;</span></font><div><span style="line-height:18px;">(Please refer to the attached screenshot)</span></div> |  |  |  |  | 0 |  |  |  | Issue has been verified in 3.6.0_U9 and found Fixed. | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | There was a problem with too large incoming message. The default limit has been increased. And from now on it can be dynamically increased on a system by adding/modifying a config file for Diagnostic tool. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  |  | Implementation | U9 |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | <p><br></p> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol style="direction:ltr;"><li><p style="margin-top:0in;margin-bottom:0pt;">Click on Windows START icon than go to All Programs\Ovation\Ovation Utilities.</p></li><li style="font-family:Calibri, sans-serif;font-size:11pt;"><p style="margin-top:0in;margin-bottom:0pt;font-size:11pt;">Click on SIS Diagnostics</p></li><li style="font-family:Calibri, sans-serif;font-size:11pt;"><p style="margin-top:0in;margin-bottom:0pt;font-size:11pt;">An error Message comes up &quot;Problem contacting diagnostic service&quot;</p></li></ol> |  | U6 |  |  | FINDING | [6 empty] | 97448
36178 | FINDING | Vxsim License requires an environment variable with it’s value, this infromation needs to be updated in the document | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-25 04:20 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-25 04:20 | 3.6.0_U9 |  |  | 2016-05-25 04:20 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-04-14 03:30 |  | <p>After upgrade of VCH machine to Ovation 3.6.0 U6 it has been observed that Vxsim is not able to find license file, hence unable to boot-up properly. Please refer the attached screenshot.</p><p>If the license file is removed, VxSim does not ask for license when Vcoordiantor service is restarted. please note that Vcoordinator and Vxsim services are running.</p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><strong>RS 04/16/2016:</strong> </span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">The license philosophy for Vxsim has been changed. Accordingly&nbsp;Vxsim License requires an environment variable with it’s value being the license file location, for example C:\Ovation\OvationVirtual\WRSlicense_360_D148.lic. Therefor after performing these steps the problem is resolved. Hence this finding is assigned to documentation where this&nbsp;information needs to be&nbsp;incorporated.</span><br></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><font face="Times New Roman" size=3> <br></font></p> | AA (04-25-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). Topic 3.2.2 has been added. The updated manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | <p>AA (04-25-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). Topic 3.2.2 has been added. The updated manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Lal, Ramesh External | Goyal, Ashish EMR SYSS PWS NOIDA | [5 empty] | Implementation | 3.6.0_U9 |  | VCH drop148 and Drop171&nbsp;(win7 64 bit) on net#26, Drop111 (win2008R2) on Net#36 with Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p><br></p><p>AA (04-25-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). Topic 3.2.2 has been added. The updated manual is kept at: <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_57.pdf.</strong></p><p><strong><br></strong></p><p><br></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><strong>RS 05/25/2016:</strong></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"> Verified the section &quot;3.2.2 To create an environment variable for the Vxsim license&quot; and its giving information to create a new Environment variable. Hence finding is closed.</span></p><font size=3><p><br></p><p><br></p><b><font size=3><p><br></p></font><p><br></p></b><p><br></p></font><p><br></p></span><p><br></p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Upgraded Ovation VCH Drop from Ovation 3.6.0 U4 to U6.</p><p>2. Performed manual steps to enable DDB protocol&nbsp;on Network Bridge. (received steps form Pittsburg)</p><p>3. Rebooted the VCH Drop.</p><p><br></p><p>&nbsp;Observation:</p><p>1.&nbsp;Did not get a&nbsp;popup for Vxsim licenses request after VCH Boot up.</p><p>2.&nbsp;Navigate &quot;C:\Ovation\OvationVirtual&quot; folder and&nbsp;double clicked&nbsp;Vxsim.exe. An error message appeared in Vxsim Consol as &quot;cannot find&nbsp;license file&quot;. </p><p><br></p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 97676
36180 | FINDING | Programmable touch keys on the Dell Extended keyboard is not functioning | Augustine, Lisa EMR SYSS PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Augustine, Lisa EMR SYSS PWS PITT | 2016-05-25 08:21 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-05-25 08:21 | [7 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-04-14 05:16 |  | <p>Alarm commands from the programmable touch keys on the &quot;Dell Extended keyboard&nbsp; is not functioning</p><p><br></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  | <p>When the script is run by hand the Ovation Software does the correct thing.&nbsp; It seems like the touch keys are the issue.&nbsp; Possibly they&nbsp;are not properly configured to initiate the scripts correctly or there is some other problem.&nbsp; Can you configure the touch keys to&nbsp;run any scripts successfully?&nbsp; Please respond in the History and not the Resolution Field.</p> | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OV 3.6.0 U6</p><p>Drop155</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Need More Information to Duplicate | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>&quot;Alaressm list.jps&quot;. is typed mistakenly .I also had&nbsp;ran the &nbsp;4 scripts&nbsp; &quot;AckPageAlarm.js&quot;, &quot;AckPageSilenceAudioAlarm.js&quot;, &quot;OpenAlarmList.js&quot;, and &quot;SilenceAudioAlarm.js&quot;&nbsp; in C:\ovation\ovationbase.However here I couldn't open the list by pressing the relevant key buttons associated with Dell Enhanced keyboard..&nbsp;.</p><p><br></p><p>Yes it is working by hand</p> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Installed the driverof the Dell extended keyboard. Programmable&nbsp; keys are assigned with different alarm command like &quot;Alaressm list.jps&quot; .</p><p>Press the keys those are assigned with alarm cmds.</p><p>No list is opened.</p><p><br></p><p>Verified the touch keys and found it is working</p> |  | U6 |  |  | FINDING | [6 empty] | 97722
36182 | FINDING | Online help for SIS CHARM's algorithms is missing | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-11 05:48 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-11 05:48 |  |  |  | 2016-05-11 05:47 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-14 07:25 |  | Online help for SIS CHARM's algorithms is missing in U6 build. SIS CHARM's algorithms help is not available on searching also.<br>This help was available till U4 build. | Updated algorithm online help to display help for SIS algorithms. |  |  | Check algorithm online help to see if help appears for SIS algorithms. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>LC 04/15/2016: Updated algorithm online help so that is now contains SIS algorithms.&nbsp; Fix will be available in U7 build.</p> <p>&nbsp;</p> <p>ASG 05/11/2016: Issue found resolved in Ovation 3.6.0_U7 build, hence closing the finding.</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U6 |  |  | FINDING | [6 empty] | 96599
36183 | FINDING | Ovation Error Log messages are not appearing properly for CSLS | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-19 14:33 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-19 14:33 |  |  |  | 2016-04-19 14:33 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-14 08:19 |  | Ovation Error Log messages are not appearing properly for CSLS. Please find the following Observation:<div><br><div><span style="line-height:1.5em;text-indent:-0.25in;">1. Load, Assign and Un-assign initiation message on Ovation error log don’t give details of the CSLS being Loaded, Assigned and unassigned respectively. But the completion message have details of the CSLS.</span></div><div><span style="font-family:Calibri, sans-serif;font-size:11pt;">Please refer to the attached screenshots for your reference (CSLS_Load messages.png, CSLS_Assign messages.png, CSLS_Unassign messages.png) &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp;</span><br><span style="line-height:1.5em;text-indent:-0.25in;font-family:Calibri, sans-serif;font-size:11pt;">2. CSLS Clear operation message are not there in Ovation error log, instead when CSLS is cleared it gives message of Controller load:</span></div><div><i style="line-height:1.5em;font-family:Calibri, sans-serif;font-size:11pt;">&nbsp;CSLS Operation “LoadController” on “Drop30” initiated</i></div><div><i style="line-height:1.5em;font-family:Calibri, sans-serif;font-size:11pt;">CSLS Operation “LoadController” on “Drop30/Drop80” completed</i></div><div><i style="line-height:1.5em;font-family:Calibri, sans-serif;font-size:11pt;">CSLS Operation “LoadController” on “Drop30” initiated</i></div><div><i style="font-family:Calibri, sans-serif;font-size:11pt;"><span style="font-size:11.0pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;">CSLS Operation “LoadController” on “Drop30/Drop80” completed</span></i></div><div><span style="font-size:11pt;font-family:Calibri, sans-serif;">Please refer to attached screenshot(CSLS_Clear messages.png) &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp; &nbsp;</span></div><div style="text-indent:0px;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;font-size:11pt;">3.&nbsp;</span><span style="line-height:1.5em;text-indent:-0.25in;font-family:Calibri, sans-serif;font-size:11pt;">Controller load (performed after CSLS load) initiation message mentions only one controller (the controller drop being loaded), but Controller load completion mentions both the controller. This should be consistent and both should mention only one Controller (the controller drop being loaded)</span></div><div style="text-indent:0px;"><span style="font-size:11pt;font-family:Calibri, sans-serif;">Please refer to attached screenshot(CSLS_Controller Load messages.png)</span></div><div><span style="font-size:11.0pt;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><br></span></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Error Log/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  |  | Implementation |  |  | 3.6.0 &nbsp;+ U6 |  | Ovation for Windows | Ovation | Operator Station/Error Log | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | When a CSLS is cleared the controller in control is notified.&nbsp; When abnormal conditions are encountered, these message help diagnose the system's operational status.&nbsp; | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Perform Assign, Load (With Controller Load), Clear and un-assign operations on a CSLS.</li><li>Check the Ovation error log messages for the respective operation.&nbsp;</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 95235
36184 | FINDING | Consistency checks for the SRF2137 Suppress Drop Alarm enhancements are not implemented in 3.6.0 | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-05-27 07:32 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-05-27 07:32 |  |  |  | 2016-05-27 07:32 |  |  |  | Capani, Innocenzo AUTOSOL PWS PITT | 2016-04-14 10:25 |  | The SRF 2137 Functional Spec (rev 1.0) section 2.1.9 states:<font face="Times New Roman" size=3> <br></font><p style="margin:0in 0in 0pt;"><font size=3><font face="Times New Roman">When configuring a node in Ovation Developer’s studio, the user shall be given an option to suppress drop alarms if the node is in alarm.<span style="">&nbsp; </span></font></font></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3>Ovation Developer’s studio shall perform Consistency Checks on the Node Configuration:</font></p><ul style="list-style-type:disc;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;page-break-after:avoid;">ERROR – An Ovation Local Node or Remote Node is configured to suppress the drop alarm or node alarm.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;page-break-after:avoid;">WARNING – Any Non Ovation Local Node or Remote Node is configured to suppress the drop alarm or node alarm<br><br>The consistency checks are not implemented in 3.6.0 </p></li></ul><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  | IC 4/14/16&gt; per Rick K:&nbsp;&nbsp; <span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>SDR &amp; DIR the missing functionality.</font></span><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>It will be added to 3.6.0 in a future patch.</font></span><font face="Times New Roman" size=3> <br><br>IC 5/27/16&gt; closed finding, added note to DIR, track as SDR 36645 </font> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U6 |  |  | FINDING | [6 empty] | 97929
36189 | FINDING | Some of test cases of TR "3.6.0_CONTROLLER_SVTP_rev5.6" can not be tested in GEC due to unavailable of additional Gateway | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-15 05:54 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-15 05:54 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-15 03:52 |  | <p>&nbsp;In GEC only one 1420 Gateway is available so test cases 5.25.3,5.25.4 and 5.25.9 of TR &quot;3.6.0_CONTROLLER_SVTP_rev5.6&quot;</p><p>can not be tested in GEC as these test&nbsp; needs one additional Gateway.</p><p>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95029
36190 | FINDING | SDR 20780_Screen saver time out 60minute in group policy is reflecting as 53 minute in EWS screen server | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-04-26 15:12 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-04-15 04:27 |  | <p>SDR 20780_Screen saver time out 60minute in group policy is reflecting as 53 minute in EWS screen server .</p><p>Other time settings like 5 minute,10 minute, 30 minute are correctly in EWS</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OV 3.6.0 </p><p>Drop127 W7 64bit</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>In group policy in policies tab in scree saver time out select the time out as 60 minute ,</p><p>Then logged of the EWS and logged in and verified&nbsp; then it seen as 53 minute.</p><p>Attached the image of group policy setting(1-60m_Group policy.jpg) &nbsp;and EWs Screen saver settings(1-60m_53m.jpg)</p> |  | U6 |  |  | FINDING | [6 empty] | 112961
36198 | FINDING | Error on loading a virtual controller with MHM configured | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 10:56 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 10:56 | 67578 |  |  | 2016-05-16 10:56 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-15 13:23 |  | <p>A virtual controller configured with an MHM module can not be loaded without an error.&nbsp; Please see attachment for error. </p><p><br></p><p>MP 4/20/16 update:&nbsp; This was tracked down to the fact that the module was not 'Engineered', so the file MHM4810.XML did not exist on the DBS.&nbsp; Once the module was 'Engineered' and the file existed on the DBS, the load completed successfully.&nbsp;&nbsp;&nbsp; If this file is required, should there be a default file? or should the error message be more descriptive of the problem?</p> |  |  |  | <p>The affected area is in the software which copies the downloaded MHM XML file to the &quot;distribution directory&quot; on the Database Server.&nbsp; This copy operation will be modified slightly to treat the existence of the source file as optional.&nbsp; </p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Boehmer, Robert W AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0_U7 |  | Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The error shown occurs during the process of copying the implicitly downloaded MHM XML file (if any) to the directory on the Database Server used by the Ovation Online Synchronizer.&nbsp; The software will be changed to treat this copy operation as optional (if the source file does not exist). | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Configure a virtual controller with and MHM module.&nbsp; Perform a load of the virtual controller.&nbsp; Attached error will occur. |  | U6 |  |  | FINDING | [6 empty] | 96943
36201 | FINDING | Incorrect I/O device number is mentioned for Wireless hart device. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 03:39 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 03:39 | 3.6.0_U8 |  |  | 2016-05-23 03:39 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-16 06:02 |  | Incorrect I/O device number is mentioned for Wireless hart device on help file&nbsp;under &quot;to insert a new I/O device&quot; section. User is allowed to configure IO device number for wireless hart device from 5 to 11. |  |  |  | <p>MG (April 25, 2016): According to this Finding, updated the screenshot (<strong>Figure 13: Insert New I/O Device wizard</strong>) in the <strong>Section 5.1.1 To insert a new I/O device</strong> of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><b><font size=2><p><span style="color:rgb(34, 34, 34);font-size:12px;font-weight:normal;line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);font-size:12px;font-weight:normal;line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p></font></b> | 0 |  |  |  | <p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that&nbsp; IO device number for wireless hart device&nbsp;is shown as&nbsp;5. Hence this finding is closed by validation.</p> | 0 |  |  | <p>MG (April 25, 2016): According to this Finding, updated the screenshot (<strong>Figure 13: Insert New I/O Device wizard</strong>) in the <strong>Section 5.1.1 To insert a new I/O device</strong> of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | Ovation3.6.0_U6, OvptStudio360 help file |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | MG (April 25, 2016): The issue according to this has been fixed and will be available in U7 build.<div><span style="color:rgb(34, 34, 34);">MG (May 17, 2015): Available in&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Ovation 3.6.0 U8 build.</span><br></div> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the OvptStudio360 help file and verify the Wireless hart IO device number details.</p><p>Screenshot is also attached for your reference.</p> |  | U6 |  |  | FINDING | [6 empty] | 97457
36202 | FINDING | Wireless hart gateway and device configuration details are missing on help file | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 04:01 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 04:01 | 3.6.0_U8 |  |  | 2016-05-23 03:59 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-16 06:06 |  | Wireless hart gateway and device configuration details are missing on help file under Wireless HART device configuration and Wireless HART gateway configuration section of OvptStudio360 help file&nbsp;. |  |  |  | <p>MG (April 25, 2016): According to this Finding,&nbsp;added the&nbsp;hyperlinks for the wireless HART gateway and device configuration details&nbsp;in the&nbsp;<strong>Section 3.2 Wireless HART gateway configuration and Section 3.3 Wireless HART device configuration&nbsp;</strong>of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 0 |  |  |  |  | 0 |  |  | <p>MG (April 25, 2016): According to this Finding,&nbsp;added the&nbsp;hyperlinks for the wireless HART gateway and device configuration details&nbsp;in the <strong>Section 3.2 Wireless HART gateway configuration and Section 3.3 Wireless HART device configuration&nbsp;</strong>of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | Ovation3.6.0_U6, OvptStudio360 help file |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 25, 2016): The issue according to this has been fixed and will be available in U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): Available in</span><span style="color:rgb(34, 34, 34);line-height:normal;box-sizing:border-box;">&nbsp;Ovation 3.6.0 U8 build.</span></p><span style="color:rgb(34, 34, 34);line-height:normal;box-sizing:border-box;"><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p><p><br></p></span><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the OvptStudio360 help file and verify the Wireless hart gateway and device configuration details.</p><p>Screenshot is also attached for your reference.</p> |  | U6 |  |  | FINDING | [6 empty] | 97459
36203 | FINDING | I/O device number description is missing for OCR1100 | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 04:05 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 04:05 | 3.6.0_U8 |  |  | 2016-05-23 04:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-17 01:17 |  | I/O device number description is missing for OCR1100 under attributes of the wireless hart I/O device&nbsp;object section. |  |  |  | <p>MG (April 25, 2016): According to this Finding, updated the screenshot description of the field I/O device number in the table Attributes of the Wireless HART I/O device object in the <strong>Section 5.1 Attributes of the wireless hart I/O drivers and&nbsp;devices&nbsp;</strong>of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that&nbsp;I/O device number description is&nbsp;added for OCR1100 .Hence this finding is closed by validation | 0 |  |  | <p>MG (April 25, 2016): According to this Finding, updated the screenshot description of the field I/O device number in the table Attributes of the Wireless HART I/O device object in the <strong>Section 5.1 Attributes of the wireless hart I/O drivers and&nbsp;devices&nbsp;</strong>of the Using Wireless Devices in Ovation manual. </p><p>The updated PDF is placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/CON_35.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\CON_35.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | Ovation 3.6.0_U6,OvptStudio360 help file. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 25, 2016): This finding has been fixed and&nbsp;will be&nbsp;available in U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): Available</span><span style="color:rgb(34, 34, 34);line-height:normal;box-sizing:border-box;">&nbsp;in the Ovation 3.6.0 U8 build.</span></p><p><span style="color:rgb(34, 34, 34);line-height:normal;box-sizing:border-box;"><font color="#000000">LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</font></span><br></p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the OvptStudio360 help file and verify the I/O device number description for OCR1100 under attributes of the wireless hart I/O device&nbsp;object section. Screenshot is also attached for your reference. |  | U6 |  |  | FINDING | [6 empty] | 97460
36205 | FINDING | Dump CRC file is not getting generated for SIS Legacy Logic Solver | Daly, Joshua D EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-25 04:33 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-25 04:33 | 68160 | [6 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-04-18 02:32 |  | Dump CRC file is not getting generated for SIS Legacy Logic Solver and&nbsp;shows an error as &quot;Data returned from the Dump CRC. Files not created&quot;. |  |  |  |  | 0 |  |  |  | <p><strong>RS 05-25-2016:</strong> Still issue exists in Ovation 3.6.0 U9. Unable to generate Dump CRC for Legacy SIS. Even if tried to generate at Ovation System Level here only CHARMS Dump CRC is getting generated.</p><p>For reference please find the attached snapshot &quot;Dump_CRC_Error_for_Legacy_SIS.png&quot; and generated&nbsp;&quot;dump CRC&nbsp; Ovation System.html&quot; file for Ovation System.</p> | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | Drop100 DBS with Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p><br></p> | 11 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face="Times New Roman" size=3> <br></font></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Right click on Logic Solver.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Select Dump CRC option &nbsp;from the List.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Select Yes in next POP up window.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Give the dump CRC file name and location to save the file.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">CRC window appears and select OK.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">File is not created and following&nbsp; error message appeared in Developer Studio &quot;Data returned from the Dump CRC. Files not created&quot;. Please find the attachment.</span></p></li></ol><p><font face="Times New Roman" size=3> <br></font></p><p><br></p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 97677
36207 | FINDING | Name character length for inserting a new Logic Solver in Developer Studio is limited to 13 characters | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-19 14:34 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-19 14:34 |  |  |  | 2016-04-19 14:34 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-04-18 06:17 |  | <p>In Ovation 3.6.0 U4, user is able to&nbsp;insert a new&nbsp;Logic Solver&nbsp;name&nbsp;having&nbsp;more than 13 characters in Developer Studio.&nbsp;e.g. Legacy LS name &nbsp;D27_SDS01_LS10&nbsp;and D30_CSLS000010. </p><p>After Upgrade of Ovation 3.6.0 U4 to U6, character length is limited to 13. e.g Legacy LS name &nbsp;D27_SDS01_LS1&nbsp;and D30_CSLS00001.</p><p><br></p><p>Note: Issue is observed in both Legacy and CHARMS Logic Solver.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA |  |  | Implementation |  |  | Drop100 DBS with Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p>The limitation is to account for control module prefix.</p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Verify the character length on Logic Solvers in legacy and CHARMS , <span style="">&nbsp;</span>which was earlier (In Ovation 3.6.0 U4) configured in Developer Studio. </span></span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">e.g. Legacy LS name &nbsp;D27_SDS01_LS10&nbsp;and D30_CSLS000010.</span></span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">After upgrade of Ovation 3.6.0 U6, insert a new Logic Solver and give the name to the Logic Solver in same format (having more than 13 character) as given in Ovation 3.6.0 U4.</span></span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">User can give only 13 characters name to Logic Solver.</span></span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">e.g. Legacy LS name &nbsp;D27_SDS01_LS1&nbsp;and D30_CSLS00001.</span></span></li></ol><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><p><font face="Times New Roman" size=3> <br></font></p> |  | U6 |  |  | FINDING | [6 empty] | 95236
36208 | FINDING | Test case 5.1.24 of 3.6.0_SRF1725_SVTP_rev1.2_XX SVTP cannot be performed. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 | [7 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-18 06:24 |  | <p>In the test case 5.1.24 of SVTP 3.6.0_SRF1725_SVTP_rev1.2_AG point (9) cannot be performed hence need to be marked as NA</p><p>Packed digital point cannot be viewed in system viewer so 50 character description of packed digital point cannot be checked in system viewer so point (9) of section 5.1.24 can be marked as NA.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation |  |  | 3.6.0_SRF1725_SVTP_rev1.2_AG |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <ul><li></li></ul> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 118595
36209 | FINDING | The error message should come if in SIS I/O LSDVC and LSDO configured in one CHARMS Logic Solver and are getting used in another Logic Solver Control Sheet. | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:15 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:15 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-04-18 07:45 |  | <p>The error message is not coming if User has configured SIS IO CHARMS LSDVC and LSDO in one Logic Solver and same LSDO and LSDVC are used in another Logic Solver&nbsp; Control Sheet.</p><p>In manual&nbsp;its mentioned&nbsp;as </p><p>LSDO - </p><font size=2><p>The LSDVC algorithm must be used in the same Logic Solver as the physical connection of the channel. please refer the attachment LSDO.png</p><p>LSDVC -</p><font size=2><p></p><p>The LSDVC algorithm must be used in the same Logic Solver as the physical connection of the channel. please refer the attachment LSDVC.png</p><p>NOTE: Same is observed in Legacy Logic Solver also.</p></font></font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA |  |  | Implementation |  |  | <ol><li>Configure a new LSDCV and LSDO in SIS I/O Charms&nbsp;of one Logic Solver. But&nbsp;don't use those configured LSDO and LSDVC&nbsp;in any Control Sheet of that Logic Solver. e. LSDO and LSDVC are configured in Logic Solver 15</li><li>Load the Logic Solver.</li><li>Insert a new Control sheet in any other Logic Solver (other than step 1 Logic Solver) having&nbsp;a&nbsp;logic with&nbsp;LSDO and LSDVC algo. e.g Control Sheet is created in Logic Solver 1 Control&nbsp;Module 1. Please refer the attached Control Sheet.</li><li>Click on LSDO algo and in Property editor go to Discrete IO output channel and select the LSDO configured in Step 1.</li><li>Click on LSDVC algo and in Property editor go to&nbsp;Hart 2-State IO output channel and select the LSDVC configured in Step 1.</li><li>Save&nbsp;the Control Sheet and it gets saved without any error.</li><li>Load the Logic Solver. Logic Solver loaded successfully without any error.</li><li>Load the Controller Drop. Controller Drop loaded successfully.</li><li>Open the Signal Diagram for the Control sheet created in Step 4.</li><li>User is able to change the value for LSOD and LSDVC.</li></ol><p><br></p><p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <em>SDR 18981</em> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95742
36210 | FINDING | SRU Reports both PDC & RDC as Primary Domain Controllers | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-20 15:44 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-20 15:44 |  |  |  | 2016-04-20 15:44 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 15:00 |  | <p>On Multi Ovation level system, where the Primary Domain (PDC) is Ov-3.6.0 DBS - Emily network</p> <p>and the Redundant Domain (RDC) is Ov-3.5.1 - David Network, The SRU reports both Drops</p> <p>as Primary Domain Controllers, when run on either side.&nbsp;</p> <p>&nbsp;</p> <p>Note: The history of the Emily &amp; David DCs is that because of OS Reloads constraints, </p> <p>the Primary Domain function was switched back and forth few times between the 2 drops, </p> <p>in order to maintain the DC Clients information during the upgrades.&nbsp;</p> <p>&nbsp;</p> <p>In the Registry of both DCs:</p> <p>&nbsp; &nbsp;HKEY_LOCAL_MACHINE\Software\Wow6432Node\Westinghose\Misc\Install</p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;DomainRole&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; PRIMARY_DOMAIN_CONTROLLER</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>msb - 4/20/2016</p> <p>A reload of Ov-3.5.1 on the RDC was performed</p> <p>In the Registry of David:</p> <p>&nbsp; &nbsp;HKEY_LOCAL_MACHINE\Software\Wow6432Node\Westinghose\Misc\Install</p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;DomainRole&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; BACKUP_DOMAIN_CONTROLLER</p> <p>&nbsp;</p> <p>The SRU reports correctly&nbsp; the Em drop as&nbsp; as PDC and David drop as RDC</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95331
36211 | FINDING | SRU upgrade from 1.4 to 1.5 does not install .NET 4.5.1 | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Staab, Randy AUTOSOL PWS PITT | 2016-04-21 09:22 | [11 empty] | Staab, Randy AUTOSOL PWS PITT | 2016-04-21 09:22 | 67388 |  |  | 2016-04-21 09:22 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 15:16 |  | <p>Upgrade of SRU on a Non-Ovation drop from 'OvSysReg&nbsp; 1.40.0000' to 'Ovation Sytem Registarion Utility 1.5.0.0000',</p> <p>wihout first removing SRU-1.4, does not install the '.NET Framework 4.5.1' on the Workstaion.</p> <p>While in a clean install of SRU-1.5 from the Ov-3.6.0_U6 DVD the&nbsp;.NET 4.5.1 is installed properly during the SRU installation.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software | 2016-04-21 RStaab: Determined to be user error. However, discovered related issue that the standalone SRU installer in v3.5.2 and early v3.6.0 contained an incorrect GUID. The mismatching GUID caused them to be treated as separate products. <span style="font-size:14.4px;">This has been corrected in 3.6.0_U7.</span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95365
36212 | FINDING | SysReg.log file returns non-descriptive name for Non-Ovation drop | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-14 14:42 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-14 14:42 | 67423, 67634 |  |  | 2016-05-14 14:42 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-04-18 16:10 |  | <p>SysReg.log file returns non-descriptive name for Non-Ovation drop:</p> <p>&nbsp;</p> <p>&nbsp;a. &nbsp;Info&nbsp;Requesting workstation information from 172.16.136.124 (Non-Ovation Drop)<br>&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;Info&nbsp;Successfully collected workstation information from Non-Ovation Drop (DROP-Non-Ovation)<br>&nbsp;b. &nbsp;Info&nbsp;Requesting workstation information from 172.16.154.230<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;Info&nbsp;Successfully collected workstation information from GENE</p> <p>&nbsp;</p> <p>In casa a. the name of the DROP is KAVMgr10, the htm report identidies the drop as&nbsp;&nbsp;&nbsp;&nbsp; Workstation: KAVMGR10</p> <p>the returned in the log file as 'DROP-Non-Ovation' is misleading</p> <p>&nbsp;</p> <p>In case b. it will be usefull if the returned info would list both IP &amp; Name.&nbsp;&nbsp; Ex.&nbsp; &nbsp;'172.16.154.230 - &nbsp;GENE'</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p><span style="FONT-SIZE:14px;">2016-04-21 RStaab: Status messages should now identify Ovation vs. Non-Ovation drops and include both host name and IP whenever possible.</span></p> <p><span style="FONT-SIZE:14px;">---</span></p> <p><span style="FONT-SIZE:14px;">msb 5/14/2016 -</span></p> <p><span style="FONT-SIZE:14px;">&nbsp; log - OK:</span></p> <p><span style="FONT-SIZE:14px;">&nbsp;&nbsp;a. &nbsp;KAVMGR10 (172.16.136.124)</span></p> <p><span style="FONT-SIZE:14px;">&nbsp;&nbsp;b.&nbsp; GENE (172.16.154.230)</span></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 96852
36216 | FINDING | Online help needs to be updated for SRF2137 feature "configuration to suppress Drop Alarm functionality". | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:53 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:53 | 3.6.0_U8 |  |  | 2016-05-20 03:53 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-19 00:28 |  | <p>Online help needs to be updated for SRF2137 feature &quot;configuration to suppress Drop Alarm functionality&quot;.</p><p>As we have support for this feature in Ovation 3.6.0, so online help for this needs to be updated. Please refer the attached snapshot.</p> |  |  |  | <p>MG (April 26, 2016): According to this finding,&nbsp;Added the&nbsp;field Disable&nbsp; drop alarm when node point alarm and Highly managed alarm,&nbsp;and its description in the table&nbsp;Alarm tab fields for module and node points&nbsp;in&nbsp;the&nbsp;<strong>Section&nbsp;8.7.7 Alarm tab field description</strong> of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 0 |  |  |  | ST(05/20/2016): <span style="color:rgb(34, 34, 34);line-height:normal;box-sizing:border-box;">Checked OvptStudio online help in the Ovation 3.6.0 U8 build. Online help is updated&nbsp;to support&nbsp;SRF2137 feature &quot;configuration to suppress Drop Alarm functionality&quot;. So closing this finding.</span> | 0 |  | Ovation for Windows/General/Documentation | <p>MG (April 26, 2016): According to this finding,&nbsp;Added the&nbsp;field Disable&nbsp; drop alarm when node point alarm and Highly managed alarm,&nbsp;and its description in the table&nbsp;Alarm tab fields for module and node points&nbsp;in&nbsp;the&nbsp;<strong>Section&nbsp;8.7.7 Alarm tab field description</strong> of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in&nbsp;U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>GEC Lab,</p><p>EWS Drop195</p> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | MG (April 28, 2016): This finding has been fixed and&nbsp;will be available in U7 build.<div><br></div> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open any node point from Developer Studio.</p><p>2. Go to Alarm Tab.</p><p>3. Check new field &quot;Disable Drop Alarm When Node Point Alarms&quot; is present.</p><p>4. Check that online help for this field is not updated.</p> |  | U6 |  |  | FINDING | [6 empty] | 97309
36217 | FINDING | SVTP "3.6.0_SRF2137_SVTP_rev1.1.doc" needs modification. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-19 00:49 | [11 empty] | USPITTFSService | 2016-04-19 00:49 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-19 00:49 |  | <p>Section 5.9 of SVTP &quot;3.6.0_SRF2137_SVTP_rev1.1.doc&quot; need changes as per the below details:</p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0cm 0cm 0pt;"><font face=Times><span lang=EN-US><font size=3>Test Case 5.9.1 should be modified as: </font></span></font></p><p style="margin:0cm 0cm 0pt;"><font face=Times><span lang=EN-US></span></font><font face="Times New Roman" size=3><font face=Times><strong>&quot; </strong><font size=3><strong>When configuring a node point&nbsp;in Studio, verify an option is given to suppress drop alarms if the node point is in alarm.&quot;</strong></font></font></font></p><font face=Times size=3><font face=Times><span lang=EN-US><font size=3><p style="margin:0cm 0cm 0pt;">Test Case 5.9.2 should be modified as: </p><p style="margin:0cm 0cm 0pt;"><strong>&quot;<span lang=EN-US style="color:black;font-family:&quot;Times&quot;,&quot;serif&quot;;font-size:12pt;">Verify Studio performs a Consistency check on the Node point Configuration and report the following ERROR when appropriate:</span></strong><span lang=EN-US><font face="Times New Roman" size=2><strong> <br style=""></strong></font></span><b style=""><span lang=EN-US style="color:black;">&nbsp; ERROR – An Ovation Local Node point or Remote Node point is configured to suppress the drop alarm.&quot;</span></b></p><font face="Times New Roman"><font face=Times><p style="margin:0cm 0cm 0pt;">Test Case 5.9.3 should be modified as: </p><p style="margin:0cm 0cm 0pt;"><strong>&quot;<span lang=EN-US style="color:black;font-family:&quot;Times&quot;,&quot;serif&quot;;font-size:12pt;">Verify Studio performs a Consistency check on the Node point Configuration and report the following WARNING when appropriate:</span></strong><span lang=EN-US><font face="Times New Roman" size=2><strong> <br style=""></strong></font></span><font face="Times New Roman"><span lang=EN-US style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;"><strong>&nbsp; WARNING – Any Non Ovation Local Node point or Remote Node point&nbsp;is configured to suppress the drop alarm.</strong>&quot;</span></font></p></font><p style="margin:0cm 0cm 0pt;">Test Case 5.9.5 should be modified as:</p><p style="margin:0cm 0cm 0pt;">&nbsp;<strong>&quot;<span lang=EN-US style="color:black;font-family:&quot;Times&quot;,&quot;serif&quot;;font-size:12pt;">Verify Drop alarms are suppressed correctly when the supress option is used.&quot;<span style="">&nbsp; </span></span></strong><br></p></font><p style="margin:0cm 0cm 0pt;"><br></p></font><p style="margin:0cm 0cm 0pt;"><br></p></span><p style="margin:0cm 0cm 0pt;"><br></p></font><p style="margin:0cm 0cm 0pt;"><br></p></font><p><strong><font face=Times size=3><br></font></strong></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please check the details in &quot;Description&quot; tab of this finding. |  | U6 |  |  | FINDING | [6 empty] | 95199
36218 | FINDING | SVTP "3.6.0_SRF2227_SVTP_rev1.1.doc" needs modification. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-19 01:54 | [11 empty] | USPITTFSService | 2016-04-19 01:54 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-19 01:54 |  | <p>SVTP &quot;3.6.0_SRF2227_SVTP_rev1.1.doc&quot; need changes as per the below details:</p><p>1. Test case 5.1.5.c, 5.1.5.d, 5.1.6.c, 5.1.6.d,&nbsp;5.1.7.c, 5.1.7.d, 5.1.9.c, 5.1.9.d, 5.1.10.c, 5.1.10.d, 5.1.11.c, 5.1.11.d needs to be removed as this SRF is not applicable for output points.</p><p>2. Test case 5.2.5.c, 5.2.5.d, 5.2.6.c, 5.2.6.d,&nbsp;5.2.7.c, 5.2.7.d, 5.2.9.c, 5.2.9.d, 5.2.10.c, 5.2.10.d, 5.2.11.c, 5.2.11.d needs to be removed as this SRF is not applicable for output points.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please refer the details mentioned in Description tab of this finding. |  | U6 |  |  | FINDING | [6 empty] | 95201
36219 | FINDING | SVTP 3.6.0_PROCESSINFO_SVTP_rev1.1.doc needs modification. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-19 03:20 | [11 empty] | USPITTFSService | 2016-04-19 03:20 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-19 03:19 |  | <p>SVTP 3.6.0_PROCESSINFO_SVTP_rev1.1.doc needs modification as per the below mentioned details:</p><p><strong>1. Test Case 5.3&nbsp;should be removed:</strong></p><p>As per the discussion with developer input quality will not be propagated to the output for PROCESSINFO algorithm.&nbsp;</p><p><strong>2.</strong>&nbsp;<strong>Test Case 5.6.5&nbsp;should be removed:</strong></p><p>Since holding registers are typically used for storing values in special functions and ladder applications and PROCESSINFO algorithm is not a special function algorithm.&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please refer the details mentioned in Description tab of this finding. |  | U6 |  |  | FINDING | [6 empty] | 95204
36224 | FINDING | Signal diagram "Find (Search document titles for)" is not working when searching a document in up direction | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 14:39 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 14:39 |  |  |  | 2016-04-26 14:39 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-20 03:10 |  | Signal diagram &quot;Find (Search document titles for)&quot; is not working when searching up direction. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation3.6.0_U6</p><p>OS-WS12,WIN7 64 BIT</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>Search does not have an Up/Down option and it does not wrap.</p> | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the signal diagram application.</p><p>2)Search a document&nbsp;on the document tree. e.g Unit2 / Task4 / Sheet 25</p><p>3)Now search a document&nbsp;listed up&nbsp;compare to document on step2. e.g. Unit0 / Task2 / Sheet 10</p><p><br></p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 95730
36225 | FINDING | Test case 5.8 of SVTP “3.6.0_FAILOVER_SVTP_rev3.6_VP.doc” needs to be modified. | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-20 03:49 | [11 empty] | USPITTFSService | 2016-04-20 03:49 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-20 03:49 |  | <p><font face="Times New Roman" size=3> </font><a name=_Toc67600001><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;font-weight:normal;">Test case 5.8 Controller-to-Controller Communication</span></a><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;font-weight:normal;">In Test setup section, step-5 needs to be modified.</span><font face="Times New Roman" size=3> </font></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;font-weight:normal;">In Test case 5.8,<span style="">&nbsp; </span>Step-5</span><font face=Helvetica><span style="font-size:11pt;font-weight:normal;"> says <span style="">&nbsp;</span>“Load the four redundant controllers </span><span style="color:black;font-size:11pt;font-weight:normal;">and download the monitor graphics.”</span></font><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-size:11pt;font-weight:normal;"><font face=Helvetica><br></font></span></p><p><span style="color:black;font-size:11pt;font-weight:normal;"><font face=Helvetica>Modification needed: Removal of download of monitor graphics from step-5 as this not valid for Ov3.6.0.</font></span></p><p><font face="Times New Roman" size=3> </font><font face=Helvetica><span style="color:black;font-size:11pt;font-weight:normal;"><br></span></font></p><p><font face=Helvetica><span style="color:black;font-size:11pt;font-weight:normal;">Note: In Ovation, there is no requirements of download of graphics on Ov 3.2.0 <span style="">&nbsp;</span>and onwards</span><span style="color:red;font-size:11pt;font-weight:normal;">.</span></font><font face="Times New Roman" size=3> </font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0 |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95280
36226 | FINDING | Controller points can be shelved successfully; but the “Suppressed Alarm Status” value in PI window remains blank also the 1W B27 remains 0. | Cooper, David External Self Employed | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Cooper, David External Self Employed | 2019-03-20 05:42 | [11 empty] | Cooper, David External Self Employed | 2019-03-20 05:42 | 67770 | [6 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-20 04:14 |  | <p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Controller points can be shelved successfully; but the “Suppressed Alarm Status” value in PI window remains blank also the 1W B27 remains 0.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">This is true for both Real &amp; Virtual Controllers; whereas EWS generated points show correct behaviour.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Notes :</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">1: The above behaviour also&nbsp;observed for Alarm Check OFF, Limit Check OFF &amp; Alarm Cutout.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">2:&nbsp;The above behaviour is&nbsp;observed for OPP Slow &amp; OPP fast point types.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">3:&nbsp; Above issue is observed&nbsp;for&nbsp;LA/DA/LP/DP whereas digital points both LD/DD work as desired.&nbsp;</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">PP:04/26/2016-Ov3.6.0_U6-If a point (which is in alarm) is shelved then the point&nbsp;goes out of alarm&nbsp;&amp; when the same point is unshelved it does not come back into alarm.</span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">PP:05/13/2016-The above issues are verified in Ov3.6.0_U7 but the problems still persists.</font></span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI"></font><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">PP:05/24/2016-The above issues are again verified in Ov3.6.0_U9 but the problems still persists.</font></span><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Cooper, David External Self Employed |  |  |  | Implementation | U7 |  | Ov3.6.0_U6, DBS / EWS |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 12 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p><span lang=EN-US style="font-size:10pt;"><font color="#666666" face="Times New Roman">1. Create a&nbsp;analog point</font></span></p><font face="Times New Roman" size=3> </font><p><span lang=EN-US style="font-size:10pt;"><font color="#666666" face="Times New Roman">2. Define all alarm limits</font></span></p><font face="Times New Roman" size=3> </font><p><span lang=EN-US style="font-size:10pt;"><font color="#666666" face="Times New Roman">3. Open Point in Ovation Point Information window</font></span></p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><p><span lang=EN-US style="font-size:10pt;"><font color="#666666" face="Times New Roman">4. Now point&nbsp;is in alarm</font></span></p><font face="Times New Roman" size=3> </font><p><span lang=EN-US style="font-size:10pt;"><font color="#666666" face="Times New Roman">5. Right click on the point &amp; shelve the whole point</font></span></p><font face="Times New Roman" size=3> </font><p><font color="#666666"><font face="Times New Roman"><span lang=EN-US style="font-size:10pt;">6. The Value of&nbsp;&quot;Suppressed alarm status (Bit27) of 1W is showing 0&quot;&nbsp;&nbsp;instead of 1</span></font></font><font color="#666666"><font face="Times New Roman"><span lang=EN-US style=""><font size=3>&nbsp;</font></span></font></font></p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 139635
36227 | FINDING | view algorithm order's number not updated as algorithm order is changed | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-12 22:27 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-12 22:27 | 67428 |  |  | 2016-05-12 22:27 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-20 05:49 |  | <p>Algorithm ordering symbol at the bottom left corner of the control builder showing whether the algorithm ordering is automatic or manual does not change when algorithm ordering is changed from automatic to manual or manual to automatic. It changes only after we close the sheet and open it again.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Also when algorithm ordering is done the order of algorithms does not update with changing algorithm ordering. It shows updated algorithm order only after refresh. </p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U7 |  | <p>3.6.0_U6_Net#36&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Controller drop37/87 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>DBS Drop100 (WS12 64-bit)<br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <p>No Plans to fix the first issue (Status Bar Icon Not Updated when Algorithm Order Mode Changed)</p><p><br></p><p>Fixed Algorithm Order Number Updates to main view as order is edited.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Create a control sheet and add some algorithms to it. </p><p>2.Go to the view tab of the control builder and select algorithm ordering. </p><p>3. In the object browser window select algorithm and then go to the property editor window and change the ordering from automatic to manual or from manual to automatic. </p><p>4. Algorithm ordering symbol at the bottom left corner of the control builder&nbsp; does not update with changing algorithm ordering mode. </p><p>5. Now change the order of algorithms keeping ordering in manual mode.</p><p>&nbsp;6. The algorithms on the control sheet does not update with the changing algorithm order and reflects the initial algorithm order. </p><p>7. After refresh the algorithms shows the updated algorithm order.</p> |  | U6 |  |  | FINDING | [6 empty] | 96741
36233 | FINDING | AMS device manager is not reporting thum wired devices | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-21 01:23 | [11 empty] | USPITTFSService | 2016-04-21 01:23 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-21 01:23 |  | While testing Wireless HART, it is observed&nbsp;AMS is reporting wireless devices&nbsp;but unable to report the Thum wired&nbsp;device. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation3.6.0_U6</p><p>OS-WS12,WIN7 64 BIT.</p> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the AMS device manager</p><p>2)Click on&nbsp;Device connection View option</p><p>3)Rebuild Hierarchy.</p><p>It is observed that wireless devices are seen on AMS device manager but thum wired device&nbsp;were not seen on AMS</p><p><br></p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 95345
36234 | FINDING | Test procedure 3.6.0_CONTROLLER_SVTP_rev5.6 needs changes | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-21 01:59 | [11 empty] | USPITTFSService | 2016-04-21 01:59 | [7 empty] | Lal, Ramesh External | 2016-04-21 01:59 |  | 4/21/16: Deluxe point do not allow configuring I/O Module&nbsp;if Third Party Device is External Ovation Network. Therefore, I/O Access Path can't be defined for Deluxe points. These points do not have TT field in Hardware tab of Point Info. Hence, Deluxe points can't be tested for External Ovation Network driver. In view of this Test Case 5.24.6 c), d) of Test procedure 3.6.0_CONTROLLER_SVTP_rev5.6 should be removed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U6 |  |  | FINDING | [6 empty] | 95350
36238 | FINDING | Virtual Controller network daemon requires new configuration | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:57 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:57 | 68047 |  |  | 2016-06-07 13:57 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-21 08:44 |  | <p>According to Dev and WindRiver, a new configuration is required in the vxsimnetd.conf file.&nbsp; This file is created by Studio and downloaded to VCH machines.&nbsp; The new configuration <span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">SUBNET_FILTERED_MCAST_IN has been added manually for 3.6.0 testing.&nbsp;&nbsp;&nbsp; If this new configuration is definitely required, please supply information to Dev Studio group so that it can be added to the file.&nbsp; </span></p><p><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><br></span></p><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><p><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Per email from G. Silvaggio 5/12/2016:</span></p><p><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">New configuration item in the file is:</span></p><p><br></p><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><p><font face=Arial>DEFAULT_FILTERED_MCAST_IN = 01:40:03:00:00:80;</font></p><p><font face="Times New Roman" size=3></font><font face="Times New Roman" size=3>and should be before the SUBNET_START item in the configuration file.&nbsp; In addition, the above specified MAC address is fixed and should be hardcoded based on the above specification.</font></p></span><p><br></p></span><p><br></p> | <p>Due to changes in the VxSim operating environment used in Virtual Controller Hosts (VCHs), the format of a VCH configuration file has changed. &nbsp;The change permits the VxSim newtwork daemon service to operate more efficiently by filtering out unnecessary network traffic. &nbsp;In order for this VCH configuration file to be updated, the user must open and save (via Ok or Apply) each VCH in the Ovation Developer Studio.&nbsp; This will generate a new version of the vxsimnetd.conf file which must be subsequently Downloaded to the target VCH drop.</p> |  |  | <p>The affected area is in the Engineering Tools software which creates the vxsimnetd.conf file for Virtual Controller Hosts (VCHs).&nbsp; Note that the user must open and then save each VCH in the Ovation Developer Studio.&nbsp; This will generate a new version of the file which can be subsequently Downloaded to the target drop.</p><p>Tests should verify that the file is generated on the database server in each VCH drop's &quot;config&quot; folder in the OvPtSvr directory structure and conforms to the proper format as indicated in the Description of this Finding.</p><p>Testing should also verify that the applicable VxSim network configuration(s) take place on the VCH following download (and reboot).</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Augustine, Lisa EMR SYSS PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U8 |  | Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The format of the vxsimnetd.conf will be modified based on the information supplied in this finding's Description. | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U6 |  |  | FINDING | [6 empty] | 98352
36251 | FINDING | Deluxe points U8 and U9 field is not showing the time of scan data | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2016-04-22 03:33 | [11 empty] | USPITTFSService | 2016-04-22 03:33 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-22 03:33 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><span style="color:black;font-size:12pt;"><font face="Times New Roman">The time that a point’s value has been read from I/O shall be recorded in the U8 and U9 fields of deluxe points.<span style="">&nbsp; </span>The controller software will store the time when the I/O cycle begins. This time will be copied into every point for every I/O cycle. But on ovation3.6.0_U6, it is observed that&nbsp;Deluxe points U8 and U9 field is not showing the time of scan data</font></span></b></p><span style="color:black;font-size:12pt;"><font face="Times New Roman"><p>Note-Deluxe points U8,U9 fields&nbsp;was updating properly on Ovation3.6.0_U4 build.</p></font></span><p style="margin:0in 0in 0pt;"><b style=""><span style="color:black;font-size:12pt;"><font face="Times New Roman"><br></font></span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><span style="color:black;font-size:12pt;"><font face="Times New Roman">&nbsp;</font></span></b></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation3.6.0_U6</p><p>OCR1100 and OCR400</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developers&nbsp;studio</p><p>2)Create DA,DD,DP hardware points.</p><p>3)Load the controller</p><p>4)Open the points on Point information window.</p><p>5)Verify the U8 and U9 fields. Time of scan data not available on U8,U9 fields.</p><p>Screenshot is also attached for your reference.</p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 95420
36253 | FINDING | Online Help is not opening from Alarm Shelve Shift Configuration & Shift Time window. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-24 06:00 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-24 06:00 | 3.6.0_U7 |  |  | 2016-05-24 06:00 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-22 04:51 |  | <p>Online Help is not opening from Alarm Shelve Shift Configuration &amp; Shift Time window.</p><p>When clicked on help tab of Alarm Shelve Shift Configuration (or Shift Time) window,&nbsp;it says &quot;Can't load help file=c:\Ovation\help\EN\OvPtStudio.chm', help id=1903&quot;.</p><p>Please find attached snapshots.</p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">PP:05/24/2016-Verified in Ov3.6.0_U9 &amp; found O.K.</font></span></p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">Hence, Finding is closed.</font></span></p> | SJ April 25, 2016: The help ids have been added to these topics. |  |  | SJ April 25, 2016: The help ids have been added to these topics. Please check OvptStudio online help in&nbsp;Ovation 3.6.0 U7 build. | 0 |  |  |  |  | 0 |  |  | SJ April 25, 2016: The help ids have been added to these topics. Please check OvptStudio online help in&nbsp;Ovation 3.6.0 U7 build. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Jain, Swati EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0 |  | Ov3.6.0_U6,Ws12R2,W7 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | SJ April 25, 2016: Check Ovation 3.6.0 U7 build. | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Opened Ovation Developer Studio.</p><p>2. &nbsp;Go to Alarm Shelve Shift Configuration under Network level.</p><p>3. Opened the Alarm Shelve Shift Configuration&nbsp;window</p><p>4. Clicked on Help tab.</p><p>5. The Help is not opened &amp; it is gives error.</p> |  | U6 |  |  | FINDING | [6 empty] | 97585
36254 | FINDING | VCH -> Host Based Redundancy -> Virtual controllers fail with <Error initializing watchdog interface> | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:49 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-08 08:49 |  |  |  | 2016-06-08 08:49 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-22 05:09 |  | VCH -&gt; Host Based Redundancy -&gt; Virtual controllers fail with &lt;Error initializing watchdog interface&gt; error |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Lal, Ramesh External | Capani, Innocenzo AUTOSOL PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | OV360_U6; W7 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | IC 6/8/16&gt; closed finding, updated DIR, track as SDR #36737. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Host Redundancy is configured successfully. (VCH Drop148 &amp; VCH DRop171)</li> <li>Redundant VC is configured successfully. (VC 41 OCR1100 on VCH Drop148 &amp; VC 91 OCR1100 on VCH Drop171)</li> <li>Vcoordinator shows correct refernce of&nbsp;VC 41 on VCH Drop148 &amp; VC 91&nbsp;on VCH Drop171.</li> <li>Download and reboot VCDrop41 and VCDrop91.</li> <li>The Ovation Error log reports &quot;Copy to Backup : Error initializing watchdog interface&quot;&nbsp;</li> <li>&quot;REDUND_PROC MSG :&nbsp;&nbsp;Switching to Failed Mode&nbsp;&quot;</li> <li>The controllers are cleared but could not be brought to Healthy Primary and Backup modes.&nbsp;</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 98398
36255 | FINDING | Incorrect help link is opening for I/O interface. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-24 04:00 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-24 04:00 | 3.6.0_U8 |  |  | 2016-05-24 04:00 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-22 05:24 |  | Incorrect help link is opening for I/O interface. |  |  |  | <p>MG (April 28, 2016): Added&nbsp;Help ID in AuthorIT. Correct Help topic will be&nbsp;invoked now.</p><p>Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> | 0 |  |  |  | LB-05/24/16:Verified on Ovation3.6.0_U9 and observed that ,correct help link is opening for I/O interface.Hence this finding is closed by validation. | 0 |  |  | <p>MG (April 28, 2016): Added&nbsp;Help ID in AuthorIT. Correct Help topic will be&nbsp;invoked now.</p><p>Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p><p><span style="color:rgb(34, 34, 34);line-height:normal;">MG (May 17, 2015): The Finding 36432 is fixed and the online help will be available.&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);line-height:normal;">Check the OvptStudio help in the Ovation 3.6.0 U8 build.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>Ovation3.6.0_U6</p><p>OvPtStudio360 help file</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | MG (April 28, 2016): This finding has been fixed and&nbsp;will be available in U7 build.<div><span style="color:rgb(34, 34, 34);">MG (May 17, 2015): Available</span><span style="color:rgb(34, 34, 34);box-sizing:border-box;">&nbsp;in the Ovation 3.6.0 U8 build.</span></div><div><span style="color:rgb(34, 34, 34);box-sizing:border-box;"><p>LB-05/24/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p></span><br></div> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the developers studio</p><p>2)Go to controller drop&gt;I/O Devices&gt;I/O interfaces/I/O Interface 1 local ovation, right click and open it and verify its help link.</p><p>It is opening the help link of I/O device number</p> |  | U6 |  |  | FINDING | [6 empty] | 97572
36257 | FINDING | Entries of non-existent CSLS are seen in Control Builder Operations Window | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-05 13:13 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-05 13:13 |  |  |  | 2016-05-05 13:13 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-22 06:05 |  | <p>Entries of non-existent CSLS are seen in Control Builder Operations Window&nbsp;for SIS CHARMs Setup.</p> <p>a. We have configured 16 CSLSs on our system. But while we try to do any Control Builder Operation like Compile/Export/Import, it lists 18 CSLSs out of which&nbsp;two CSLSs&nbsp;do not exist. </p> <p>b. Control Sheets inside are also seen in those CSLSs. </p> <p>c. Compilation of those Control Sheets give errors as &quot;Unable to Get Solver&quot;.</p> <p>d. .svg entries of these Control Sheets are also found at D:\OvPtSvr\ValSys36\VALNET36\UNIT0\ControlFunctions. For Control Sheets present in the configured Logic Solvers, .svg, .htm and .xml entries are present.</p> <p>&nbsp;</p> <p>Please see the attached screenshots of:</p> <p>a. View Live Devices List showing 16 CSLSs configured on our SIS CHARMs setup.</p> <p>b. Compile Operation Window showing in total 18 CSLSs of which CSLS12_D30 and CSLS13_D30 have not been configured on our system.</p> <p>c. Compile Operation window listing the Control Sheets present in non-existent CSLSs.</p> <p>&nbsp;</p> <p>Note:</p> <p>In previous builds, we had used the notation of CSLSs as CSLSx_D30&nbsp;and later changed it to D30-CSLS00x after new build was installed in the system.</p><p><br></p><p>Did you change the name of the CSLS in Studio?</p><p>Where there sheets attached to the CSLS before the name was changed?</p> |  |  |  |  | 0 |  |  |  | <p>Not a vaild use case.&nbsp; You cannot just rename the CSLS in the exp file and recompile the sheets or even bulk import the sheets.&nbsp; You would have to reimport all the sheets back into the appropriate CSLS.</p><p><br></p><p>No Plans to fix.&nbsp; It would be impossible for the compile to match the previous names to the new names.&nbsp; </p> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U6 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>SIS Controller Drop30/80</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>In total, 16 CSLSs have been configured and commissioned on the setup. (D30-CSLS001-D30-CSLS0016)</font></span></p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Right Click on the Controller Drop and select Control Options.</p> <p>2. Select any of the Operation from Compile/Export/Import</p> |  | U6 |  |  | FINDING | [6 empty] | 96341
36258 | FINDING | Mention of Digital Secure Parameter Clear Procedure is not mentioned in any SIS User Manual | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:40 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:40 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-22 06:28 |  | <p>Mention of Digital Secure Parameter Clear Procedure is not mentioned in any SIS User Manual.</p> <p>Digital Secure Parameters in SIS CHARMs need to be cleared in certain circumstances which should be clearly mentioned in the manual.</p> <p>Please see the attached screenshot as Clear-DSP.png.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U6 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Go to SIS Controller Drop --&gt; I/O Devices --&gt; I/O Device 5 Ovation SIS CHARMs --&gt; LSN --&gt; SIS CHARMs Logic Solvers --&gt; Digital Secure Parameter.</p> <p>2. Right Click on any DSP and select Clear.</p> |  | U6 |  |  | FINDING | [6 empty] | 111016
36259 | FINDING | Help File for Digital Secure Parameter is not working | Maggu, Mukesh EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-04-27 01:51 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-22 06:43 |  | <p>Help File for Digital Secure Parameter is not working.&nbsp;Upon clicking on 'Help' we get an error message as</p> <p><em>&nbsp;&quot;Can't load Help File = 'C:\Ovation\help\EN\OvPtStudio.chm', HelpID=1303&quot;</em></p> |  |  |  | MM(4/27/16): Will fix in the future released of the manual. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;">Ov3.6.0_U6 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | MM(4/27/16): Will fix in the future released of the manual. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Go to SIS Controller Drop --&gt; I/O Devices --&gt; I/O Device 5 Ovation SIS CHARMs --&gt; LSN --&gt; SIS CHARMs Logic Solvers --&gt; Digital Secure Parameter.</p> <p>2. Right Click on any DSP and open it.</p> <p>3. Click on Help.</p> |  | U6 |  |  | FINDING | [6 empty] | 112961
36260 | FINDING | Incorrect message is displayed when the user tries to Lock/Unlock/Reboot the CSLS when both the Controllers are off. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-23 09:36 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-23 09:36 |  |  |  | 2016-05-23 09:36 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-22 09:13 |  | <p>Incorrect&nbsp;message is displayed when the user tries to Lock/Unlock/Reboot the CSLS when both the Controllers are off.</p><p>&quot;It displays the message as 'INTERNAL ERROR: Partner Drop is not in control' while when the user performs Clear and load operation then the correct message is displayed as &quot;Neither Drop30 or Drop80 were found to be in a Control state'.</p><p>Please find attached the error messages when</p><p>a. Lock/Unlock/Reboot Operation is performed.</p><p>b. Clear/Load operation is performed.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Ov3.6.0_U6 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | No Plans To Fix extremely abnormal situation (Both Controller are non-operational) error message. | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Power Off both the Controller Drops.</p><p>2. Perform Lock/Unlock/Reboot operation on the CSLS.</p> |  | U6 |  |  | FINDING | [6 empty] | 97492
36262 | FINDING | From Finding 36170 - FACEPLATE algorithm online help link is incorrect | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:18 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:18 |  |  |  | 2016-04-26 15:18 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 13:53 |  | LC 04/22/2016: Creating a software finding for Steve to replace Finding 36170.&nbsp; New Qt software does not recognize our context IDs. Therefore, it does not display the correct algorithm help. This applies to Control Builder and Signal Diagrams. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Development |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Duplicate of 35910 - Invalid Context Ids in QT Help Documents. |  | U6 |  |  | FINDING | [6 empty] | 95745
36263 | FINDING | From Finding 35910 - Control Builder Help not working | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-24 23:35 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-24 23:35 | 67748 |  |  | 2016-05-24 23:35 |  |  |  | Casteel, Linda EMR SYSS PWS PITT | 2016-04-22 13:58 |  | <p>LC 04/22/2016:&nbsp; From Finding 35910, this is a software issue (Qt), not a documentation issue.&nbsp; Finding 35910 says, &quot;When user adds an algorithm on control sheet and open its help by right clicking and selecting the help option ,details of that particular algorithm will open. But when user is adding an algorithm on control sheet and try to open its help file by right clicking and selecting the help option ,it is observed that details of last opened algorithm help&nbsp;got open&nbsp;which is not correct.&quot;</p> |  |  |  |  | 0 |  |  |  | ST(05/25/2016): Checked in Ov3.6.0_U9 build, issue is fixed. So closing this finding. | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Tripathi, Sandeep AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Development |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U6 |  |  | FINDING | [6 empty] | 97662
36264 | FINDING | Redundant EWS do not reflect correctly in System Viewer | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-17 06:47 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-05-17 06:47 | 67391 |  |  | 2016-05-17 06:47 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-04-23 00:56 |  | <p>Redundant EWS do not reflect correctly as redundant controllers drops in System Viewer; instead appear as simplex machines and partner drop ID&nbsp;also don't reflect. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Wozniak, Diane M EMR SYSS PWS PITT | Sahay, Madhukar EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | PS 17May16: The above mentioned issue is found fixed. A fresh pair of EWS was added to UNIT2 and systemviewer demonstarted correct behaviour. Hence the finding is Closed as fixed. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Configure EWS redundancy. (Here Drop148 &amp; Drop171 on Net#26 were configured as redundant EWS drops)</li> <li>Verify in graphics, the status is seen correctly as Primary &amp; Backup EWS.</li> <li>Verify in PI, the status is seen correctly as Primary &amp; Backup with the partner drop IDs as desired. Attached PI_Drop148_Drop171.jpeg </li> <li>However,&nbsp;in System Viewer, the status is seen as simplex drop also the Partner ID is&nbsp;seen as 0. Attached Drop148.jpeg &amp; Drop171.jpeg. Also, the drop mode reflects the status&nbsp;correctly as In Control &amp; Backup.&nbsp;</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 97053
36265 | FINDING | Incorrect message appears while Commissioning or Decommsissioning field bus bus device from system viewer | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-16 02:56 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-16 02:56 | 67630 |  |  | 2016-05-16 02:56 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-04-23 02:57 |  | <p>when a point of a fieldbus function block&nbsp; is commissioned or uncommissioned in system viewer the message to confirm commission or uncommission request is incorrect. When point is uncommissioned message appears &quot;confirm commission ON request&quot; and when point is commissioned message appears &quot;confirm commission OFF request&quot;</p><p><br></p><p>As per documentation commissioning is setting commission On and Uncommissioning is setting Commission Off.</p><p>Also message box appears in upper right corner of the screen and&nbsp;a part of the message is not readable. Please refer attached&nbsp;snapshot &quot;message.jpg&quot;.</p><font size=2><p><br></p></font><p><br></p><font size=2><p><br></p><p><br></p></font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0_U7 |  | <p>3.6.0_U6_Net#26&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>Controller drop24/74 (OCR400)&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p><p>DBS Drop220 (WS12 64-bit)</p> |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Select a analog point from the point attribute grid in system viewer.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>2. Select the commission tab from the top ribbon bar.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>3. select the uncommission buttons, a window with a message &quot;confirm commission ON request&quot; appears to confirm the uncommision operation.</p><p>4. Please refer the attached snapshot &quot;commission.jpg&quot;.</p> |  | U6 |  |  | FINDING | [6 empty] | 96868
36266 | FINDING | SIS Event messages may be more descriptive for scenario where base plate with incorrect Address plug or duplicate address. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-24 02:53 | [11 empty] | USPITTFSService | 2016-04-24 02:53 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-24 02:53 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>SIS Event messages may be more descriptive for scenario where base plate with incorrect Address plug or duplicate address.</font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Following observation for scenario where bad address or incorrect address plug on Base:</font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri><b style=""><font size=3>RN points status for CSLS where base with incorrect address plug</font></b><font size=3> .</font></font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Bit#5 [IO Channel Error] go High and cause Alarm.</font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Bit#11 [Maintenance Alert] go High and cause Alarm. </font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Red (flashing ten times per second) due to Duplicate address.</font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><b style=""><font face=Calibri size=3>CHARMS LEDs behavior.</font></b></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font><font face=Calibri><span style=""><font size=3>&nbsp;</font></span><font size=3>Green then red flashing three or four times per second due to bad address or incorrect address plug: this pattern is seen on a group of 12 LS CHARMs on the base.</font></font></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> <span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><strong>SIS Events shows following HAC messages for the event</strong></span></font></p><font face="Times New Roman" size=3><span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p style="margin:0in 0in 10pt;"><strong><em>MM/DD/YYYY <span style="">&nbsp;</span>Time <span style="">&nbsp;</span>&lt;Hac: CSLS&gt;:<span style="">&nbsp;&nbsp; </span>Set: CHARM Error</em></strong></p><p style="margin:0in 0in 10pt;"><strong><em><font face="Times New Roman" size=3> </font>MM/DD/YYYY <span style="">&nbsp;</span>Time <span style="">&nbsp;</span>&lt;Hac: CSLS&gt;:<span style="">&nbsp;&nbsp; </span>Cleared: CHARM Error</em></strong></p><p style="margin:0in 0in 10pt;"><font face="Times New Roman" size=3> </font>SIS event messages for the events are generic Hac messages not specific for the incorrect Address Plug .<span style="">&nbsp;&nbsp; </span></p><p style="margin:0in 0in 10pt;"><strong>Enhancement Request</strong>: Event may be more descriptive so that User may know about the problem of Bad address or incorrect Address plug.</p></span></font><p style="margin:0in 0in 10pt;"><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0+Historical Review + SIS Events |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>Configure Charms IO on Base. &nbsp;</p><p>LEDs are on Charms in Normal Mode.</p><p>Place incorrect Address plug on Base with configured Charms IO. e.g. Remove Address plug from Base#2 and place Address plug#5 on Base#2</p><p><font face=Calibri><span style=""><font size=3>&nbsp;LED pattern on a group of 12 LS CHARMs on the base#2 is seen: </font></span><font size=3>Green then red flashing three or four times per second due to bad address or incorrect address plug.</font></font></p><p><font face=Calibri size=3>RN point of CSLS to&nbsp; Bit#5, Bit#11 go high and Alarm.</font></p><p><font face=Calibri size=3>In Historical review, Generate SIS Events.</font></p><p><font face=Calibri size=3><br></font></p> |  | U6 |  |  | FINDING | [6 empty] | 95517
36267 | FINDING | Online help for SIS charms need to be updated with correct screenshots of attributes screenshot for HART Input and Output charms IO. | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:45 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:45 | 3.6.0_U7 |  |  | 2016-05-20 06:45 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-24 03:19 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Online help for SIS charms need to be updated with correct screenshots of attributes screen for HART Input and Output charms IO.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Screenshot for Two-State DVC Output CHARMS Class. For reference see the attached screenshot “CHARMS_DVC_ATTRIBUTES_SCREENSHOTS.jpg”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Screenshot for Two-State DVC Output Redundant CHARMS Class. For reference see the attached screenshot “CHARMS_RED_DVC_ATTRIBUTES_SCREENSHOTS.jpg”</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Screenshot for HART Analog Input CHARMS Class also need to be updated.</font></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>MM(4/27/16): Updated the required screen shots. Please check figure 123 and 124 in the sections 4.11.8 and 4.11.9 respectively in the manual of SIS Charms. The pdf (<strong>OW360_43-25_Apr</strong>) is kept at the following location:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a></p><p>Please see the online help too in U7 built. </p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation | <p>MM(4/27/16): Updated the required screen shots. Please check figure 123 and 124 in the sections 4.11.8 and 4.11.9 respectively in the manual of SIS Charms. The pdf (<strong>OW360_43-25_Apr</strong>) is kept at the following location:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a></p><p>Please see the online help too in U7 built. </p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p><br></p><p>This issue has been fixed and&nbsp; available in U7 built. </p><p>VP-05/20/2016&gt; Verified with U8, Found fixed. Hence finding is closed.&nbsp;</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | See the online help for &quot;<font face=Calibri size=3>To Configure Two State DVC Redundant CHARM Class</font><font face="Times New Roman" size=3>&quot; and&nbsp; &quot; <font face=Calibri>To Configure Two State DVC&nbsp;CHARM Class</font> &quot;</font> |  | U6 |  |  | FINDING | [6 empty] | 97340
36268 | FINDING | Help button on SIS IO Charms configuration/Attributes window open a page, there is no link of required information. It needs to link with help for configuration and Attributes parameters detail. | Maggu, Mukesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:26 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-20 06:26 |  |  |  | 2016-05-20 06:26 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-24 04:33 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Help button on SIS IO Charms configuration/Attributes window open a page, there is no link of required information. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Help button on SIS IO Charms configuration/Attributes window open a Help page, there is no link of required information. It needs to link with help for configuration and Attributes parameters detail. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Help button on SIS IO Charms configuration/ Attributes window does not provide configuration and Attributes parameters detail. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>It gives brief information about creating SIS Charms IO and prerequisites, no detail of Config/Attribute parameters detail. Also, on this Help window no link of page where required information of Charms IO configuration and Attributes parameters detail are available. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>For reference, screenshot is attached.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3><br></font></p><font face="Times New Roman" size=3> </font> |  |  |  | MM (4/25/16): Check the online help in U7. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation | MM (4/25/16): Check the online help in U7. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | <p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Steps:</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 10pt;"><font face=Calibri><font size=3>1. <span style="">&nbsp;</span></font><font size=3>Select a Configured Charms IO and Open it. There are two tabs: a. Config </font><font size=3><span style="">&nbsp;</span><span style="">&nbsp;</span></font><font size=3>b. Attributes</font></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>12 Click the Help button on window.</font></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>MM (4/25/16): Check the online help in U7. resolution is available&nbsp; in U7 Built.</p><p>VP- 05/20/2016: Verified in U8, found fixed. Finding is closed.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | MM (4/25/16): Check the online help in U7. |  | U6 |  |  | FINDING | [6 empty] | 97330
36269 | FINDING | An Error is encountered for the workstation report in OSR | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Rathi, Ankur AUTOSOL PWS NOIDA | 2016-05-25 06:27 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2016-05-25 06:27 | 67426, 67634 |  |  | 2016-05-25 06:27 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2016-04-24 22:33 |  | An error is seen in generated OSR report for every workstation &quot;An exception was caught while searching for Ovation add-on software......&quot;&nbsp;(refer attachment &quot;Error in OSR.JPG&quot;). |  |  |  |  | 0 |  |  |  | <p>AR Tested in Ov3.6.0_U9</p><p>fixed in U9</p> | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | Ws12 R2, Ovation 3.6.0_U6 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Generate the OSR report via 'Sure Service' application, C:\ProgramData\Microsoft\Windows\Start Menu\Ovation\Ovation Utilities\SureService Ovation System Registration Utility.</p><p>2. Check the 'Errors' in the generated report for&nbsp;'Workstations'</p> |  | U6 |  |  | FINDING | [6 empty] | 97697
36270 | FINDING | SVTP "3.6.0_SIS_CHARMS_SVTP_rev1.4_SHS.docx" needs to be updated | Kumar, Shailendra EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-25 00:36 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-25 00:36 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-25 00:32 |  | SVTP &quot;3.6.0_SIS_CHARMS_SVTP_rev1.4_SHS.docx&quot; needs to be updated. The issue are mentioned below:<div><br></div><div>1. Test Case 5.6.5 &amp; 5.6.7 :&nbsp;</div><div>&nbsp; &nbsp; Test case &nbsp;5.6.5 should be &quot;Perform unplug if network cable from Primary Safety network port. It causes failure to Partner Safety network port. Verify the following&quot;.</div><div>&nbsp; &nbsp; Test case &nbsp;5.6.7 should be &quot;Perform unplug if network cable from Partner Safety network port. It causes failure to Primary Safety network port. Verify the following&quot;.<br></div><div><br></div><div>2. Test Case 5.6.10 :</div><div>&nbsp; &nbsp; Test case 5.6.10 Should be &quot;Reconnect network cables from N1 and N4 Ports of the SIS controller, Restore the primary controller. Verify the following&quot;</div><div><br>3. Section 5.6 :</div><div>&nbsp; &nbsp; 2 Test cases should be added, same as 5.6.9 and 5.6.10 for Failover to Primary SIS controller.&nbsp;</div><div><br></div><div>4. &nbsp;Section 5.9 :</div><div>&nbsp; &nbsp; &nbsp;A test cases should be added to &quot;Verify the following for CHARM class &quot;Voltage&quot;&quot;. Same as &nbsp;test cases 5.9.4.</div><div>&nbsp;&nbsp;</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Arora, Priyanka AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <ol><li>Open the mentioned SVTP.</li><li>Check the above mentioned test cases in SVTP.&nbsp;</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 95539
36274 | FINDING | User is able to use same Digital Value Controller channel (LSDVC) reference multiple times at different outputs within same Control Sheet | Hutchison, Steven EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:12 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-26 15:12 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-25 06:37 |  | <p class=MsoNormal style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><b>Description:</b></font></font></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>User is able to use same&nbsp;</font></font><span style="font-family:Calibri;font-size:medium;">Digital Valve Control</span><font face=Calibri size=3>ler</font><span style="font-family:Calibri;font-size:medium;line-height:1.5em;">&nbsp;channel reference multiple times at different outputs within same Control Sheet. User is also able to load CSLS and load Controller&nbsp;without any error. For checking LSDVC DTA CHARM was used.</span></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><b><i>Note:</i></b>&nbsp;If user is adding same Digital Valve Control</font></font><font face=Calibri size=3>ler</font><span style="font-family:Calibri;font-size:medium;line-height:1.5em;">&nbsp;channel in other Control sheet whether in same Control Module or different Control Module, then an error “Point is originated by another Sheet” is observed while saving the Control Sheet in Control Builder.</span></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font size=3><font face=Calibri><b>Attachment:</b></font></font></p><p class=MsoNormal style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>Please find attached&nbsp;<i>LSDVC_Multiple.png</i>&nbsp;for the screenshot of the Control Sheet using multiple references of same&nbsp;</font></font><span style="font-family:Calibri;font-size:medium;">Digital Valve Control</span><font face=Calibri size=3>ler</font><span style="font-family:Calibri;font-size:medium;line-height:1.5em;">&nbsp;channel at different output points.</span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Create a control having multiple LSDVC algorithms.<br></li><li>Assign the same DVC channel to all Algorithms.</li><li>Save the sheet. (No error &nbsp;is observed)</li><li>Load the CSLS and controller. (Loads successfully)&nbsp;</li></ol><div><br></div> |  | U6 |  |  | FINDING | [6 empty] | 95741
36275 | FINDING | Synchronize Online Functionality in Control Builder doesn't work for SIS Control Sheets | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-21 05:11 | [11 empty] | Aditya, Abhinav AUTOSOL PWS NOIDA | 2017-06-21 05:11 | 76415 |  |  | 2017-06-13 23:44 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-04-25 06:39 |  | <p>Synchronize Online Functionality in Control Builder doesn't work for SIS Control Sheets. </p> <p>&nbsp;</p> <p>PA 5/26/16: As per the Dev, SIS Control Functions are only published when the Logic Solver is Loaded. So this needs to be documented.</p> | <p><br></p><p>AA (05-26-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 21.4</u> of the manual has been modified. Step <u>number 7</u> has been added. The sentence added is as follows:</p><p align=LEFT></p><p><br></p><font size=2><p><strong>7. SIS Control Functions are only published when the Logic Solver is loaded. </strong></p></font><p><br></p><p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span><p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p><p><br></p><p><strong>The name of the pdf is OW360_80.pdf</strong></p> |  |  |  | 0 |  |  |  | <p>AA(06-21-2017): The following note has also been added:</p><p><br></p><span lang=EN-NZ></span><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2></font></font><p><i><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2><b>Note:</b></font></font></font><font face=Arial size=2><font face=Arial size=2> You can<span lang="">not</span><span lang=EN-NZ> use the </span></font></font></i><a href="https://uspit-tfs-v.emrsn.org/tfs/_static/tfs/12/App_Themes/Default/H_142701"><i><u><font color="#0000ff" face=Arial size=2><font color="#0000ff" face=Arial size=2><font color="#0000ff" face=Arial size=2><span lang=EN-NZ>Synchronize Online function</span></font></font></font></u></i></a><i><font face=Arial size=2><font face=Arial size=2><span lang=EN-NZ> for SIS Control Sheets</span><span lang="">, since they are published</span><span lang=EN-NZ> only when the Logic Solver is loaded.</span></font></font></i></p> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Documentation | <p><br></p><p>AA (05-26-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 21.4</u> of the manual has been modified. Step <u>number 7</u> has been added. The sentence added is as follows:</p><p align=LEFT></p><p><br></p><font size=2><p><strong>7. SIS Control Functions are only published when the Logic Solver is loaded. </strong></p></font><p><br></p><p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span><p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p><p><br></p><p><strong>The name of the pdf is OW360_80.pdf</strong></p><p><strong><br></strong></p><p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p><p>The updated manual (OW360_80V2) is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP3/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Agarwal, Gaurav EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [6 empty] | Implementation | OV360FP3U1 |  | <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U6 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span></p> <p><span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2></font></span>&nbsp;</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  | <p>SIS Control Functions are only published when the Logic Solver is Loaded.</p> <p><br></p> <p>AA (05-26-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 21.4</u> of the manual has been modified. Step <u>number 7</u> has been added. The sentence added is as follows:</p> <p align=left></p> <p><br></p><font size=2> <p><strong>7. SIS Control Functions are only published when the Logic Solver is loaded. </strong></p></font> <p><br></p> <p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span> <p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p> <p><br></p> <p><strong>The name of the pdf is OW360_80.pdf</strong><br></p> <p><br></p> <p><br></p> <p>AA (05-30-16): This issue will be taken care in the next Ovation release.</p> <p><br></p> <p><strong><br></strong></p> <p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p> <p>The updated manual (OW360_80V2) is kept at:</p> <p><a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> <p>&nbsp;</p> <p>ASG (06-14-2017)&gt;</p> <p>Verified </p> <p>1. In the Topic 21.4 of Control Builder manual (OW360_80V2) is kept at <a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> <p>2. In OVA360FP3_U1 Control Builder help (topic 'Best practices for using SIS algorithms on a sheet)</p> <p>that step 7 (SIS Control Functions are only published when the Logic Solver is loaded)<strong> </strong>has been added.</p> <p>Hence closing the finding as Confirmed to be Fixed.</p><p><br></p><p>AA(06-21-2017): The following note has also been added:</p><p><br></p><span lang=EN-NZ></span><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2></font></font><p><i><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2><font color="#000040" face=Arial size=2><b>Note:</b></font></font></font><font face=Arial size=2><font face=Arial size=2> You can<span lang="">not</span><span lang=EN-NZ> use the </span></font></font></i><a href="https://uspit-tfs-v.emrsn.org/tfs/_static/tfs/12/App_Themes/Default/H_142701"><i><u><font color="#0000ff" face=Arial size=2><font color="#0000ff" face=Arial size=2><font color="#0000ff" face=Arial size=2><span lang=EN-NZ>Synchronize Online function</span></font></font></font></u></i></a><i><font face=Arial size=2><font face=Arial size=2><span lang=EN-NZ> for SIS Control Sheets</span><span lang="">, since they are published</span><span lang=EN-NZ> only when the Logic Solver is loaded.</span></font></font></i></p> | 17 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create a SIS Control Sheet. </p> <p>2. Load the CSLS and the SIS Controller Drop.</p> <p>3. Make some changes in the Control Sheet in the Control Builder.</p> <p>4. Save the Control Sheet.</p> <p>5. Go to Tools and select Synchronize Online option.</p> <p>6. The SIS Control Sheet is not listed in the list.</p> |  | U6 |  |  | FINDING | [6 empty] | 114641
36278 | FINDING | SDR 35904 Failed: C1 field in the algorithm template is not updated. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-05-20 00:04 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-05-20 00:04 | 67812 |  |  | 2016-05-20 00:04 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-25 13:02 |  | C1 &quot;Release output target (2)&quot; field displays a value of -10000 instead of 10000 as per Algorithm template attached in SDR 35904. The algorithm template should be updated to display the same. |  |  |  |  | 0 |  |  |  | TK 20-May-2016 : The algorithm template&nbsp;is updated to display the same. Hnece closing this finding. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U8 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Updated template with 10000 for C1. |  | U6 |  |  | FINDING | [6 empty] | 97280
36282 | FINDING | SimControl.exe is not working as expected. | Shiferaw, Tedla AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-04-26 09:16 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-04-26 09:16 | [7 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-04-25 22:51 |  | SimControl.exe is not working as expected. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>Ovation:- Ov 3.6.0_U6</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>Drop:- Drop148 on Net#26</font></span></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>1:- Initially Created variable points in Virtual Controller and loaded it.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>2:- Above created point is appearing in the Alarm window, trend and PI properly. See Screen shots <b style="">“Variable point.jpg”</b></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>3:- Run SIMCommand.exe -i –a and reboot the system.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>4:- Start the Alarm window . “Simulator Ovation Alarm System 1 ” window is open. See screen shots <b>“Simulator Ovation Alarm window.jpg ”</b></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>5:- <span lang=EN-IN style="">Freeze/Save the snapshot (e.g. AV004) using SimControl&nbsp; GUI.</span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>6:- Execute Run Command from SimCOntrol GUI.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>7:- Above Point is properly updating.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>8:- Freeze/Load the snapshot (AV004) and Execute Run Command .</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri><font size=3><span style="">&nbsp; </span><span style="">&nbsp;&nbsp;&nbsp;</span><span style="">&nbsp;&nbsp;&nbsp;</span></font><font size=3>Point starts updating in PI and Signal Diagram but it is not updating in trend. See screen shot</font><b><font size=3> “ Stop Updating in Trend.jpg”</font></b></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp; To overcome this issue we need to refresh trend window.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span lang=EN-IN style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style=""><font face=Calibri size=3>As per user point of view , user should not use refresh option after Executing Run Command.</font></span></p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 95688
36284 | FINDING | THUM wired device going IN and OUT from GOOD quality | Ritchie, Mark AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-05-09 14:26 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-05-09 14:26 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-04-26 00:55 |  | <p>THUM has been&nbsp;connected with&nbsp; HART wired device (644 ,rev 7).</p><p>It is observed that all the parameters (PV,SV, etc) of wired device (644) are&nbsp;switching GOOD to BAD&nbsp;quality.</p><p>(please refer attached snapshot)</p><p>However 1420 GUI,&nbsp;all the parameters of wired device remains always GOOD.&nbsp;&nbsp;</p> |  |  |  |  | 0 |  |  |  | GWS&gt; Assigning to Mark Ritchie to investigate. | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U6</p><p>OCR1100 </p> |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. 1420 wireless gateway has been configured in studio ( as per manual CON_035)</p><p>2. Configured Wireless HART device and driver in drop38/88 ( as per manual CON_035)&nbsp;&nbsp;&nbsp;</p><p>2. &nbsp;Connected THUM to HART wired device (644 , rev 7)</p><p>3. HART wired device can be seen as a live device in 1420 web interface&nbsp;GUI</p><p>4. In studio,&nbsp;select&nbsp;Wireless Gateway (at network level)&nbsp;&amp; perform right click &amp; click &quot;Engineer&quot;&nbsp;to open&nbsp;Data Base configuration window.</p><p>5. THUM and&nbsp;the wired device are seen as&nbsp;Unassigned device. in Sensed device subwindow&nbsp;&nbsp;</p><p>6. Assigned the wired device.&nbsp;&nbsp;&nbsp;</p><p>7. Now in&nbsp;drop38/88 , created LA points&nbsp;&amp; assigned&nbsp;various parameters (PV, SV, TV etc)&nbsp;of&nbsp;wired HART device</p><p>8. It is observed that all the parameters of wired HART device&nbsp;switching between GOOD and BAD quality&nbsp;</p><p>&nbsp;&nbsp; irrespective of their values are always remain GOOD in 1420 web interfcae&nbsp;GUI.</p><p>&nbsp;<br></p> |  | U6 |  |  | FINDING | [6 empty] | 96503
36285 | FINDING | Information regarding insert a drop point on help file is not correct | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 07:01 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 07:01 | 3.6.0_U8 |  |  | 2016-05-23 07:01 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-26 01:38 |  | <p>following &nbsp;Information regarding insert a drop point on help file is not correct</p><p>1)Drop point navigation on developers studio.</p><p>2)Attached picture.</p><p>3)Alarm tab description.</p><p>Screenshot is also attached for your reference.</p> |  |  |  | <p>MG (April 26, 2016): According to this finding,&nbsp;updated the&nbsp;following&nbsp;in&nbsp;the&nbsp;<strong>Section 5.4.2 To insert a new drop point</strong> of the&nbsp;Controller (OCR 400 and 1100) user guide for Ovation 3.6. This is available in online help for U7 build.</p><ul><li>Updated the Point no. 2 navigation path</li><li>Figure 18: New drop point dialog box has been updated</li><li>Added the fields and their description of the Alarm&nbsp;in the table New drop point dialog box descriptions</li></ul><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p> | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed the correct&nbsp;information regarding insert a drop point on help file topic.Hence this finding is closed by validation | 0 |  |  | <p>MG (April 26, 2016): According to this finding,&nbsp;updated the&nbsp;following&nbsp;in&nbsp;the&nbsp;<strong>Section 5.4.2 To insert a new drop point</strong> of the&nbsp;Controller (OCR 400 and 1100) user guide for Ovation 3.6. This is available in online help for U7 build.</p><ul><li>Updated the Point no. 2 navigation path</li><li>Figure 18: New drop point dialog box has been updated</li><li>Added the fields and their description of the Alarm&nbsp;in the table New drop point dialog box descriptions</li></ul><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>Ovation3.6.0_U6</p><p>OvPtStudio360 help file</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 26, 2016): This finding has been fixed and&nbsp;will be&nbsp;available in U7 build.</p><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the developer studio and verify the drop point details on OvPtStudio360 help file |  | U6 |  |  | FINDING | [6 empty] | 97478
36286 | FINDING | Information regarding load a controller drop on help file is not correct | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:49 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:49 | 3.6.0_U8 |  |  | 2016-05-23 05:49 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-26 01:38 |  | Information regarding load a controller drop on help file is not correct. Screenshot is also attached for your reference |  |  |  | <p>MG (April 29, 2016): According to this finding, updated the point no.&nbsp;6 in the&nbsp;<strong>Section 4.3.3&nbsp;To load the Controller&nbsp;drop </strong>of the Controller (OCR 1100) user guide for Ovation 3.6. This is available in U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p> | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that information regarding load a controller drop on help file is correct&nbsp;.Hence this finding is closed by validation | 0 |  |  | <p>MG (April 29, 2016): According to this finding, updated the point no.&nbsp;6 in the&nbsp;<strong>Section 4.3.3&nbsp;To load the Controller&nbsp;drop </strong>of the Controller (OCR 1100) user guide for Ovation 3.6. This is available in U7 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_58.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_58.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U7 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>Ovation3.6.0_U6</p><p>OvPtStudio360 help file</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 29, 2016): This finding has been fixed and&nbsp;is available in U7 build.</p><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the developer studio and verify the Information regarding load a controller drop on OvPtStudio360 help file. |  | U6 |  |  | FINDING | [6 empty] | 97462
36287 | FINDING | SVTP "3.6.0_CONTROLLER_SVTP_rev5.6.docx" needs modification. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-26 03:48 | [11 empty] | USPITTFSService | 2016-04-26 03:48 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-04-26 03:48 |  | <p>SVTP &quot;3.6.0_CONTROLLER_SVTP_rev5.6.docx&quot; needs changes as per the below mentioned details:</p><p><br></p><p>a) Test case 5.11.24.b&nbsp;should be&nbsp;changed as: &nbsp;&quot;Verify that <strong>RN</strong> points assigned to each Port update correctly.&quot;</p><p>b) Test case 5.11.25.b&nbsp;should be&nbsp;changed as: &nbsp;&quot;Verify that <strong>RN</strong> points assigned to each Port update correctly<strong>.&quot;</strong></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | GEC Lab |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please refer the details mentioned in Description tab of this finding. |  | U6 |  |  | FINDING | [6 empty] | 95663
36289 | FINDING | OCR1100 partner drop is showing offline state | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-12 06:05 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-12 06:05 |  |  |  | 2016-05-12 06:05 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-26 05:26 |  | <font face=Calibri size=3>Observation on OCR 1100 controllers: Partner controller drop is showing in offline mode but on rebooting of controller in control mode, partner controller comes in Control mode (which was in offline state).</font><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Detail: Setup: OCR1100-G02 [drop27/77, unit0, net#26].</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>We have observed the following for controllers on ovation3.6.0 Net#26 and Net#36.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><font face=Calibri size=3>1)</font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font face=Calibri size=3>Drop27 is showing offline mode while drop77 is on control mode. Also verified in PI and Controller diagnostics, Drop mode of drop27 is showing offline.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><font face=Calibri size=3>2)</font><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:7pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font face=Calibri size=3>We are able to perform drop download operation on drop27.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>After rebooting the drop77, drop27 comes in control mode and drop77 is showing offline mode. Again rebooted the drop27, drop77 takes the control and drop27 goes to offline state. </font></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Observed the same above scenario on drop36/86 controllers (OCR1100-G01).</span></p><p><br></p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><font face="Times New Roman" size=3> </font>Note: After deleting the compact flash data controller works fine but after&nbsp;powering off both the controller simultaneously and power on&nbsp;it one by one,&nbsp;partner controller drop&nbsp;starts behaves as mentioned above.</p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;">&nbsp;</p><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p> |  |  |  |  | 0 |  |  |  | <p>This issue is not observed on ovation3.6.0_U7.Hence this finding is closed by validation.</p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | <p>Ovation3.6.0_U6</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face=Calibri size=3>1)Verify the current state of drop27/77 on graphics/PI/Controller diagnostic.</font></p><p><font face=Calibri size=3>2)drop27 shows control mode while drop77 shows offline mode.</font></p><p><font face=Calibri size=3>3)Reboot the drop27,drop77 comes on control mode while drop27 goes to offline mode.</font></p><p><font face=Calibri size=3>Remote login details are also attached for your reference.</font></p> |  | U6 |  |  | FINDING | [6 empty] | 96681
36298 | FINDING | Bit#14 'Any Module Not Configured' bit is not working for CSLS RN Point | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-29 12:30 | [11 empty] | USPITTFSService | 2016-04-29 12:30 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-27 00:30 |  | <p>Bit#14 'Any Module Not Configured' bit is not working for CSLS RN Point</p><p>'Any Module Not Configured' bit is not working for CSLS RN Point. It is always reset and show state as 'Configured'.</p><p>According to the manual, this bit is set when a<span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;">t least one of the Control modules is not configured for SIF data.</span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U6 on DBS Drop100 (OS: Windows Server 2012 R2) |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.&nbsp;Delete all the Control Sheets from one of the Control Modules.</p><p>2. Load the CSLS and the Controller Drop (In Control).</p><p>3. As the bit remains reset even after step#2, so in the next step tried to delete all the Control Sheets from all the Control Modules.</p><p>4. 'Any Module Not Configured' bit remains reset.</p><p>5.&nbsp; remove node points from all Control Modules.</p><p>6. 'Any module not Configured' bit remains reset.</p> |  | U6 |  |  | FINDING | [6 empty] | 95972
36302 | FINDING | On VCH machine in Wind River WRTAP properties Maximum Buffer Number should be manually changed from 20 to 2000. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2016-05-20 01:39 | [11 empty] | Lal, Ramesh External | 2016-05-20 01:39 | 3.6.0_U8 |  |  | 2016-05-20 01:39 |  |  |  | Lal, Ramesh External | 2016-04-27 06:36 |  | <p>Following steps should be added in Ovation Virtual Controller user manual:</p><p>Under Network Connection select Wind River WRTAP</p><p>Right click and select Properties</p><p>Select Configure</p><p>In Wind River Properties window select Advanced tab</p><p>Select Maximum Buffer Number. In the Value field change 20 to 2000</p><p>Press O.K.</p> | AA (04-28-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). <strong>Topic 4.3.2</strong> has been added. The updated manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_57.pdf.</strong> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | <p>AA (04-28-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). <strong>Topic 4.3.2</strong> has been added. The updated manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_57.pdf.</strong></p><p><br></p><p>5/20/2016: RL - Checked the OW360_57.pdf document and on line help in 3.6.0_U8 and found O.K.. Finding closed.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0_U8 |  |  |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | AA (04-28-2016): I have added the required new topic to the Virtual Controller Manual (OW360_57). <strong>Topic 4.3.2</strong> has been added. The updated manual is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation">\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</a>. The name of the pdf is <strong>OW360_57.pdf.</strong> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | 3.6.0_U6 |  |  | FINDING | [6 empty] | 97296
36303 | FINDING | When Controller Fail over is done by removing N1 and N4 cables Logic Solver redundancy lost bit of CSLSes becomes high for 4 seconds (Approx) | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-05-12 10:41 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-05-12 10:41 |  |  |  | 2016-05-12 10:41 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-27 06:47 |  | When Controller Fail over is done by removing N1 and N4 cables of active controller, Logic Solver redundancy lost bit of CSLSes becomes high for 4 seconds (Approx)<div>After removing the N1 and N4 cables of Active controller, controller fail over happens and during the failover the Logic Solver redundancy lost bit of some CSLS becomes high for&nbsp;4 seconds (Approx)&nbsp;and then becomes low.&nbsp;</div><div>In Validation lab setup we have 16 CSLS configured out of which we observed for 10 CSLS.</div><div>Please find the attached Historical Review Logs. (N1 and N4 cables of active controller were removed at <i>04/27/2016 10:31:34</i>)</div><div><br></div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | This is per design:<br>The active controller is communicating with both CSLSs therefore the redundancy flag is up. The backup controller is communicating only with active CSLS only, therefore when the switchover happens it is expected.<br> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Select &quot;Fail Controller on Error&quot; for controller as true.</li><li>Remove the N1 and N4 cables of the controller. Controller Fail over happens.</li><li>Observe the Node points of CSLSes.</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 96702
36304 | FINDING | When Controller Fail over is done by removing N1 and N4 cables Registered bit of CSLSes becomes low for 13 seconds (Approx) | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-14 06:30 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-14 06:30 | U7 | [6 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-27 06:47 |  | When Controller Fail over is done by removing N1 and N4 cables of active controller, registered bit of CSLSes becomes low for 13 seconds (Approx)<div>After removing the N1 and N4 cables of Active controller, controller fail over happens and during the fail over the Registered bit of CSLS becomes high for&nbsp;13 seconds (Approx)&nbsp;and then becomes low.&nbsp;</div><div><br></div><div>Please find the attached Historical Review Logs. (N1 and N4 cables of active controller were removed at&nbsp;<i>04/27/2016 10:31:34</i>)</div> |  |  |  |  | 0 |  |  |  | Still when Controller Fail over is done by removing N1 and N4 cables Registered bit of CSLSes becomes low for 13 - 14 seconds (Approx).<div>Please find the attached historical review logs (<i>N1N4 Failover_Finding retest.txt</i>)</div><div>Controller Failover was done at&nbsp;05/14/2016 16:40:59.</div><div><br></div><div><br></div> | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation | U7 |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | The redundancy was improved in u7<br> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Select &quot;Fail Controller on Error&quot; for controller as true.</li><li>Remove the N1 and N4 cables of the controller. Controller Fail over happens.</li><li>Observe the Node points of CSLSes.</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 96850
36305 | FINDING | GBNt-OPC Browse point application is crashing | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-05-16 01:06 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-05-16 01:06 | 67591 |  |  | 2016-05-16 01:06 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-04-27 06:50 |  | <p><font face=Calibri>GBNT-OPC<span style="">&nbsp; </span><font size=3>Browse point application is crashing in the scenario mentioned in steps to reproduce. AppCrash message snapshot and Event Viewer details are attached for reference.</font><span style=""><font size=3>&nbsp;&nbsp;&nbsp;</font></span></font></p> |  |  |  | Retest above steps | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0u7 |  | <p><font face=Calibri>OV 3.6.0_U6. Graphics builder</font></p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | prs 16 May 2016: Finding found&nbsp;fixed in Ov3.6.0_U7.&nbsp;Browse OPC window is closing properly at step7.&nbsp;Hence closing the finding. Thanks | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face=Calibri>1&gt;<span style="">&nbsp; </span></font><font face=Calibri size=3>Open or Insert New Graphics in GBNT .<br></font><font face=Calibri size=3> 2&gt; Click to open Browse OPC points window (from tool bar).<br> 3&gt; In Browse OPC points window, select OPC Server and click browse OPC to open OPC Item Browser window.<br> 4&gt; In OPC Item Browser Window double click on Net&gt;Unit&gt;Drop&gt;Point name in the hierarchy. <br> 5&gt; Point got selected in the Browse OPC window. Click again on “Browse OPC”.<br>6&gt; Blank OPC Item Id window open. Cancel it.<br> 7&gt; Close the Browse OPC Points Window. It does not close.<br> 8&gt; Click on Browse OPC again. Application Crashes. Displayed error message says “ Browse_pts MFC Application has stopped working.”</font></p> |  | U6 |  |  | FINDING | [6 empty] | 96861
36306 | FINDING | NONSECURE Parameters are not appearing in General tab of Logics Solver (1508) however Nonsecure parameters algorithms are being used in control sheet. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-27 07:00 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-27 07:00 | [7 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-04-27 06:58 |  | <p><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>NONSECURE Parameters are not appearing in&nbsp;General tab of Logics Solver (1508) however Nonsecure parameters algorithms are being used in control sheet.</font></span><font face="Times New Roman" size=3> </font></p><p><font face="Times New Roman" size=3> For reference please find attached Screen shot of &quot;Nonsecure_parameters_are_not_appeared.jpg&quot;.</font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | Ov3.6.0_U6,SIS Controller-OCR400G02,Ws12R2,Logic Solver (1508) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face="Times New Roman" size=3> </font><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">1. Created a new control sheet in Logic Solver02 (D27_SDS01_LS02)</span></p><p><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">2. </span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">Add NONSECURE PARAMETER algorithms into digital voter algorithm as inputs. Please find attached snapshot.</span></p><p><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">3. </span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">Loaded the Logic Solver &amp; SIS controller successfully.</span></p><p><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">4. </span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">Right clicked &amp; opened the Logic Solver02 (D27_SDS01_LS02)</span></p><p><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">5. </span><span lang=EN-US style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">Go to General Tab &amp; found the Nonsecure Parameters are not appeared.</span></p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 95787
36307 | FINDING | Insert new option may be removed from studio ovationsecurity and licenses features | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:24 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:24 | 67635 |  |  | 2016-05-13 04:24 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-27 08:16 |  | User cannot insert anything new on ovation security and licenses so right click insert new option&nbsp;may be removed from ovationsecurity and licenses. |  |  |  | The affected areas is in the definition of the operations applicable for the Ovation Security Manager and Licensing objects (in the lower panel of the Ovation Developer Studio) and their associated folders (in the hierarchy portion of the Ovation Developer Studio -- the locations shown in the original submitted attachments). | 0 |  |  |  | LB 05/13/16-Verified on Ovation3.6.0_U7 and observed that Insert new option&nbsp;is removed from studio for ovation security and licenses features. Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U7 |  | Ovation3.6.0_U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | Since these two items/objects are created implicitly when an Ovation System object is created, the context menu for these items will be changed to remove the &quot;Insert New&quot; option.&nbsp; In addition, the &quot;Delete&quot; operation will also be removed from the Ovation Security Manager object. | 6 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1)Open the developers studio</p><p>2)Go to systems&gt; licenses or Ovation security right click on it to view insert new option.</p><p>3)Now select insert new a new window will appear.</p><p>4)Click ok nothing will add. So this can be removed</p><p>Screenshot is also attached for your reference.</p> |  | U6 |  |  | FINDING | [6 empty] | 96770
36315 | FINDING | "3.6.0_RSR_SVTP_rev1.1_TK.docx" needs to be updated. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-27 14:54 | [11 empty] | USPITTFSService | 2016-04-27 14:54 | [7 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-04-27 14:54 |  | <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">1) The SVTP was prepared in reference to REF 1500. REF 1500 referred to G01, G02 and G03 Servo Drive modules which are now obsolete.</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Con_047 is the new user guide for Servo Drive Module for G04, G05 and G06 modules.</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">The SVTP needs to be updated to refer the same. </font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">2) Test Case 5.3 refers to “Invalid Test Case” scenarios.</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.2 (a), (b) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.3 (b), (c) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.4 (b), (c) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.5 (b), (c) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.6 (b), (c) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">Test Case 5.3.7 (b), (c) &gt; Invalid Test Case</font></span></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">&nbsp;</font></span></p><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font color="#000000">3) Test Case 5.7.2: Time Out Value for the Servo Driver Module refers to Latch and Reset options. However there is no such option available for Servo Drive Modules. The test case needs to be updated accordingly</font></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0</p> |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 95836
36318 | FINDING | Warning message may display if user enters the value above or below the ranges and the field may not accept values on password polices | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-06-20 09:04 | [11 empty] | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | 2016-06-20 09:04 |  |  |  | 2016-06-20 09:04 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-28 00:22 |  | Password polices like Maximum Password Age, Minimum Password Age, Minimum password length, Enforced password history are accepting values above or below their ranges. for e.g range of minimum length for user passwords is an integer value&nbsp;between 0 and 14 but user is able to enter the values above or below ranges,negative numbers, special characters etc. When user enters the value above or below the range a warning message should display and field will not accept these values. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1)Launch the developers studio.</p><p>2)Open the Ovation security manager.</p><p>3)Go to&nbsp;&nbsp;manage&nbsp;domain policies&gt;Default domain policies&gt;password policies select minimum password length and try to enter the values above or below ranges, negative numbers, special characters etc</p><p>Screenshot is also attached for your reference</p> |  | U6 |  |  | FINDING | [6 empty] | 98818
36319 | FINDING | CSLS Node point changes state and reverts back to original state when Controller fail over is done after removing network cable from one IOP | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-17 05:49 | [11 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-17 05:49 | u7 | [6 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-28 00:31 |  | <div>CSLS Node point changes state and reverts back to original state when Controller &nbsp;fail over is done after removing network cable from one IOP.</div><div>After removing network cable from one IOP from CSLS base when Controller fail over is done in this state, CSLS changes its state (Node point) and later goes back to old state.</div><div><i>For example (In Logs):&nbsp;</i></div><div><i>Initial&nbsp;state:&nbsp;</i></div><div><i>Registered, Configured, commissioned and&nbsp;</i><i>maintenance alert bits were high.</i><i>&nbsp;Primary in Control was low.</i></div><div><i>During fail over:&nbsp;</i><i>Primary in control bit becomes high. Registered, Configured, Commissioned and maintenance alert bits become low.&nbsp;</i><i>Later registered bit becomes high and primary in control becomes low.&nbsp;</i><i>In next state commissioned and configured bits become high.&nbsp;</i></div><div><i>At last maintenance alert bit also becomes high(Old state).</i></div><div><br></div><div>There should not be any change in the Node point of CSLS during controller fail over.</div><div>Please refer to the attached historical review logs (At 04/27/2016 18:06:10 Network cable was removed from Primary IOP. At 04/27/2016 18:06:46 Failover was performed )&nbsp;</div> |  |  |  |  | 0 |  |  |  | Still CSLS Node changes state and reverts back to original state when controller fail over is done after removing network cable from one IOP.<div>Please refer to attached historical review logs (<i>SHS_Finding 36319 retest.txt</i>)</div><div>At 05/17/2016 15:48:22 network cable was removed from 1 IOP of CSLS 5<br></div><div>At 05/17/2016 15:48:55 controller fail over was done<br></div> | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation | u7 |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | redundancy was improved in u7<br> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Remove one IOP network cable of CSLS<br></li><li>Perform Controller fail over (Switch off active controller).<br></li><li>Monitor the Node of CSLS.<br></li></ol> |  | u6 |  |  | FINDING | [6 empty] | 97047
36320 | FINDING | Performing the Controller load after CSLS load without any changes changes the Modified sequence of the controller | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-29 12:28 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-04-29 12:28 |  |  |  | 2016-04-29 12:28 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-28 00:31 |  | <div>Performing the Controller load after CSLS load without any changes to CSLS or controller, changes the Modified sequence number of the controller.</div><div>If the controller is loaded without any changes then Modified sequence is not changed.</div><div><br></div><div>The behaviour of loading the CSLS and controller without any change should be same as loading the controller without any change.&nbsp;</div><div>Please refer to attached screenshots</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <div><ol><li>Load a CSLS without any change and also perform the controller load.<br></li><li>Modified sequence of controller changes.<br></li><li>Load a controller without any change and modified sequence of CSLS is not changed<br></li></ol></div> |  | u6 |  |  | FINDING | [6 empty] | 95970
36321 | FINDING | Dump CRC file that opens automatically after creating dump CRC of CSLS is blank | Daly, Joshua D EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Daly, Joshua D EMR SYSS PWS PITT | 2019-08-28 05:58 | [11 empty] | Daly, Joshua D EMR SYSS PWS PITT | 2019-08-28 05:58 |  |  |  | 2019-08-28 05:58 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-04-28 00:38 |  | Create a Dump CRC file, give location of that file from Developer Studio. The dump CRC file that opens automatically after creating dump CRC of CSLS &nbsp;is blank .<div>When the same file is opened manually from location it opens properly with all data.<br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | Unable to reproduce. The file showing blank when it opens automatically is due to a load issue in internet explorer that happens occasionally. The correct workout is manually opening the file.<br> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Create a dump CRC of a CSLS by right clicking the CSLS.</li><li>Provide location for Dump CRC.</li><li>Dump CRC that opens automatically is empty.</li><li>Open Dump CRC from the location where it is stored. It opens properly.</li></ol> |  | U6 |  |  | FINDING | [6 empty] | 145777
36322 | FINDING | Help file is not available on ovation license manager window. | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Swartz, Mark EMR SYSS PWS PITT | 2016-04-28 07:39 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-04-28 07:39 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-04-28 01:36 |  | Help file is not available on ovation license manager window. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U6 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the developers studio.</p><p>2)Under systems,select licenses and&nbsp;open licensing, this will open the license manager window</p><p>3)On license manager window go to help tab and select view help. Help file will not open.</p> |  | U6 |  |  | FINDING | [6 empty] | 95877
36323 | FINDING | ‘Config tab field descriptions’ topic displays incomplete information in online help. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jha, Rahul AUTOSOL PWS NOIDA | 2016-05-23 07:51 | [11 empty] | Jha, Rahul AUTOSOL PWS NOIDA | 2016-05-23 07:51 | 3.6.0_U9 |  |  | 2016-05-23 07:51 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-04-28 04:23 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>In online help OvPtStudio360, the ‘Config tab field descriptions’ topic does not display information about config tab fields that apply to the applicable point type(s). </font></p><font face="Times New Roman" size=3> </font><span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Snapshot is attached for reference.</span> |  |  |  | <p>MG (April 29, 2016):&nbsp;Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p><p><span style="line-height:normal;color:rgb(34, 34, 34);">MG (May 20, 2016):</span><span style="line-height:normal;box-sizing:border-box;color:rgb(34, 34, 34);">Check the OvptStudio help in the Ovation 3.6.0 U9 build.</span><br></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Documentation | <p>MG (April 29, 2016):&nbsp;Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p><p><span style="line-height:normal;color:rgb(34, 34, 34);">MG (May 20, 2016):</span><span style="line-height:normal;box-sizing:border-box;color:rgb(34, 34, 34);">Check the OvptStudio help in the Ovation 3.6.0 U9 build.</span><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | Ovation3.6.0_U6 online help. |  | Ovation for Windows | Ovation | Engineering Tools/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 29, 2016): This finding has been fixed and&nbsp;is available in U8 build.</p><p>-------</p><p>RJ- 05/23/16: Verified the issue in Ovation.3.6.0_U9 build. Issue found to be fixed. Hence, closed the finding.</p><p><br></p><p><br></p> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Access the online help OvPtstudio360.</p><p>2. Click on the index and type '<font face=Calibri>Config tab field descriptions’ and access the associated help.</font></p><p><font face=Calibri><br></font></p> |  | U6 |  |  | FINDING | [6 empty] | 97481
36325 | FINDING | Newly added drops are not reflecting in System viewer application. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-05-26 23:05 | [11 empty] | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-05-26 23:05 | 67391 |  |  | 2016-05-26 23:05 |  |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | 2016-04-28 05:59 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>On Ovation3.6 setup updated with U6 build, added two Controller drops but not able to check them in System viewer application as these drops are not reflecting in System Viewer. </font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>On further investigation it is found that files or information related to these drops should be copied from “C:\OvPtSvr\Ovation\mmi\SystemViewer” to “$WDPF_HOME\mmi\SystemViewer” but it is not happening.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Also tried by performing download and clear/load operations on DB server but found no improvements were observed.</font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3 face=Calibri>Just for more information, able to get the status of drop in PI and Diagnostics applications.</font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 35 | FINDING |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Kant, Krishna EMR SYSS PWS NOIDA | Gupta, Ankit EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  |  |  | Implementation | 3.6.0_U7 |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">Ovation </span><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">3.6.0_U6</span> |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jindal, Deepak EMR SYSS PWS NOIDA | Software Quality |  | [DJ-27/5/2016]: Checked on Ovation3.6.0 U9 build and found that able to see newly added drop in system viewer. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font face=Calibri>Following steps were performed:</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3 face=Calibri>1)</font><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font size=3><font face=Calibri>Update Ovation3.6 setup with U6 build.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3 face=Calibri>2)</font><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font size=3><font face=Calibri>Create any Controller drop in existing database.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3 face=Calibri>3)</font><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font size=3><font face=Calibri>Perform download, clear and load operation for the drop.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3 face=Calibri>4)</font><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font size=3><font face=Calibri>Perform download, clear and load operation for the DBServer or station drop where one wants to check the System viewer application.</font></font></p> <p class=MsoListParagraph style="MARGIN:0in 0in 0pt 0.5in;TEXT-INDENT:-0.25in;"><font size=3 face=Calibri>5)</font><span style="FONT-SIZE:7pt;FONT-FAMILY:&quot;Times New Roman&quot;,&quot;serif&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span><font size=3 face=Calibri>Open System viewer and check for the newly added drop.</font></p> | EPM Product Development | U6 |  |  | FINDING | [6 empty] | 97883
36329 | FINDING | Virtual SDS machine to support Windows 2012 R2 | Maggu, Mukesh EMR SYSS PWS NOIDA | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:39 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:39 | U7 | [6 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-04-28 08:59 |  | Windows 2012 R2 should be added to supported operating systems for VSDS software in manual OW360_48<br> |  |  |  | MM 04/10/17: Windows 2012 R2 is added to supported operating systems for VSDS software in manual OW360_48 | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Documentation | MM 04/10/17: Windows 2012 R2 is added to supported operating systems for VSDS software in manual OW360_48 |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | U7 |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Documentation | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Raciborski, Mikolaj AUTOSOL PSS WRSW | Development |  | <p><br></p> | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U6 |  |  | FINDING | [6 empty] | 111015
36332 | FINDING | Saving a snaphsot on a hardware simcontroller is taking excessively long. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-04-28 15:26 | [11 empty] | USPITTFSService | 2016-04-28 15:26 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-04-28 15:26 |  | <p>Sending a save command to a hardware simcontroller is taking an excessively long time. On an 1100 controller in the validation lab, it is taking about 30 seconds. </p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Bush, Kirt T EMR SYSS PWS PITT | Shiferaw, Tedla AUTOSOL PWS PITT | [8 empty] | Implementation |  |  | Ovation 3.6.0 U6 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Send a simulator save command to an Ovation SimController (hardware controller).&nbsp; To see the length of time it takes, you will have to watch the file size increasing&nbsp;within the controller&nbsp; (use the 'll' command in /ata0/wdpf/dpu/sim directory).&nbsp; or use coord_tools within the controller to do the save and check the time until it returns. </p> |  | U6 |  |  | FINDING | [6 empty] | 95912
36336 | FINDING | Ladder Monitoring observation for ADD lago- Discrepancy between help document and online functionality of Ladder-ADD algo, If algo use Point or Register Data type. | Bush, Kirt T EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2016-04-29 09:52 | [11 empty] | USPITTFSService | 2016-04-29 09:52 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-04-29 04:11 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font size=3><font face=Calibri>Discrepancy between help document and online functionality of Ladder-ADD algo, If algo use Point or Register Data type.<span style="">&nbsp; </span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>Function of ADD algo {Result=REG1+RE2};</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><i style=""><font face=Calibri size=3>Help Document says:</font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><i style=""><font face=Calibri size=3>REG 1: This operand is one of the addends of the addition. It is a binary number held in a single register with a range of -32,767 to +32,767. </font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><i style=""><font face=Calibri size=3>REG 2: This operand is the other addend of the addition. It is a binary number held in a single register with a range of -32,767 to +32,767.</font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>REG1, REG2 and Result support three Data Type.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>1. Register Type 2. Point Type 3. Constant Type.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Following are the three scenarios with conditions in which discrepancy observed between online functionality and help document. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri><b style=""><u><font size=3>Scenario-I</font></u></b><font size=3>: If Data Type is </font><b style=""><font size=3>Ovation</font></b><font size=3> </font><b style=""><font size=3>Point</font></b><font size=3>.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri><font size=3><span style="color:rgb(31, 73, 125);"><span style="">&nbsp;</span></span><b>REG1: Ovation Point</b></font><font size=3>; </font><b><font size=3>REG2: Ovation Point</font></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>Note: If Point Values within range -32767 and +32767 then ADD algo Works fine.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Following are the three conditions in which discrepancy observed between online functionality and help document. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><font size=3>Condition-I</font></b><font size=3>: </font><b><font size=3>If Point values of REG1 or REG2 less than is -32767</font></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using Internal Algorithm calculation.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Point values of REG1 is less than -32767 then</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{65536+ (REG1)} +REG2= Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Point values of REG2 is less than -32767 then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>REG1 + {65536+ (REG2)} = Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>&nbsp;</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style=""><font face=Calibri size=3>For reference screenshot “Point less than -32767.jpg”is attached. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style=""><font face=Calibri size=3>Following are detail of screenshot: </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Ovation Point (AG_xx_ADD8) configured for Input1; Value= -35000</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Ovation point (AG_xx_ADD7) configured for Input2; Value= 25</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><font size=3>Ovation point (AG_xx_ADD6) configured for Result: Result=</font></b><font size=3> {(65536+ (-35000)) + 25} =30561</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>&nbsp;</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Condition-II: If Point values of REG1 or REG2 greater than is +32767 </font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using Internal Algorithm calculation</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Point values of REG1 greater than&nbsp;+32767</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{(REG1-65536)} +REG2= Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Point values of REG2 is greater than +32767&nbsp;then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>REG1+ {(REG2-65536)} = Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style=""><font face=Calibri size=3>For reference screenshot “Point greater than 32767.jpg” is attached. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style=""><font face=Calibri size=3>Following are detail of screenshot:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Ovation Point (AG_xx_ADD8) configured for Input1; Value =40000</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Ovation point (AG_xx_ADD7) configured for Input2; Value=25</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Ovation point (AG_xx_ADD6) configured for Result; Result= [(40000-65536)+25]= -25511</font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>*******************************************************************************</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><b style=""><u><font size=3>Scenario-II</font></u></b><font size=3>: If Data Type is </font><b style=""><font size=3>Register</font></b><font size=3>.</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><font size=3>If <b>REG1: Regis</b><span style="">te<b>r Type</b></span></font><font size=3>; </font><b><font size=3>REG2: Register Type</font></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>Note: If Register Values within range: 0 &lt;Register Value&lt;32767 ADD algo Works fine.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;-ms-text-autospace:;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Following are the three conditions in which discrepancy observed between online functionality and help document. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><u><font size=3>Condition-I</font></u><font size=3>:&nbsp; If Value of REG1 or REG2 greater than +32767</font></b><font size=3> </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Signal diagram display value as entered. e.g. REG1 value is +38000, signal diagram will show the 38000.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using Internal Algorithm calculation:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If REG1 is greater than +32767 then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{(REG1)-65536} +REG2=Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If REG2 is greater than 32767 then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>REG1 + {(REG2)-65536} =Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><b><u><span style="text-decoration:none;"><font face=Calibri size=3>&nbsp;</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><u><font size=3>Condition-II</font></u><font size=3>:</font><u><font size=3> </font></u><font size=3>If Value of REG1 or REG2 less than -32767</font></b><font size=3> </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Signal diagram display REG1 value after internal calculation.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Internal Calculation: REG1= {REG1 +65536}</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><span style=""><font size=3>&nbsp;</font></span><font size=3>e.g. </font><span style=""><font size=3>&nbsp;</font></span><font size=3>REG1 value is -38000, signal diagram show {-38000+65536] = +27536</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using Internal Algorithm calculation:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If REG1 is less than -32767 then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{(REG1) + 65536} +REG2=Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If REG2 is less than -32767 then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>REG1 + {(REG2) + 65536} =Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><b><font face=Calibri><u><font size=3>Condition-III</font></u><font size=3>: If Value of REG1 in range:&nbsp; 0 &gt;REG1&gt; -32767 </font></font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Signal diagram display value show after internal calculation {REGX value +65536}</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>e.g. REG1 value= -10000, signal diagram show {-10000+65536] = +55536</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using standard calculation.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>If REG1 is in range<b> 0 &gt;REG1&gt; -32767</b></font><font size=3> then </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{REG1+REG2}= Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>If REG2 is in range <b>0 &gt;REG1&gt; -32767</b></font><font size=3> then </font></font></p><font face="Times New Roman" size=3> </font><div style="border-width:medium medium 3pt;border-style:none none dotted;border-color:currentColor currentColor windowtext;padding:0in 0in 1pt;"><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;padding:0in;border:currentColor;"><font face=Calibri size=3>{REG1+REG2}=Result</font></p><font face="Times New Roman" size=3> </font></div><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><u><span style="text-decoration:none;"><font face=Calibri size=3>&nbsp;</font></span></u></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b style=""><u><font size=3>Scenario-III</font></u><font size=3>:</font></b><font size=3> If Data Type is </font><b style=""><font size=3>Constant</font></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><font face=Calibri size=3>Condition-I: If Point values of REG1 or REG2 greater than is +32767 </font></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Result calculated using Internal Algorithm calculation</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Constant values of REG1 greater than&nbsp;+32767</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>{(REG1-65536)} +REG2= Result</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Constant values of REG2 is greater than +32767&nbsp;then </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>REG1+ {(REG2-65536)} = Result</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  | 3.6.0+Control Bulider + Ladder |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Create Ladder control sheet using ADD algo.</p><p>Use three type of data type for Input1, Input2 and&nbsp;Result.</p><p>Load the sheet. &nbsp;&nbsp;</p><p>&nbsp;</p><p><br></p> |  | U6 |  |  | FINDING | [6 empty] | 95959
36342 | FINDING | Smart Process logo is missing at the Smart Process Optimizer page. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-04-29 14:33 | [11 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-04-29 14:33 | [7 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-04-29 14:31 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri><font size=3>It has been observed that ‘Smart Process’ <b style="">logo</b></font><font size=3> is not available either at the top-left corner of Smart Process Optimizer home page or other pages. </font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Please refer attached snapshot for reference.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>The issue is seen on WS12_R2_64bit and WS08_R2_64bit machines with IE version 11.0. However, the logo is available on W7_SP1_64Bit.</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face="Times New Roman" size=3> </font><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Open Smart Process Optimizer from start menu.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Enter the log in credentials.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Smart Process Optimizer home page will appear.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:10pt;">Smart Process <b style="">logo</b> will not be available at the Smart Process Optimizer home page.</p></li></ol><font face="Times New Roman" size=3> </font> |  | u6 |  |  | FINDING | [6 empty] | 95982
36345 | FINDING | Ov3.6.0_U6 Alarm Sequence number (AZ field) in Alarm tab of Point Information Window keeps updating itself when individual alarm limits are cutout. | Cooper, David External Self Employed | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Cooper, David External Self Employed | 2019-03-20 06:30 | [11 empty] | Cooper, David External Self Employed | 2019-03-20 06:30 | [7 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2016-04-30 04:21 |  | <p>Ov3.6.0_U6 Alarm Sequence number (AZ field) in Alarm tab of Point Information Window keeps updating itself when individual alarm limits are cutout with packed point.</p><p>This behaviour is same for all alarm limits of an analog point.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Cooper, David External Self Employed | Prasad, Parmatma EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6 FP4 |  | <p>Ov3.6.0 + Windows server 2012 R2</p><p>Ov3.6.0 + Windows7</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  |  | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Create an analog point and define alarm limits in the limit tab in the point record of developer studio.</p><p>2. Define a packed point at &quot;Alarm cutout name&quot; field and check &quot;Treat packed alarm cutout as a bit mask&quot; field.</p><p>3. Save and load controller where the point is created.</p><p>4. Open point in&nbsp;Point Information window.</p><p>5.&nbsp;Take the point into alarm of a particular limit say HIGH3.</p><p>6. Open packed point in Point Information Window and&nbsp;cutout analog point with A2 bit&nbsp;2 of packed point.</p><p>7. Verify that the analog point is cutout from alarm in the Point Information Window.</p><p>8. Verify the &quot;Cutout Status&quot; field in alarm tab of Point Information.</p><p>9. Observe the Alarm Sequence Number (AZ) field is updating continuously in every 3 seconds (Please refer to snapshot 1.jpg).</p><p>10. Also &quot;Time of First Alarm (sec) (U4) &quot; and &quot;Time of Last Event (sec) U6&quot; is also changing in every 3 seconds.</p><p><br></p><p>SS:04/30&gt; All the points are created in controller and observation is same for fast as well as slow points.</p> |  | U6 |  |  | FINDING | [6 empty] | 139727
36346 | FINDING | Synchronize Online option does not synchronize any control sheets to Signal Diagram | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-05 10:02 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2016-05-05 10:02 | 67738 |  |  | 2016-05-05 10:02 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-30 06:45 |  | Synchronize Online option does not synchronize any control sheets to Signal Diagram<br>If a new control sheet is created and without loading controller this sheet is synchronized through Tools-Synchronize Online option in Control Builder, the sheet does not appear in Open Document list of Signal Diagram (even after regenerating title cache).<br>Similarly after making changes to a control sheet which is already loaded into the controller, if the control sheet is synchronized, the changes does not reflect in Signal Diagram |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Agarwal, Gaurav EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  | Implementation |  |  | Ovation 3.6.0_U4<br>Net#36 DBS Drop100 (Windows Server 2012) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | No Action Required | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Duplicate of 36275 | EPM Validation | U6 |  |  | FINDING | [6 empty] | 96337
36347 | FINDING | Publish and Edit options are not working for Supplemental Documents | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-02 22:57 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-02 22:57 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-30 06:45 |  | <p>Publish and Edit options are not working for Supplemental Documents.</p> <p><br>For Publish option, no window comes up to ask for the path of .pdf file (to be saved) for selected Supplemental Documents to be published.<br>For Edit option, in Edit Supplemental Document window if a control sheet is selected and click OK, then nothing happens (it is expected that selected control sheet will open up for editing.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Agarwal, Gaurav EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  | Implementation |  |  | Ovation 3.6.0_U6<br>Net#36 DBS Drop100 (Windows Server 2012) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | In Validation | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U6 |  |  | FINDING | [6 empty] | 96098
36348 | FINDING | Supplemental Documents does not open in Signal Diagram | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Daly, Joshua D EMR SYSS PWS PITT | 2016-05-17 08:17 | [11 empty] | Daly, Joshua D EMR SYSS PWS PITT | 2016-05-17 08:17 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-04-30 06:46 |  | <p>Supplemental documents (documents opened through hyperlink in Control Builder) do not open in Signal Diagram.</p> <p><br>The supplemental documents (for Link Type = Supplemetal Documentation) are saved by defualt to offline path whereas Signal diagram tries to open them through online path and no such sheet is found in online path. Please refer to attached snapshot for offline and online paths as observed in Control Builder and Signal Diagram respectively.<br>If Link Type is set to Component Code Reference, linked control sheets are correctly opened.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Agarwal, Gaurav EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  | Implementation |  |  | Ovation 3.6.0_U6<br>Net#36 DBS Drop100 (Windows Server 2012) |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | In Validation | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | U6 |  |  | FINDING | [6 empty] | 97066
36349 | FINDING | In GBNT, Desired help file is not opening in ‘default colors’ and ‘alarm color setup’ tab of HPCR Analog Indicator. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Casteel, Linda EMR SYSS PWS PITT | 2016-05-03 09:34 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-05-03 09:34 |  |  |  | 2016-05-03 09:34 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-05-01 02:09 |  | <span style="line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">In GBNT, Desired help file is not opening in ‘default colors’ and ‘alarm color setup’ tab of HPCR Analog Indicator.</span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Documentation | <p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Ov 3.6.0_U6</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Documentation | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | LC 05/03/2016: Help for the HPAI colors tab uses the same help as the regular analog indicator.&nbsp; You can only assign one help ID to a single topic. Therefore, the help IDs for default colors and alarm color setup are defined for the regular Analog Indicator. There are no plans to fix this. | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>1:- In GBNT, HPCR Analog Indicator are configured.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>2:- Open the Properties window of HPCR Analog Indicator and go to ‘default colors’ tab.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>3:- Press Help button.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style=""><font face=Calibri size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;</font></span><font size=3>‘Default color’ tab of Analog indicator help is opening in place of ‘default color’ tab of HPCR analog indicator help. See screen shots”Incorrect Help is open of HPCR indicator.jpg”</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Note:- Same issue is also observed with ‘alarm color setup’ tab of HPCR analog indicator help.</font></p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 96173
36352 | FINDING | SVTP “3.6.0_SRF2048_SVTP_rev1.13_XX.doc need to be modified as per description. | Joshi, Parmesh EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:18 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2018-12-15 04:18 |  |  |  | 2018-12-15 04:18 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-02 03:31 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">1. UD (Nanosecond) in test cases 5.1.2, 5.1.4, 5.1.5 &amp; 5.2.0 (a &amp; b) and UF (Nanosecond) in test cases 5.3.4 &amp; 5.3.6 should be removed from SVTP “3.6.0_SRF2048_SVTP_rev1.13_XX.doc.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Since these fields are not available in alarm tab of point information window.</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">2. Shelve option in test case 5.2.4 should be removed from SVTP “3.6.0_SRF2048_SVTP_rev1.13_XX.doc.</span></p><font face="Times New Roman" size=3></font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Since this option is not available in alarm tab of point record in developer studio.</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">3. “Shelve status field” should be replace with “Alarm Shelve” in test case 5.2.13 (a, b, c, d, e, f, g, h, &amp; I).</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">4. &nbsp;For <span><font face=Calibri><font size=3>Alarm Shelve shift Configuration, we need to &quot;download &amp; rebooted&quot; the concern drops so in test case 5.2.14(f, g &amp; h) need to be added Reboot)<span>&nbsp; </span></font><font size=3>after download. </font></font></span></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"> <br></p></span><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face="Times New Roman" size=3><br></font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span><font face=Calibri size=3>&nbsp;</font></span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  | <p>PP-12/15/2018: Verified in Attached TR of &nbsp;&quot;SRF2048_SVTP_rev1.14.doc&quot; &amp; found the issue is fixed.</p><p>Hence, it is closed validation.</p> | 0 |  | Ovation for Windows/Operator Station/Alarms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Augustine, Lisa EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | Ov3.6.0-U6,Ws12R2,Ws0764B,Ws08R2 |  | Ovation for Windows | Ovation | Operator Station/Alarms | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | PJ 12/11/2018&gt; Attached Rev 1.14 addresses the issue. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 135731
36353 | FINDING | Online Help is not available for "Device mode" in online help of “Plant Mode tab field descriptions” for deluxe point. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-24 06:04 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-24 06:04 | 3.6.0_U8 |  |  | 2016-05-24 06:04 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-02 03:31 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face=Calibri><span><font size=3>Online Help is not available for &quot;Device mode&quot; in online help of “</font></span><font size=3>Plant Mode tab field descriptions” for deluxe point.&nbsp;&nbsp;</font></font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face=Calibri><font size=3>Note: The device mode option is&nbsp;available under plant mode tab of point record of deluxe point in developer studio.</font></font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><font face=Calibri size=3><span style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><font color="#000000" face="Segoe UI">PP:05/24/2016-Verified in Ov3.6.0_U9 &amp; found the online help is available for device mode</font></span></font></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>MG (May 2, 2016): According to this finding,&nbsp;Added the&nbsp;field Device Mode Point and its description in the tables in&nbsp;the&nbsp;<strong>Section&nbsp;8.7.11 Plant Mode tab field description</strong>&nbsp;of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in&nbsp;U8 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> | 0 |  |  |  |  | 0 |  |  | <p>MG (May 2, 2016): According to this finding,&nbsp;Added the&nbsp;field Device Mode Point and its description in the tables in&nbsp;the&nbsp;<strong>Section&nbsp;8.7.11 Plant Mode tab field description</strong>&nbsp;of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in&nbsp;U8 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jain, Swati EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0 |  | Ov3.6.0-U6,Ws12R2,Ws0764B,Ws08R2 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | <span style="line-height:18px;">MG (May 2, 2016): This finding has been fixed and will be available in U8 build.</span> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face="Times New Roman" size=3> </font>1. Opened developer studio.</p><p>2. Opened created deluxe point.</p><p>3. Clicked on help tab.</p><p>4. Go to plant mode tab.</p><p>5.&nbsp;But the help for device mode is not available.</p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 97586
36354 | FINDING | Under the Default tab in Developer's studio no data is available | Swartz, Mark EMR SYSS PWS PITT | More Information Required | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Swartz, Mark EMR SYSS PWS PITT | 2016-05-02 15:26 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-05-02 15:26 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-02 05:11 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:rgb(0, 112, 192);"><font face=Calibri size=3>In GEC Ovation 3.6.0 has two network, Net#26 &amp; Net#36.&nbsp;</font></span><span style="color:rgb(0, 112, 192);"><font face=Calibri size=3>In Net#36&nbsp;It observed that under the Defaults tab in Developer’s studio&nbsp;NO data</font></span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">(e.g Default Analog points, Default Deluxe points &nbsp;etc &nbsp;&nbsp;) is available (please refer attached screen shot).</span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Database have been imported &amp; observed that Default data are available in it.</span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">E-mail correspondence with Mark Swatz has been&nbsp;done (please refer the attached e-mail)&nbsp;</span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">However in Net#26 default data are seen correctly.</span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="color:rgb(0, 112, 192);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p> |  |  |  |  | 0 |  |  |  | As stated in the attached email, it is unclear how this situation occurred.&nbsp; We have been unable to duplicate the situation in Pittsburgh.&nbsp; Until more information becomes available (e.g., definitive actions/steps which produced this situation), then this may have to be considered an anomaly. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p><font color="#0070c0" face=Calibri size=3>Ovation 3.6.0 (Net#36)</font></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Need More Information to Duplicate | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font color="#0070c0" face=Calibri size=3>l. Open the Developer's studio from any EWS or DBS</font></p><p><font color="#0070c0" face=Calibri size=3>2. Go to Default tab</font></p> |  | U6 |  |  | FINDING | [6 empty] | 96092
36358 | FINDING | Product Marketing provide Module Process Variable to be used instead of SMV/RDP in the GUIs | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-05-26 00:30 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-05-26 00:30 | 67635 |  |  | 2016-05-26 00:30 |  |  |  | Costlow, Kim EMR SYSS PWS PITT | 2016-05-02 10:41 |  | Replace SMV and RDP with Module Process Variable in the GUIs and user documentation. |  |  |  | <p>The affected area in the Ovation Developer Studio is in the definition of the labels on the Hardware tab of&nbsp;an analog point assigned to an MHM (or DGC) module and in the labels shown&nbsp;when Engineering an MHM module.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | Casteel, Linda EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [6 empty] | Implementation | 3.6.0_U7 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Costlow, Kim EMR SYSS PWS PITT | Development |  | <p>The Labels when editing/viewing Analog Points assigned to the MHM module in the Ovation Developer Studio will be changed as follows (on the Hardware tab):</p><p>The box formerly labeled &quot;RDP&quot; will be named &quot;Module Process Variable&quot;.</p><p>The attribute label which previously read &quot;RDP Tag&quot; will be renamed &quot;Module Process Variable Tag&quot;.</p><p>The attribute label which previously read &quot;RDP Deadband&quot; will be renamed &quot;Module Process Variable Deadband&quot;.</p><p><br></p><p>The labels in the Ovation Developer Studio UI when Engineering an MHM module will also be changed.</p><p><br></p><p>These modifications will also be back-fit into an Ovation 3.5.1 engineering patch (OVA351066). </p><p><br></p><p><br></p><p>SDK: The attribute label&nbsp;has renamed to &quot;Module Process Variable Tag&quot; and &quot;Module Process Variable Deadband&quot;.</p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 97772
36367 | FINDING | Plant Mode & Device Mode functionality are not working. | Cooper, David External Self Employed | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-09 01:25 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-09 01:25 |  |  |  | 2016-05-09 01:25 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-03 03:27 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Plant Mode &amp; Device Mode functionality are not working, w</font></span><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>hen&nbsp;change the value of analog point (Plant mode point-D155_PLANT_MODE_LA) from 0 to 4 but the deluxe point mode not changed &amp; it takes limit of Plant mode 1 only. </font></span><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri><span><font size=3>&nbsp;</font></span><font size=3>Please find attached snapshot of “Plant_Device_mode.jpg”.</font></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Note: The above same observation also observed for Device mode type.</font></span></p><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);">PS: The above functionality was working fine in Ov3.6.0_U4.</span></p><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);">PP:05/09/2016-Again we have verified the Plant Mode &amp; Device Mode in&nbsp;Ov3.6.0_U7&nbsp; for Operation station (EWS) points &amp; found both Device &amp; Plant Mode working fine.</span></p><p style="margin:0cm 0cm 10pt;"><span style="color:rgb(31, 73, 125);">Hence, I am closed the finding.</span></p><p style="margin:0cm 0cm 10pt;"><font color="#000000" face="Times New Roman"> <br></font></p></font><p style="margin:0cm 0cm 10pt;"><br></p></span><p style="margin:0cm 0cm 10pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING |  | Sharma, Satish AUTOSOL PWS NOIDA |  |  | Capani, Innocenzo AUTOSOL PWS PITT | [5 empty] | Implementation |  |  | Ov3.6.0-U6,Ws12R2,Ws08R2,Ws07 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Investigate After Release | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | <p><br></p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">1. Created analog point_“D155_PLANT_MODE_LA” in drop155 (EWS) under UNIT0 for “Plant Mode” &amp; load the drop155.</span></p><p><span style="color:rgb(31, 73, 125);">2. </span><span style="color:rgb(31, 73, 125);">Inserted new plant mode window &amp; assigned above created point (D155_PLANT_MODE_LA) as Plant Mode Point.</span></p><p><span style="color:rgb(31, 73, 125);">3. Performed d</span><span style="color:rgb(31, 73, 125);">ownload &amp; Reboot operation&nbsp;of&nbsp;drop155.</span></p><p><span style="color:rgb(31, 73, 125);">4. </span><span style="color:rgb(31, 73, 125);">Now created deluxe point in Controller drop39/89 (OCR400G02)&nbsp;&amp; gave limits for Plant mode 1 &amp; plant mode 2 and rest modes are having default values. Please find attached snapshot “Plant_Device_mode.jpg”. </span></p><p><span style="color:rgb(31, 73, 125);">5. </span><span style="color:rgb(31, 73, 125);">Load the controller drop39/89.</span></p><p><span style="color:rgb(31, 73, 125);">6. </span><span style="color:rgb(31, 73, 125);">Now opened deluxe point in point information window &amp; go to Plant Mode tab.</span></p><p><span style="color:rgb(31, 73, 125);">7. C<font face=Calibri>hanged the value of analog point (Plant mode point-D155_PLANT_MODE_LA) from 0 to 4 but the deluxe point mode not changed &amp; it takes limit of Plant mode 1 only. </font></span></p><font face="Times New Roman" size=3> </font> |  | U6 |  |  | FINDING | [6 empty] | 96410
36374 | FINDING | Some of the test cases of TR "3.6.0_CONTROLLER_SVTP_rev5.6" needs modifications | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-04 01:54 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-04 01:54 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-03 06:50 |  | <p>Below test cases of TR &quot;3.6.0_CONTROLLER_SVTP_rev5.6&quot; needs modifications :-</p><p><br></p><p>1.&nbsp;Test case : 5.21.4(e) : &quot;<span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;"> Disconnect the <strong>N3</strong> cable, verify the controller reports link down/fault info to the Ovation Error log and reports a Drop fault&quot;</span></p><p><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:11pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span>&nbsp;Text N3 should be replaced with N2 as this test is related to N2.</p><p><br></p><p>2. Test case : 5.21.4 (m-q) : These tests are to monitor K0 and K1 field.&nbsp;</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;Since test case 5.21.4 is for N2 as single highway interface so test case 5.21.4(m-q) is N/A.</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;As test case 5.21.5 is for Dual highway test so test case 5.21.4(m-q) should be included in it.</p><p><br></p><p>3.&nbsp;Test&nbsp;case : 5.23.2(g-h) :&nbsp;Test case numbering 5.23.2(g-h) is repeated multiple times, it should be corrected accordingly.&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p><br></p><p>4. Sign off Page : In sign off page (Page no 123) under &quot;Test Procedure Section&quot;&nbsp;Test5.23 (Security and MISC) is not listed.&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | TR &quot;3.6.0_CONTROLLER_SVTP_rev5.6 |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the TR &quot;3.6.0_CONTROLLER_SVTP_rev5.6</p><p>2. Review the test case 5.21.4(e),5.21.4(m-q) and 5.21.5(b)</p><p>3. Also review the sign off page of TR for point 4 (mentioned in SDR)</p> |  | U6 |  |  | FINDING | [6 empty] | 96237
36380 | FINDING | Numalogic vxworks6.9 binaries are not built and deployed to the Controller projects | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2016-05-25 08:06 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-05-25 08:06 | 67660 |  |  | 2016-05-25 08:06 |  |  |  | Souders, Sarah EMR SYSS PWS PITT | 2016-05-03 13:13 |  | Presently, Numalogic vxworks6.5 binaries are checked into TFS as part of the controller prototype directory.&nbsp;We want to instead&nbsp;build vxworks6.9 binaries. |  |  |  | <p><br></p> | 0 |  |  |  | Attempting to attach session results.<br> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | [8 empty] | Implementation | U7 |  | Numalogic node |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Souders, Sarah EMR SYSS PWS PITT | Development |  | Build and deploy scripts are reconfigured to build Numalogic on VxWorks 6.9. The vx6.5 binary is removed from the controller&nbsp;prototype directory. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Connect to the Numalogic node's serial console and boot the node. Boot messages show VxWorks 6.5.</p> |  | U6 |  |  | FINDING | [6 empty] | 97721
36386 | FINDING | No help is available to support SDR35688 | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:57 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-20 03:57 | 3.6.0_U8 |  |  | 2016-05-20 03:57 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-04 00:56 |  | <p>It is observed that functionality details of SDR35688 (Top Ten 2014 - After doing a consistency check, add ability to delete a point) is not available in online help. </p><p>However functionality as per the SDR is working fine.</p> |  |  |  | <p>MG (May 13, 2016): According to this finding, updated the bullet point no. 6 and the screenshot (Figure 65: Consistency check Report window) in&nbsp;the&nbsp;<strong>Section 4.9.1 To run a consistency check</strong>&nbsp;of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in&nbsp;U8 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> | 0 |  |  |  | ST(05/20/2016): Checked the OvptStudio online help in the Ovation 3.6.0 U8 build. Online help is updated to support SDR35688, So closing this finding. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software | <p>MG (May 13, 2016): According to this finding, updated the bullet point no. 6 and the screenshot (Figure 65: Consistency check Report window) in&nbsp;the&nbsp;<strong>Section 4.9.1 To run a consistency check</strong>&nbsp;of the&nbsp;Developer Studio&nbsp;user guide for Ovation 3.6. This is available in&nbsp;U8 build.</p><p>The updated PDF file is&nbsp;placed at:&nbsp;<a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_60.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_60.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>GEC Lab,</p><p>DBS220</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <span style="line-height:18px;">MG (May 13, 2016): This finding has been fixed in the document and is available in U8 build.</span> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open Ovation developer studio application.</p><p>2. Perform consistency check operation to any drop.</p><p>3. Open online help from the consistency check result window.</p><p>4. Check that online help is not updated to support SDR35688.</p> |  | U6 |  |  | FINDING | [6 empty] | 97310
36389 | FINDING | Test case 5.8.6 and 5.8.7 of TR"3.6.0_STUDIO_SVTP_Rev3.7" should be modified | Benzvi, Mati EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-05-04 04:06 | [11 empty] | USPITTFSService | 2016-05-04 04:06 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-04 04:06 |  | <p>Below new features of&nbsp;security Rules are not&nbsp;included in test case 5.8.6 and 5.8.7 of TR&quot;3.6.0_STUDIO_SVTP_Rev3.7&quot; </p><p>1. Allow Modification of Ancillary Data</p><p>2. Allow Alarm shelve on-off</p><p>3. Allow highly managed alarm shelve on-off</p><p>These Rules needs to be added in TR</p><p>Please refer attached screen shot </p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Security/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the TR 3.6.0_STUDIO_SVTP_Rev3.7</p><p>2. Review the test case 5.8.6 and 5.8.7</p> |  | U6 |  |  | FINDING | [6 empty] | 96250
36400 | FINDING | Test Case – ‘5.1.32.9’ of TR ‘3.6.0_SRF1725_SVTP_rev1.2_XX.docx’ should be marked as ‘NA’ for multinet testing (3.6.0 & 3.3.1 MultiNet). | Benzvi, Mati EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2016-05-05 00:08 | [11 empty] | USPITTFSService | 2016-05-05 00:08 | [7 empty] | Jha, Rahul AUTOSOL PWS NOIDA | 2016-05-05 00:08 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>As per SRF1604 ‘Ovation Alarm Guidance Functional Specification’, the Alarm Guidance window can accommodate remote points if they are originated from a system that contains Alarm Guidance functionality.</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>As per Ovation 3.6.0 STP, test Case – ‘5.1.32.9’ of TR ‘3.6.0_SRF1725_SVTP_rev1.2_XX.docx’ should be tested with multinet </font><span style="line-height:115%;font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:9pt;-ms-layout-grid-mode:line;">3.6.0 &amp; 3.3.1. However, the </span><font face=Calibri size=3>Alarm Guidance functionality is not available in Ovation 3.3.1. So, the test case ‘5.1.32.9’ should be marked as ‘NA’.</font><font face="Times New Roman" size=3> </font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV-3.6.0 with OV-3.3.1 (for test case – ‘5.1.32.9’) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the SVTP '3.6.0_SRF1725_SVTP_rev1.2_XX.docx'. </p><p>2. Review the test case – ‘5.1.32.9’.</p> |  | U6 |  |  | FINDING | [6 empty] | 96305
36401 | FINDING | TR "3.6.0_SystemTests_SVTP_rev2.G" needs some modifications | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-05 04:40 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-05 04:40 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-05 04:06 |  | <p>Following test case of TR &quot;3.6.0_SystemTests_SVTP_rev2.G&quot; needs to be modified :-</p><p><br></p><p>1. Test case 5.3.13 : Adaptec and FDDI drivers are no longer use so these drivers should be remove from test case 5.3.13.</p><p><br></p><p>2. Test case 5.3.14 :&nbsp; It state to install &quot;Symantec Antivirus&quot; but since KAV antivirus is used instead of Symantec now a days</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; So test case 5.3.14 should be modified accordingly&nbsp;&nbsp;</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p><br></p> |  | Ovation for Windows | Ovation | Add-Ons | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the TR &quot;3.6.0_STUDIO_SVTP_Rev3.7&quot;</p><p>2. Verify the test case 5.3.13 and 5.3.14</p> |  | U6 |  |  | FINDING | [6 empty] | 96314
36402 | FINDING | 3.6.0_SRF2137_SVTP_rev1.1 needs some modification | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-05 05:27 | [11 empty] | USPITTFSService | 2016-05-05 05:27 | [7 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-05 05:27 |  | <p>In page no 29 of TR &quot;3.6.0_SRF2137_SVTP_rev1.1&quot; under Appendix A, test result of another test case is listed.</p><p>This test result does not have any significance of SRF 2137, Hence should be removed.&nbsp;&nbsp;&nbsp;&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the TR &quot;3.6.0_SRF2137_SVTP_rev1.1&quot;</p><p>2.&nbsp;Go to page 29 and review the page&nbsp;</p> |  | U6 |  |  | FINDING | [6 empty] | 96316
36404 | FINDING | Few image in OW 360 _40.pdf manual are to be replaced as to match the Ovation security manager window in OV 3.6.0 | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-23 03:12 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-23 03:12 | 3.6.0_U8 (pdf + help) |  |  | 2016-05-23 03:12 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-05 06:06 |  | Few image in OW 360 _40.pdf manual are to be replaced as to match the Ovation security manager window in OV 3.6.0 | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Updated the&nbsp;Managing Security&nbsp;3.6.0 manual with new screenshots, wherever applicable, as appropriate.</span> |  |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Refer to the&nbsp;Managing Security&nbsp;3.6.0 manual (Prelim 02)&nbsp;and check&nbsp;screenshots.</span> | 0 |  |  |  |  | 0 |  |  | <p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Updated the&nbsp;Managing Security&nbsp;3.6.0 manual with new screenshots, wherever applicable, as appropriate.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">This fix is available in both online help and pdf.</span></font></span></font></p><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For online help,&nbsp;refer to the&nbsp;Security Manager online help in the Ovation 360 U8 build.</span></font></span></font></p><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For pdf, refer to the <strong>Managing Security - Prelim 02</strong> manual, <strong>OW360_40_Prelim02.pdf</strong>, at the following path:</span></font></span></font></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(112, 48, 160);"><font face=Calibri size=3>V:\Tests\3.6.0\DOCS_for_Validation</font></span></p><p><font face="Times New Roman" size=3> <br></font></p></span><p>Documentation done.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>OV 3.6.0</p><p>OW 360_40.pdf</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Updated the&nbsp;Managing Security&nbsp;3.6.0 manual with the required changes.</span><font face="Times New Roman" size=3> </font> | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U7 |  |  | FINDING | [6 empty] | 97446
36406 | FINDING | OW360_40_Prelim01 manual | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-23 04:28 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-23 04:28 | 3.6.0_U8 (pdf + help) |  |  | 2016-05-23 04:28 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-05 07:02 |  | <p>Some points needed to be&nbsp;modified in OW360_40_Prelim01 manual (kept at&nbsp; <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>)<span style="color:rgb(112, 48, 160);"><font face=Calibri size=3></font></span></p><font size=2><p><br></p><p>1. Page 72-&gt;Section 10.7-&gt; point 8 a) &quot;Select Users dialog box <strong>(see page 74</strong>): Selects users that will be affected by the rule being enabled&quot; page reference to <strong>74</strong> is wrong it should be <strong>73</strong>.</p><p>2. Page 86 -&gt;Section 12.2 -&gt; One more step needed to be added after step 2, &quot; click&nbsp;Add user icon and select user dialog box appears&quot;.</p><p>3. Page 87-&gt;section 12.3 -&gt; Step 4 is needed to be replaced with &quot;right click the name of the account and select remove user option from it&quot;</p><p align=LEFT></p><p> 4.&nbsp; Page 71-&gt;Section 10.7-&gt; point&nbsp;5 &quot;<font size=2>Select the </font><b><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>Policy Rules </font></font></b><font size=2>tab. The Policy Rules tab appears listing the policy rules (see page 72) that are set for the selected policy&quot; </font>page reference to <strong>72</strong> is wrong it should be <strong>71</strong>.<br></p><font size=2><p><br></p></font></font><p><br></p><p align=LEFT></p><p><font size=2><br></font>&nbsp;</p><p><font size=2><br></font></p><p><font size=2><br></font></p> | <p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Rectified&nbsp;the&nbsp;listed issues by the validator, in&nbsp;the Managing Security&nbsp;3.6.0 manual, as appropriate.</span></p> |  |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Refer to the&nbsp;Managing Security&nbsp;3.6.0 manual (Prelim 02)&nbsp;and check&nbsp;the corrections made against your listed issues in the Description field of this finding.</span> | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation | <p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Rectified&nbsp;the&nbsp;listed issues by the validator, in&nbsp;the Managing Security&nbsp;3.6.0 manual, as appropriate.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><br></span></p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">This fix is available in both online help and pdf.</span></font></span></font></p><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For online help,&nbsp;refer to the&nbsp;Security Manager online help in the Ovation 360 U8 build.</span></font></span></font></p><p><font face=Calibri><span><font size=3><span style="color:black;line-height:115%;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">For pdf, refer to the <strong>Managing Security - Prelim 02</strong> manual, <strong>OW360_40_Prelim02.pdf</strong>, at the following path:</span></font></span></font></p><p><font face="Times New Roman" size=3></font><span style="color:rgb(112, 48, 160);"><font face=Calibri size=3>V:\Tests\3.6.0\DOCS_for_Validation</font></span></p><p><font face="Times New Roman" size=3><br></font></p></span><p>Documentation done.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation | 3.6.0 |  | OW360_40_Prelim01 kept at <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>&nbsp; |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">PSH (May 16, 2016):&nbsp;Updated the&nbsp;Managing Security&nbsp;3.6.0 manual with the required changes.</span><font face="Times New Roman" size=3> </font> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the OW360_40_Prelim01 kept at <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>&nbsp;</p><p>2. Review page 71,72,86 and 87&nbsp; to find the observation mentioned in Description filed of this finding</p> |  | U6 |  |  | FINDING | [6 empty] | 97461
36408 | FINDING | Update documentation (Finding 36358) Term Module Process Variable to be used instead of SMV/RDP in the GUIs | Gola, Megha EMR SYSS PWS NOIDA | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Gola, Megha EMR SYSS PWS NOIDA | 2017-07-31 23:45 | [11 empty] | Gola, Megha EMR SYSS PWS NOIDA | 2017-07-31 23:45 | 3.6.0 FP3 U3 | [6 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-05-05 15:56 |  | LC 05/05/2016:&nbsp; Replace SMV and RDP with Module Process Variable in the GUIs and Developer Studio user documentation. |  |  |  | MG (May 24, 2016):&nbsp; The GUI related&nbsp;to RDP will reflect in&nbsp;the Controllers manual (MHM and DEC driver configuration). This will be available in an Ovation 3.6.0 feature pack. Create SDR for this.<div>MG (Aug 1, 2017): The issue cannot be fixed since these fields are not available in GUI now. So no plans to fix.<br></div> | 0 |  |  |  |  | 0 |  |  | MG (May 24, 2016):&nbsp; The GUI related&nbsp;to RDP will reflect in&nbsp;the Controllers manual (MHM and DEC driver configuration). This will be available in an Ovation 3.6.0 feature pack. Create SDR for this.<div>MG (Aug 1, 2017): The issue cannot be fixed since these fields are not available in GUI now. So no plans to fix.<br></div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Costlow, Kim EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [8 empty] | Implementation | 3.6.0 FP3 U3 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Casteel, Linda EMR SYSS PWS PITT | Development |  | MG (May 24, 2016):&nbsp; This will be&nbsp;fixed in an Ovation 3.6.0 feature pack. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U6 |  |  | FINDING | [6 empty] | 116807
36411 | FINDING | 5.4.8 Audio alarm system & 5.4.14 Enhanced key board could not perform on server grade machine as no provision in Server grade machines | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2021-12-03 06:02 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2021-12-03 06:02 |  |  |  | 2021-12-03 05:52 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-06 03:08 |  | 5.4.8 Audio alarm system &amp; 5.4.14 Enhanced keyboard could not be &nbsp;performed as there is no provision in Server grade machines to connect the external speaker and Dell extended keyboard |  |  |  |  | 0 |  |  |  | JJ&gt;Use Win 2012 R2 Server Machine<span style="white-space:pre;"> </span>assigned for Alarms, Graphics&nbsp;<span style="white-space:pre;"> </span>3.6.0_WIN_OPCON_SVTP_rev2.I_JJ.doc<div>Tests to be run&nbsp; are 5.4, 5.9. However&nbsp;<span style="font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, &quot;Helvetica Neue&quot;, Helvetica, Arial, Verdana;font-size:18px;white-space:nowrap;">5.4.8 Audio alarm system &amp; 5.4.14 Enhanced key board could not perform on server grade machine as there is no no provision physically present at system to connect these external peripheral devices.&nbsp;</span></div><div><span style="font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, &quot;Helvetica Neue&quot;, Helvetica, Arial, Verdana;font-size:18px;white-space:nowrap;"><br></span></div><div><span style="font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, &quot;Helvetica Neue&quot;, Helvetica, Arial, Verdana;font-size:18px;white-space:nowrap;">Opcon functions generally verify in Work station grade machines. 3.6.0 Later on ovation releases opcon testing are assigned with EWS system only.</span></div><div><br></div> | 0 |  | Ovation for Windows/Operator Station/Alarms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Model:-</p><p><br></p><p><span style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">PET 320</span></p><p><span style="color:blue;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:10pt;">R720</span></p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | SVTP/STP | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | u6 |  |  | FINDING | [6 empty] | 183000
36429 | FINDING | Maximum no of device details are mentioned wrong for OCR400 Controller | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:55 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:55 | 3.6.0_U8 |  |  | 2016-05-23 05:55 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-09 01:49 |  | <p>User can add up to seven additional device on OCR400 Controller but the help file shows that user can add up to four additional devices.</p><p>User must have to configure IOIC device driver for each redundant controller.</p> |  |  |  | <p>MG (May 13, 2016): According to this finding, updated the&nbsp;caution in the&nbsp;<strong>Section 1.3&nbsp;What is automatic failover control? </strong>of the Controller (OCR 400) user guide for Ovation 3.6. This is available in U8 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_54.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_54.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that, maximum no of device details are mentioned&nbsp;correct for OCR400 Controller .Hence this finding is closed by validation | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software | <p>MG (May 13, 2016): According to this finding, updated the&nbsp;caution in the&nbsp;<strong>Section 1.3&nbsp;What is automatic failover control? </strong>of the Controller (OCR 400) user guide for Ovation 3.6. This is available in U8 build.</p><p>The updated PDF file is&nbsp;placed at: <a href="file://uspit-fp04/val/Tests/3.6.0/DOCS_for_Validation/OW360_54.pdf">\\Uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation\OW360_54.pdf</a></p><p>Online help: Check the OvptStudio help in the Ovation 3.6.0 U8 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 |  | <p>Ovation3.6.0_U6</p><p>OvPtStudio360</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>MG (May 13, 2016): This finding has been fixed and&nbsp;is available in U8 build.</p><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Open the OvPtStudio360 help file.</p><p>2)Go to OCR400 Controller user guide.</p><p>3)Select the automatic failover control section.</p><p>Screenshot is also attached for your reference.</p> |  | U6 |  |  | FINDING | [6 empty] | 97463
36432 | FINDING | Linking of online help is not available from anywhere in developer studio | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-25 04:44 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-25 04:44 | 3.6.0_U8 |  |  | 2016-05-25 04:44 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-09 05:06 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Online help of developer studio is not opening while clicking on help-&gt;Contents &amp; index on developer studio &amp; it gives error as “can’t ’load help file=….”. Please find attached snapshot.</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;"><br></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Note: Online help of developer studio is not opening from any help button of configuration&nbsp;in Developer Studio.</span><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><br></p><font face="Times New Roman" size=3><p style="margin:0cm 0cm 0pt;line-height:18pt;"> <span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Ovation Security Help link is directing to the help file&nbsp;however contents are not getting while clicking on different sections.</span></p></font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><br></p><p>PP:05/25/2016-Verified the above issue in Ov3.6.0_U9 &amp; found O.K.</p><p>Note: The Ovation Security help link is not working in DBS drop100 (GEC) however Ovation Security help link is working in of PGH DBS drop.</p><p>Hence, Finding is closed.</p> |  |  |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015): </span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Check the online help OvptStudio help in the Ovation 3.6.0 U8 build.</span> | 0 |  |  |  |  | 0 |  |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015):&nbsp;</span><span style="box-sizing:border-box;color:rgb(34, 34, 34);">Check the online help OvptStudio help in the Ovation 3.6.0 U8 build.</span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jain, Swati EMR SYSS PWS NOIDA | Sharma, Puneet EMR SYSS PWS NOIDA | Gola, Megha EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA |  |  |  |  | Implementation | 3.6.0 |  | Ov3.6.0_U7,Ws12R2 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Security | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | <span style="color:rgb(34, 34, 34);">MG (May 17, 2015): The issue has been fixed and will be available in U8 build.&nbsp;</span> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>For developer studio help file-</p><p>1. Open the Developer studio.</p><p>2. Select Help menu option.</p><p>3. Click on contents &amp; index option.</p><p>4. Help is not opening &amp; it gives error. Please find attached snapshot.</p><p>For&nbsp;security manager&nbsp;help file-</p><p>1. Open the Developer studio.</p><p>2. Open the manage ovation security window from ovation security</p><p>3. Open the help file from manage ovation security window</p><p>4. Now go to contents and try to open the help of any topic</p><p>5. The particular topic help file&nbsp;is not opened.<br></p> |  | U7 |  |  | FINDING | [6 empty] | 97678
36443 | FINDING | Guide Diamond tool is not working for Ovation session manager | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 06:16 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 06:16 | Ovation 3.6.0_U8 |  |  | 2016-05-23 06:16 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-10 05:23 |  | As per the Ovation application help file Guide&nbsp; diamond tool should work for Ovation session manager window but in actual this tool is not working for Ovation session manager window.<div><br></div><div>Docking and the referenced tool are not implemented in OvSessionManager.</div> | SJ May 16, 2016: Removed references of Ovation Session manager from Guide diamond tool from suggested areas. |  |  | SJ May 16, 2016: Removed references of Ovation Session manager from Guide diamond tool from suggested areas. Check the OvationApplications.chm in Ovation 3.6.0_U8 build. | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that, Ovation Session manager references&nbsp;are&nbsp;removed&nbsp;from Guide diamond tool.Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Operator Station/General/Documentation | SJ May 16, 2016: Removed references of Ovation Session manager from Guide diamond tool from suggested areas. Check the OvationApplications.chm in Ovation 3.6.0_U8 build. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | Ovation 3.6.0 |  | <p>Ovation3.6.0_U6</p><p>Ovation Session manager</p> |  | Ovation for Windows | Ovation | Operator Station/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>SJ May 16, 2016: Check the Ovation 3.6.0_U8 build.</p><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the Ovation session manager window.</p><p>2)Select a dock able tab in the application window and drag it to another location in the application window.</p><p>3)The guide diamond&nbsp;tool did not appear as user drags the tab.</p><p>Screenshot of help file is attached for your reference</p> |  | U6 |  |  | FINDING | [6 empty] | 97470
36447 | FINDING | Alarming RN and RM points on vxsim controller | Cooper, David External Self Employed | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-05-10 12:14 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-05-10 12:14 | [7 empty] | Kijkowski, Tadeusz AUTOSOL PSS WRSW | 2016-05-10 10:13 |  | <p><span lang=EN-US style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000">On sim controller <span lang=EN-US style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">alarming of RN and RM points should be completely disabled, but currently it isn't. Instead, if an RN point has any bit in alarm, a&nbsp;message is generated and 1W_TOGGLE bit is toggled every second.</span></font></span></p> <p><span lang=EN-US style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font color="#000000"><span lang=EN-US style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;">This only happens when 1 millisecond alarm resolution is disabled.</span></font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kijkowski, Tadeusz AUTOSOL PSS WRSW | Development |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>One way to reproduce this issue is to configure Ovation SIS CHARMs (CSLS) on a virtual controller:</p> <p>-&nbsp;Configure Ovation SIS CHARMs device</p> <p>- Add&nbsp;a Logic Solver (it doesn't have to be physically present)</p> <p>- Assign an RN point to the Logic Solver</p> <p>- Load the controller</p> <p>- Open the RN point in point info</p> <p>- Observe constantly changing Toggle bit (1W:14), time of last event and alarm sequence number</p> |  | U7 |  |  | FINDING | [6 empty] | 96566
36454 | FINDING | Description for Attribute "Bad If Limited" of CHARMS needs to be modified | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:34 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:34 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-11 00:19 |  | Description for Attribute &quot;Bad if Limited&quot; needs to be modified for some CHARMS in the following sections:<div>1. To configure RTD Input Charm Class</div><div>2. To configure Analog Input Charm Class</div><div>3. To configure Thermocouple_mV Charm Class</div><div>4. To configure Voltage Charm Class</div><div><br></div><div>Current Description:</div><div><i>When this box is checked, the LSAI algorithm assigned to given CHARM propagates BAD quality to downstream algorithm if point is outside the configured over/under range. The quality of point associated with the input channel is not set to BAD.</i><br></div><div>(Please refer to the screenshot of the current description)</div><div>Updated Description:</div><div><i>When this box is checked, the LSAI algorithm assigned to given CHARM propagates BAD quality to downstream algorithm if point is outside the configured over/under range.</i><br></div><div><i><br></i></div><div>Reason:</div><div><b><i>&quot;The quality of point associated with the input channel is not set to BAD&quot;</i> </b>is valid for SIS Legacy only as<b>&nbsp;</b>the quality of point associated with input channel is set to bad if the Sensor Alarm sheet is running in the Logic Solver.<br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U7 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1. Go to the sections mentioned above<div>2. Verify the description.</div><div><br></div> |  | U6 |  |  | FINDING | [6 empty] | 111014
36481 | FINDING | Information of 'Module Not Scheduled' and 'Module Not Configured' bits of CSLS Control Module's RN point is not given in the Reference manual | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:33 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:33 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-13 00:23 |  | <p>Information of 'Module Not Scheduled' and 'Module Not Configured' bits of CSLS Control Module's RN point is not given in the Reference manual. </p> <p>Currently the user manual does not give exact information of the scenarios in which these bits are set high. The information is required to take any corrective action if the user sees the bits set. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U7 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | U7 |  |  | FINDING | [6 empty] | 111013
36482 | FINDING | Hardening section 12.1.2 in OW360_10 manual need corrections. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-05-24 04:52 | [11 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-05-24 04:52 |  |  |  | 2016-05-24 04:52 |  |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-05-13 01:26 |  | <p>Manual&nbsp;OW360_10 - Hardening section 12.1.2 (To apply Ovation Hardening setting)- Step-3 - 4th statement</p> <p><em>The object in baseline Active Directory. The script also configures the objects for Ovation hardening</em>.</p> <p><br></p> <p>Needs to be changed as&nbsp;:</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><em>Updates the existing Domain Controller GPOs and <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);">creates the new Ovation Hardened GPOs</span></em></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><em><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"></span></em></span>&nbsp;</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><font color="#1e1e1e" size=2 face="Segoe UI">Verified in updated documet named OW360_10.pdf on V:\Tests\3.6.0\DOCS_for_Validation and found the statement as :</font></span></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><font color="#1e1e1e" size=2 face="Segoe UI"></font></span></span>&nbsp;</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><font color="#1e1e1e" size=2 face="Segoe UI"><em>New Ovation hardened GPOs and updates the existing Domain Controller GPOs</em></font></span></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><em><font color="#1e1e1e" size=2 face="Segoe UI"></font></em></span></span>&nbsp;</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:rgb(31,73,125);"><font color="#1e1e1e" size=2 face="Segoe UI">Is as required , hence closed.</font></span></span></p> | <p>Updated hardening information.</p> |  |  | Check the last bullet of Step 3 in Section 12.1.2 in OW360_10. | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [7 empty] | Implementation | U8 |  |  |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  | LC 05/13/2016: Updated OW360_10, Section 12.1.2 (To apply Ovation hardening settings) to have the last bullet of Step 3 say, &quot;<p align=LEFT></p> <font size=2><p>New Ovation hardened GPOs and updates the existing Domain Controller GPOs. &quot;&nbsp; This fix is available in the OW360_10.pdf file on V:\Tests\3.6.0\DOCS_for_Validation.</p></font> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U7 |  |  | FINDING | [6 empty] | 97576
36483 | FINDING | Path of operator applications mentioned on help file is not correct. | Sharma, Puneet EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Sharma, Puneet EMR SYSS PWS NOIDA | 2018-10-23 01:57 | [11 empty] | Sharma, Puneet EMR SYSS PWS NOIDA | 2018-10-23 01:57 | Ovation 3.6.0 _Ux (next feature pack) |  |  | 2018-10-23 01:57 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:00 |  | User can access the operator applications from start&gt;all programs&gt;ovation&gt;ovation application&gt;click the&nbsp;required application. | SJ May 16, 2016: Updated all&nbsp;of the OvationApplications path, removed the notification area line except for the alarm application, updated the Point Review name, and updated system tray to notification area. |  |  | <p>SJ May 16, 2016: As discussed with the Validator, updated all&nbsp;of the OvationApplications path, removed the notification area line except for the alarm application, updated the Point Review name, updated system tray to notification area,&nbsp;and so forth.&nbsp;Check OvationApplications.chm in&nbsp;Ovation 3.6.0 U8 build. Also, check OW360_20.pdf placed @ Val:\Tests\3.6.0\DOCS_for_Validation\OW360_20.pdf</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Documentation | <p>SJ May 16, 2016: As discussed with the Validator, updated all&nbsp;of the OvationApplications path, removed the notification area line except for the alarm application, updated the Point Review name, updated system tray to notification area,&nbsp;and so forth.&nbsp;Check OvationApplications.chm in&nbsp;Ovation 3.6.0 U8 build. Also, check OW360_20.pdf placed @ Val:\Tests\3.6.0\DOCS_for_Validation\OW360_20.pdf</p><p><br></p><p>PSH (May 24, 2016): Updated the HistReview chm file. Signal Diagram chm will work the way as is.&nbsp;Check the next Ovation 3.6.0 build or feature pack.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | Ovation 3.6.0 |  | <p>Ovation3.6.0_U7</p><p>Ovation application help file</p> |  | Ovation for Windows | Ovation | Operator Station/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>SJ May 16, 2016: Changes incorporated. Check Ovation 3.6.0 U8 build.</p><p><br></p><p>PSH (May 24, 2016): Updated the HistReview chm file. Check the next Ovation 3.6.0 build or feature pack.</p><p><br></p><p>PSH (Oct 23, 2018): HistReview chm is updated&nbsp;with the required corrections. Therefore, closing this finding.</p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>&nbsp;1) OvationApplications help file and verify the information&nbsp;present under &quot;understanding the main operator station window&quot;</p><p>Screenshot is also attached for your reference.</p> |  | U7 |  |  | FINDING | [6 empty] | 133208
36484 | FINDING | Graphics application help is not linked correctly with OvationApplications help file | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Swati EMR SYSS PWS NOIDA | 2016-05-23 22:44 | [11 empty] | Jain, Swati EMR SYSS PWS NOIDA | 2016-05-23 22:44 | Ovation 3.6.0_U8 | [6 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 04:07 |  | <p>When user open the graphic help it will navigate to ovation application help file but it will not open the specific graphic help.</p><p>May 24, 2016: The help id is updated in help file. It needs to be updated in the code.</p> | SJ May 16, 2016: Added the help id in first-level topic. |  |  | SJ May 16, 2016: Added the help id in first-level topic. It was present in second-level heading. Check the OvationApplications.chm in Ovation 3.6.0_U8 build. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Documentation | SJ May 16, 2016: Added the help id in first-level topic. It was present in second-level heading. Check the OvationApplications.chm in Ovation 3.6.0_U8 build. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | Ovation 3.6.0 |  | <p>Ovation3.6.0_U7</p><p>Ovation application help file</p> |  | Ovation for Windows | Ovation | Operator Station/Graphics | Documentation | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | SJ May 16, 2016: Updated the help id. Check Ovation 3.6.0_U8 build. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the graphic application.</p><p>2)from the help menu&nbsp;select the help topics.</p><p>3)Ovation application help file opens but it will not open the specific graphic help.</p> |  | U7 |  |  | FINDING | [6 empty] | 97537
36485 | FINDING | OSR is reporting ovation software under other installed software category | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-05-13 08:35 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-05-13 08:35 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 05:49 |  | Ovation software should be reported under other ovation software category but OSR is reporting ovation software under other installed software category. In some drops it is printing the ovation software entry three times. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U7 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1)Generate the OSR report.</p><p>2)Verify the ovation software details in the generated OSR report.</p><p>OSR report is also attached for your reference</p> |  | U7 |  |  | FINDING | [6 empty] | 96815
36486 | FINDING | OSR may report Ovation APC Toolkit 3.6 - HPCR Algorithm PRELIM under other ovation software category | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-05-13 08:36 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-05-13 08:36 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 05:58 |  | like other APC algorithms OSR may report Ovation APC Toolkit 3.6 - HPCR Algorithm PRELIM under other ovation software category. In ovation3.6.0_U7 release OSR is reporting this algorithm under other installed software category. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U7 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <p>1)Generate the OSR report.</p><p>2)Verify the Ovation APC Toolkit 3.6 - HPCR Algorithm PRELIM details in the generated OSR report.</p><p>OSR report is also attached for your reference</p> |  | U7 |  |  | FINDING | [6 empty] | 96817
36487 | FINDING | For LSDVC algorithm DALRT pin does not become active for "confirm lost while commanded on" condition if Fault detection by PVD is enabled | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Konkol, Marek AUTOSOL PWS WRSW | 2017-03-06 06:05 | [11 empty] | Konkol, Marek AUTOSOL PWS WRSW | 2017-03-06 06:05 |  |  |  | 2017-03-06 06:05 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-13 06:14 |  | For LSDVC Algorithm DLART pin should become active if CASND is active and RDBK is inactive(0). But it becomes active only when Fault detection by PVD disabled. DALRT remains inactive if Fault detection is enabled.<div><span style="font-weight:bold;">CASE I</span></div><div>Initial State:</div><div>Fault Detection by PVD is enabled. CASND and RDBK are both active(1). DALRT is inactive(0)</div><div>Action:</div><div>RDBK is made inactive(0).</div><div>Observation:</div><div>No impact on DALRT (Remains inactive)</div><div><br></div><div><div><span style="font-weight:bold;">CASE II</span></div><div>Initial State:</div><div>Fault Detection by PVD is disabled. CASND and RDBK are both active(1). DALRT is inactive(0)</div><div>Action:</div><div>RDBK is made inactive(0).</div><div>Observation:</div><div>DALRT becomes active(1).</div></div><div><br></div><div><br></div><div>DLART should become active even when Fault Detection is enabled.</div><p><br></p><p>NOTE: The above same observation also persist in Legacy SIS (1508).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | 3.6.0 + U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>In SIS control sheets add LSDVC algorithm and perform following steps:</div><ol><li>Algorithm Fault Detection by PVD is enabled. CASND and RDBK are active(1).</li><li>RDBK becomes inactive (0).</li><li>No impact on DALRT.</li></ol> |  | U7 |  |  | FINDING | [6 empty] | 109629
36488 | FINDING | For LSDVC Algorithm FSTAT becomes active only for 1 second when fault state is detected by PVD | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Konkol, Marek AUTOSOL PWS WRSW | 2017-03-02 09:33 | [11 empty] | Konkol, Marek AUTOSOL PWS WRSW | 2017-03-02 09:33 |  |  |  | 2017-03-02 09:33 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-13 06:14 |  | In LSDVC Algorithm when Fault detection is enabled for PVD and Fault is detected by PVD then FSTAT becomes active only for 1 second.<div>Initial State:</div><div>Fault detection By PVD is enabled. CASND, RDBK, OUT and PVD are active (1). FSTAT is inactive (0) adn BLERR is 0</div><div>Action:</div><div>RDBK is made inactive(0).<br></div><div>Observation:</div><div>OUT becomes inactive (0), FSTAT becomes active(1) and BLERR becomes 1024 for one second and then go back to initial state.</div><div>PVD becomes inactive (0) and holds the state</div><div><br></div><div>OUT, FSTAT and BLERR should hold their state.</div><div><br></div><p><br></p><p>NOTE: The above same observation also persist in Legacy SIS (1508).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | 3.6.0 + U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  | OUT will hold its state when RQRST is true.<br>If detection based on PVD value is enabled you must also require a reset. Requiring a reset prevents the algorithm from driving the output back to On during the next scan.<br>See LSDVC algorithm description - Fault State Detection.<br> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>In SIS control sheets add LSDVC algorithm and perform following steps:<br></div><ol><li>Fault Detection by PVD is enabled.&nbsp;CASND, RDBK, OUT and PVD are active (1). FSTAT is inactive (0) adn BLERR is 0</li><li>RDBK becomes inactive (0).</li><li><div>OUT becomes inactive (0), FSTAT becomes active(1) and BLERR becomes 1024 for one second and then go back to initial state.</div><div>PVD becomes inactive (0) and holds the state</div></li></ol> |  | U7 |  |  | FINDING | [6 empty] | 109559
36489 | FINDING | OSR is printing same installed software more than one time on OSR report. | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Costlow, Kim EMR SYSS PWS PITT | 2016-05-16 07:13 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-05-16 07:13 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-13 06:43 |  | OSR is printing same installed software more than one time on OSR report. As an example AMS device manager, Kaspersky Security Center Network Agent, DTM Launcher Application are installed on drop100 these software are reported more than one times on OSR report. OSR report and drop100 control panel screenshot is attached for your reference. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U7 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Generate the OSR report and verify the AMS device manager, Kaspersky Security Center Network Agent, DTM Launcher Application software details |  | U7 |  |  | FINDING | [6 empty] | 96914
36492 | FINDING | SIS Events are not getting generated for any action performed on the CSLS | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:38 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:38 |  |  |  | 2017-02-24 07:38 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-13 07:57 |  | <p>SIS Events are not getting generated for any action performed on the CSLS (lock/unlock/reboot/clear/load etc).</p> <p><span style="COLOR:#1f497d;"><span><span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;<font size=2 face="Segoe UI">a. </font></span></span></span><span style="COLOR:#1f497d;"><font color="#000000">SIS Events&nbsp;show only few&nbsp;SifModule and SifAlert messages as</font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" face="Courier New">&nbsp; 05/12/2016 18:36:14&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS007-CM02: CM2: OCBC0A7002&gt;:&nbsp;&nbsp;Digital Voter Tripped<br>&nbsp; 05/12/2016 18:36:14&nbsp;DROP30&nbsp;&lt;SifModule: D30-CSLS007-CM02: CM2: OCBC0A7002&gt;:&nbsp;&nbsp;VOTER1 voting to trip</font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000">However, when user performs some action on CSLS, no SIS Event is appearing in Historical review application. </font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000"></font></span>&nbsp;</p> <p><font color="#000000">b. <span style="COLOR:#1f497d;"><font color="#000000">It has been observed in U7 that <b>OvSisEvents Service</b> is stopping on its own at frequent intervals on Scanner machine and <b>Event Viewer</b> also reports an Application Error for the same.</font> </span></font><span style="COLOR:#1f497d;"><font color="#000000">Please find the attached screenshot <i>OvSisEventService Event Viewer.png</i></font></span></p> <p><span style="COLOR:#1f497d;"><em><font color="#000000"></font></em></span>&nbsp;</p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font size=3>c. <font size=2 face="Segoe UI">Following messages have been observed in</font> </font><strong><font size=2 face="Segoe UI">OvSisEvents.Service.exe.log</font></strong></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" size=3 face="Courier New"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; <font size=2 face="Courier New">Message: Exception of type 'System.OutOfMemoryException' was thrown.</font></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font size=3><font size=2 face="Segoe UI">Please find attached the</font> </font><font size=3><strong><font size=2 face="Segoe UI">OvSisEvents.Service.exe.log</font> </strong><font size=2 face="Segoe UI">file</font>.</font></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font size=3></font></span></font></span>&nbsp;</p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font size=3>d. </font><font size=2 face="Segoe UI">Following SIS Events observed in sisev.log file:</font></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font face="Segoe UI">OvSisEvents.Service.exe Warning: 0 : Exception occured while parsing SIS RN point <a href="mailto:RJ_D38B1S2-SLAVE_PMR_SB2.UNIT2@NET36">RJ_D38B1S2-SLAVE_PMR_SB2.UNIT2@NET36</a> SID 8000A983H <strong>Value not available.</strong>&nbsp;&nbsp; at Emerson.Ovation.OvData.OvSHC.SHC.GetBitArray32Field(OvSID sid, String field, OvBitArray32&amp; bitArrayVal)</font></span></font></span></p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font face="Segoe UI"> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font size=3><font size=2 face="Segoe UI">Please find attached the</font> <strong>sisev</strong></font><font size=3><strong><font size=2 face="Segoe UI">.log</font> </strong><font size=2 face="Segoe UI">file</font>.</font></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" size=3><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"></span></font></span>&nbsp;</p> <p><span style="COLOR:#1f497d;"><font color="#000000" face="Segoe UI"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;">Attachments:</span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" face="Segoe UI"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;">1. Historical Review Data</span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font face="Segoe UI">2. <font color="#000000">OvSisEventService Event Viewer.png</font></font></span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" face="Segoe UI"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;">3. OvSisEvents.Service.exe.log</span></font></span></p> <p><span style="COLOR:#1f497d;"><font color="#000000" face="Segoe UI"><span style="FONT-FAMILY:&quot;Calibri&quot;,&quot;sans-serif&quot;;COLOR:#0d0d0d;"><font face="Segoe UI">4. sisev</font><font size=3><font size=2 face="Segoe UI">.log</font> </font></span></font></span></p> <p><br>&nbsp;&nbsp; </font></span></p></font></span> | Tracked by separate SDRs<br> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | Saini, Shiva AUTOSOL PWS NOIDA | [5 empty] | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U7 on&nbsp;Historian+Scanner Drop159 (OS: Win 7 64 Bit)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Generate a SIS Event by trying to load/clear/reboot/lock/unlock the CSLS.</p> <p>2. Open Historical Review application.</p> <p>3. Check for the SIS Events under SIS tab.</p> |  | U7 |  |  | FINDING | [6 empty] | 109267
36495 | FINDING | SIS CHARMS documentation for LSDVC Algorithm Quality handling section needs to be updated | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2016-05-18 16:01 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-05-18 16:01 |  |  |  | 2016-05-18 16:01 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-14 05:14 |  | Documentation for LSDVC Algorithm Quality handling section needs to be updated.&nbsp;<div>Current Documentation:</div><div><i>The quality of PVD is that of RDBK unless its quality is Bad, in which case the quality of PVD is the same as OUT.</i><br></div><div><div>Needs to be Updated as:</div><div><i>The quality of PVD is that of RDBK unless is not connected, in which case the quality of PVD is the same as OUT.</i></div></div><div><div>Reason:</div><div>In the Delta V manual it is mentioned:</div></div><div><i>The status of PV_D is that of RDBK_IN_D unless its status is Bad NotConnected, in which case the status of PV_D is the same as OUT_D.</i><br></div><div>Ovation does not have Bad Not Connected Quality.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Casteel, Linda EMR SYSS PWS PITT |  |  |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Go to Quality handling section for LSDVC algorithm in the manual.</li><li>Check the above mentioned statement.</li></ol> |  | U7 |  |  | FINDING | [6 empty] | 97218
36497 | FINDING | CSLS load script is not updated when changes are made in HART Errors Attribute for HART CHARMs | Daly, Joshua D EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-23 00:04 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-23 00:04 | 68059 |  |  | 2016-05-23 00:04 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-16 00:43 |  | <p>CSLS load script is not updated when changes are made in HART Errors Attribute for&nbsp;following HART CHARMs class:</p> <p>a. LS AI 4-20 mA HART CHARM</p> <p>b. Two State DVC Output Redundant</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0_U8 |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U7 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the configuration of any HART CHARMs.</p> <p>2. Go to Attributes tab.</p> <p>3.&nbsp;Modify any of the&nbsp;HART Errors.</p> <p>4.&nbsp;Save the configuration and load the CSLS.</p> <p>No CRC changes are seen in the Load CRC window of the CSLS.</p> |  | U7 |  |  | FINDING | [6 empty] | 97433
36498 | FINDING | CSLS load script is not updated with 'Loop Current Mismatch Detection' Attribute of LS DVC HART CHARM Class | Daly, Joshua D EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-23 00:04 | [11 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-23 00:04 | 68059 |  |  | 2016-05-23 00:04 |  |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-16 01:11 |  | <p>CSLS load script is not updated with 'Loop Current Mismatch Detection' Attribute of LS DVC HART CHARM Class. Verified for following:</p> <p>a. LS DVC HART Redundant DTA CHARM Class (0/4 mA to 20 mA with HART Output)</p> <p>b. LS DVC HART DTA CHARM Class (0-20 mA with HART Output)</p> <p>&nbsp;</p> <p>Note: CSLS load script is updated with the modified configuration of 'Loop Current Mismatch Detection' attribute of LS AI 4-20 mA HART CHARM Class.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [6 empty] | Implementation | 3.6.0_U8 |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U7 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the configuration of above mentioned CHARM Class.</p> <p>2. Go to Attributes tab.</p> <p>3.&nbsp;Modify 'Loop Current Mismatch Detection' attribute.</p> <p>4.&nbsp;Save the configuration and load the CSLS.</p> <p>No CRC changes are seen in the Load CRC window of the CSLS.</p> |  | U7 |  |  | FINDING | [6 empty] | 97434
36499 | FINDING | Incorrect Network adapter speed is printed on OSR report | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-05-16 07:04 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-05-16 07:04 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-16 03:34 |  | Speed of network adapters like OHI1,OHI2,Network&nbsp;bridge is&nbsp;100Mbps but OSR is printing it as 95.4MB and 953.7MB |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation3.6.0_U7 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Generate Extended the OSR report.</p><p>2)Verify the network section under extended information.</p><p>Extended OSR report is also attached for your reference.</p> |  | U6 |  |  | FINDING | [6 empty] | 96911
36500 | FINDING | In 1508 Logic Solver, All Algorithms output showing BAD quality if input of these algorithms are connected Non Secure Parameter | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-20 05:58 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-20 05:58 | 68058 |  |  | 2016-05-20 05:58 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-16 04:12 |  | <p>In 1508 Logic Solver, All Algorithms output showing BAD quality if input of these algorithms&nbsp;is connected to&nbsp;Non Secure Parameter.</p><p>NOTE:&nbsp;If we are using Hardware points (LSAI and LSDI) in place of Non Secure Parameter than BAD quality is not observed for the connected algorithm outputs.</p> |  |  |  |  | 0 |  |  |  | RS 05/20/2016: In Ovation 3.6.0 U8 issue is resolved. Now algorithms outputs are not going to BAD in Connected input algo is NON Secure Parameter and Good in quality. | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | [5 empty] | Implementation | 3.6.0_U8 |  | <ol><li>Insert a new control sheet&nbsp;of 1508 logic solver control module 1.</li><li>Create an SIS Logic having a Non Secure parameter&nbsp;connected to the input&nbsp;of other SIS algorithm, e.g. LSAVTR, LSMID for analog and LSDVTR, LSOR, LSAND for digital.</li><li>Save the Control sheet and Load the Logic Solver.</li><li>Load the respective Controller Drops.</li><li>Open Signal Diagram for the Control sheet&nbsp;inserted in step 1.</li><li>Algorithm outputs showing BAD quality which inputs are&nbsp;connected to Non Secure parameter.</li></ol><p><br></p><p><br></p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U7 |  |  | FINDING | [6 empty] | 97317
36502 | FINDING | Sometimes few CSLS go in to Not registered state upon performing CSLS fail over in certain scenario | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-16 04:46 | [11 empty] | USPITTFSService | 2016-05-16 04:46 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-16 04:46 |  | <div>Sometimes &nbsp;few CSLS &nbsp;go in to Not registered &nbsp;state &nbsp;upon performing CSLS fail over &nbsp;in certain scenario.</div><div><b>Initial Condition:</b></div><div>Both the controller are loaded with same modified sequence number. All 16 CSLS are loaded and running. The redundant SIS network is also in healthy state.</div><div><b>ACTION:</b></div><div>1. SIS Network is failed over (By powering off a LSN switch or removing one cable from IOP's of CSLS base). All CSLS go in maintenance alert.</div><div>2. Then Controller fail over over is done, by Switch off in control controller or removing the N1/N4 cables of the controller.&nbsp;</div><div>(If controller fail over is done by removing cables then fail over takes a sometime. During this interval soft points go in poor quality and hardware points go in bad quality for 6-7 seconds, but come to normal state after fail over)</div><div>3. In this state 4 -5 CSLSes are failed over &nbsp;by manually plugging out the &nbsp;CSLS in control</div><div>Then 1 CSLS goes in Not registered state (Not same CSLS every time). Soft Points go in Poor &nbsp;quality for 1 minute and then go in bad quality.&nbsp;</div><div><b>Work Around:</b></div><div>1. Restored the CSLS. Issue still persist.</div><div>2. Restored Failed controller, it goes in Back up state. Issue still persist.</div><div>3. Restored the SIS network. Issue still persist.</div><div>4. Brought the back up controller in control (Controller which was failed earlier). CSLS goes back in normal state and points come in good quality</div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | Ovation 3.6.0 + U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <div>Both the controller are loaded with same modified sequence number. All 16 CSLS are loaded and running. The redundant SIS network is also in healthy state.</div><div>1. SIS Network is failed over (By powering off a LSN switch or removing one cable from IOP's of CSLS base). All CSLS go in maintaience alert.</div><div>2. Then Controller failover over is done, by Switch off in control controller or removing the N1/N4 cables of the controller.&nbsp;</div><div>(If controller failover is done by removing cables then failover takes a sometime. During this interval soft points go in poor quality and hardware ponts go in bad quality for 6-7 seconds, but come to normal state after failover)</div><div>3. In this state 4 -5 CSLSes are failed over &nbsp;by manually plugging out the &nbsp;CSLS in control</div><div>Then 1 CSLS goes in Not registered state (Not same CSLS every time). Soft Points go in Poor quality for 1 minute and then go in bad quality.&nbsp;</div><div><b>Work Around:</b></div><div>1. Restored the CSLS. Issue still persist.</div><div>2. Restored Failed controller, it goes in Back up state. Issue still persist.</div><div>3. Restored the SIS network. Issue still persist.</div><div>4. Brought the back up controller in control (Controller which was failed earlier). CSLS goes back in normal state and points come in good quality</div> |  | U7 |  |  | FINDING | [6 empty] | 96885
36506 | FINDING | Control logic having Non secure parameter with downstream algorithm. Upon performing Failover in certain scenario, for few CSLSes downstream Algo output go bad for one second. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-16 23:08 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-16 23:08 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-05-16 06:56 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Control logic having Non secure parameter with downstream algorithm. Upon performing Failover in certain scenario, downstream Algo output go bad for one second. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Scenario:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>If Primary SIS network in failed state and then perform Controller Failover by plug out of network cable N4 of controller in Control.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Observed the Control logics having Non Secure parameters as input to downstream Algo output during the scenario. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Verified that downstream Algo (LSAVTR, LSDVTR, LSMID, and LSNOT) output go bad for 1 second. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Note: <span>&nbsp;</span></font><font size=3>In same scenario, downstream Algo LSTP, LSALM outputs do not go bad. LSTP, LSALM output working fine.</font></font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3><br></font></p><p style="margin:0in 0in 0pt;"><br></p><font face=Calibri size=3><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> <br></font></p><p style="margin:0in 0in 10pt;">For reference Control sheet <span>&nbsp;</span>“Failover-NSP.svg” and screenshot “Failover-NSP-Control Sheet Screenshot.png” are attached.</p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 0pt;"><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Saini, Shiva AUTOSOL PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | 3.6.0+ SIS Charms+ |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Steps to reproduce:</font></p><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Step-1: Created a sheet using Non secure parameter and following downstream algorithm. </font></p><font face="Times New Roman" size=3> </font><ol style="list-style-type:lower-alpha;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation analog point) connects to all three inputs of downstream LSAVTR. LSAVTR output terminated by secure parameter.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation Analog R point) connects to inputs of downstream LSALM. LSALM output terminated by secure parameter.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation Digital point) connects to all three inputs of downstream <span style="">&nbsp;&nbsp;</span>LSDVTR. LSDVTR output terminated by secure parameter.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation Digital point) connects to inputs of downstream LSNOT. LSNOT output terminated by secure parameter.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation Analog point) connects to inputs of downstream LSMID. LSMID output terminated by secure parameter.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Non Secure parameter (Ovation Analog point) connects to inputs of downstream LSBFO. LSBFO output terminated by secure parameter.</p><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><br></p></li></ol><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 10pt;"><font face=Calibri size=3>Step-2: Load the sheet and verified that sheet working fine.</font></p><font face=Calibri size=3><p style="margin:0in 0in 10pt;">Failover steps:</p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>Step-3: Created and loaded the above similar sheets to 6 CSLSes. Live trend updated with Non secure parameter’s downstream Algo output points for observation. </p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>Step-4: Fail the Primary SIS network via power off primary SIS switch. Verified <b style="">Bit#1</b> and <b style="">Bit#3</b> IO Device RN points go set and alarm.</p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>Step-5: Unplug the cable of <b style="">N4</b> from controller in control. Failover of Controller happens.</p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>Performed above step-4 and&nbsp;4 multiple times. Verified below observation sometimes for one CSLS or sometimes for Two CSLS randomly out of 6 CSLS placed in observation.</p><p style="margin:0in 0in 10pt;">Observation: </p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>1. Non Secure parameter downstream algorithm (<b style="">LSAVTR, LSDVTR, LSNOT, LSMID, LSBFO</b>) output <span style="">&nbsp;&nbsp;&nbsp;&nbsp;</span>connected to <b style="">secure parameter</b> go bad for one second.</p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> </font>2. In same scenario, downstream Algo LSTP, LSALM output do not go bad.</p><p style="margin:0in 0in 10pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 10pt;"><br></p><font face="Times New Roman" size=3> </font> |  | U7 |  |  | FINDING | [6 empty] | 96990
36511 | FINDING | Some virtual controllers are coming up with an error after a reboot. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 14:04 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 14:04 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-16 14:03 |  | Several virtual controllers come up in error after a reboot. Clearing the alarm and then rebooting, the errors typically return. These errors include missed loop errors and <strong>'Serious'</strong> errors.&nbsp;&nbsp; This was seen on the Tim network with drops 141, 142 and 145 at minimum. See attachments Tim_VC_error.png and Tim_VC_error1.png. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0 U7 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Clear alarms on Drop141, drop142, drop145 on Tim network in validation lab.&nbsp; Reboot controllers. Watch for errors to return. |  | U7 |  |  | FINDING | [6 empty] | 96971
36515 | FINDING | Maximize Button is disabled in OSR GUI Window | Staab, Randy AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Costlow, Kim EMR SYSS PWS PITT | 2016-05-17 07:36 | [11 empty] | Costlow, Kim EMR SYSS PWS PITT | 2016-05-17 07:36 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-17 00:44 |  | <p>Maximize Button is disabled in OSR GUI Window.</p> <p>Please find attached the screenshot OSR Maximum Button.png</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0_U7</p> <p>OS-Windows server 2012.</p> |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the OSR Utility.</p> <p>2. Try to maximize the window.</p> |  | U7 |  |  | FINDING | [6 empty] | 97060
36516 | FINDING | For Composite Block having a LSCALC algo, the output of Composite block goes to BAD | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 6 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-20 05:54 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-20 05:54 | 68058 |  |  | 2016-05-20 05:54 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-17 02:05 |  | If LSCALC algorithm is used in Composite Block&nbsp;than Output of Composite block&nbsp;goes to BAD quality. |  |  |  |  | 0 |  |  |  | <p>RS 05/20/2016: In Ovation 3.6.0 U8 Issue is resolved.</p><p>Please find the attachment &quot;LSCALC_Composite_Block_Error_Resolved.png&quot; for reference.</p> | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | <p>This is caused by an error in generated script. The thing is that LSCALC inside the composite block has it's script overridden inside the composite block's definition body. It should be moved outside composite block.</p><p><br></p><p>Example:</p><p>For now the generated composite block deifinition in ls script for attached composite block is generated as follows:</p><p><br></p><p><em>CFBD<br>{<br>TG='_CSIS01_0_'<br>TP=SCFB<br>AD { TP=FLTWS TG='IN1' FLD { TG=CV V=0 } FLD { TG=ST V=131 } }<br>AD { TP=FLTWS TG='IN2' FLD { TG=CV V=0 } FLD { TG=ST V=131 } }<br>AD { TP=FLTWS TG='OU1' FLD { TG=CV V=0 } FLD { TG=ST V=131 } LNKS=1 }<br>AD { TP=FLTWS TG='OUT2' FLD { TG=CV V=0 } FLD { TG=ST V=131 } LNKS=1 }<br>USG { UTP=EFBU TG='ALG177' TP='LSCALC' EAC { TG='IN' N=2 } EAC { TG='OUT' N=2 } LNKS=2 }<br>LD { TP=DN S='IN1' D='ALG177/IN1' }<br>LD { TP=DN S='IN2' D='ALG177/IN2' }<br>LD { TP=UP S='ALG177/OUT1' D='OU1' }<br>LD { TP=UP S='ALG177/OUT2' D='OUT2' }<br>OV { TG='ALG177/T_EXPRESSION' FLD { TG=CV<br>EXP<br>{<br>EXPS{<br>0;22;8;2;<br>Q;'OUT1.ST';V;11;O;19;Q;'IN1.ST';V;11;O;12;J;10;Q;'OUT1.CV';Q;'IN1.CV';O;19;L;0;<br>Q;'OUT2.ST';V;11;O;19;Q;'IN2.ST';V;11;O;12;J;21;Q;'OUT2.CV';Q;'IN2.CV';O;19;L;1;<br>}}</em></p><p><em>} }<br>}</em></p><p><br></p><p>and then the instance is simply created as:</p><p><br></p><p><em>USG { UTP=CFBU TG='SC00A001' TP='_CSIS01_0_' LNKS=2 }</em></p><p><em>LD { TP=DN S='NSP-0' D='SC00A001/IN1' }<br>LD { TP=DN S='NSP-0' D='SC00A001/IN2' }<br>LD { TP=IU S='SC00A001/OU1' D='AC00A009/IN1' }<br>LD { TP=IU S='SC00A001/OUT2' D='AC00A009/IN2' }</em></p><p><br></p><p>but the OV part from composite block's definition should be moved outside leaving:</p><p><br></p><p><em>CFBD<br>{<br>TG='_CSIS01_0_'<br>TP=SCFB<br>AD { TP=FLTWS TG='IN1' FLD { TG=CV V=0 } FLD { TG=ST V=131 } }<br>AD { TP=FLTWS TG='IN2' FLD { TG=CV V=0 } FLD { TG=ST V=131 } }<br>AD { TP=FLTWS TG='OU1' FLD { TG=CV V=0 } FLD { TG=ST V=131 } LNKS=1 }<br>AD { TP=FLTWS TG='OUT2' FLD { TG=CV V=0 } FLD { TG=ST V=131 } LNKS=1 }<br>USG { UTP=EFBU TG='ALG177' TP='LSCALC' EAC { TG='IN' N=2 } EAC { TG='OUT' N=2 } LNKS=2 }<br>LD { TP=DN S='IN1' D='ALG177/IN1' }<br>LD { TP=DN S='IN2' D='ALG177/IN2' }<br>LD { TP=UP S='ALG177/OUT1' D='OU1' }<br>LD { TP=UP S='ALG177/OUT2' D='OUT2' }<br>}</em></p><p><em><br></em></p><p>And creating an instance:</p><p><br></p><p><em>USG { UTP=CFBU TG='SC00A001' TP='_CSIS01_0_' LNKS=2 }</em></p><p><em>LD { TP=DN S='NSP-0' D='SC00A001/IN1' }<br>LD { TP=DN S='NSP-0' D='SC00A001/IN2' }<br>LD { TP=IU S='SC00A001/OU1' D='AC00A009/IN1' }<br>LD { TP=IU S='SC00A001/OUT2' D='AC00A009/IN2' }<br>OV { TG='SC00A001/ALG177/T_EXPRESSION' FLD { TG=CV<br>EXP<br>{<br>EXPS{<br>0;22;8;2;<br>Q;'OUT1.ST';V;11;O;19;Q;'IN1.ST';V;11;O;12;J;10;Q;'OUT1.CV';Q;'IN1.CV';O;19;L;0;<br>Q;'OUT2.ST';V;11;O;19;Q;'IN2.ST';V;11;O;12;J;21;Q;'OUT2.CV';Q;'IN2.CV';O;19;L;1;<br>}}</em></p><p><em>} }</em></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_U8 |  | DB Server&nbsp;Drop100 on Net#36 with Ovation 3.6.0 U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  | <p><br></p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Create a Composite block having a LSCALC algo and write a program for LSCALC algo.</li><li>Insert a Control sheet in any of the Control module of any CHARMS and use the same Composite block created in step1.</li><li>Save the Control sheet .</li><li>Load the CSLS and respective Controller Drop.</li><li>Open Signal diagram for same control sheet inserted in step 2.</li><li>Output of Composite block showing BAD quality.</li></ol><p>Observation: output is showing BAD quality if LSCALC is used in Composite Block.</p><p><br></p><p><br></p> |  | U7 |  |  | FINDING | [6 empty] | 97313
36518 | FINDING | Ovation Point fully qualified name format mentioned in help file is not correct | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:58 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-23 05:58 | Ovation 360_U8/68081 |  |  | 2016-05-23 05:58 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-17 05:20 |  | Ovation Point fully qualified name format is &quot;pointname.unit@network&quot; but in help file it is mentioned as &quot;pointname unit@network&quot; | SJ May 20, 2016: Added a period in the point name format as suggested. |  |  | SJ May 20, 2016: Added a period in the point name format as suggested. Check OvationApplications.chm online help in Ovation 3.6.0_U8 build. Also, check OW360_20.pdf placed @ <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u>V:\Tests\3.6.0\DOCS</u></span> | 0 |  |  |  | LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that ,Ovation Point fully qualified name format mentioned in help file is correct .Hence this finding is closed by validation. | 0 |  | Ovation for Windows/Operator Station/Point Information/Documentation | SJ May 20, 2016: Added a period in the point name format as suggested. Check OvationApplications.chm online help in Ovation 3.6.0_U8 build. Also, check OW360_20.pdf placed @ <span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><u>V:\Tests\3.6.0\DOCS</u></span> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | Ovation 3.6.0 |  | <p>Ovation3.6.0_U7</p><p>OvationApplications</p> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>SJ May 20, 2016: Check Ovation 3.6.0_U8 build.</p><p>LB-05/23/16:Verified on Ovation3.6.0_U9 and observed that issue got resolved.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Open the point information help file.</p><p>2)Verify the Point fully qualified name format&nbsp; under &quot;Home ribbon tab in the point information window section&quot;</p><p>Screenshot is also attached for your reference</p> |  | U7 |  |  | FINDING | [6 empty] | 97464
36519 | FINDING | To update change in defaulat values of points in trend the point need to be re added in trend window | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Bargaje, Prashant C EMR SYSS PWS PITT | 2016-05-17 07:08 | [11 empty] | Bargaje, Prashant C EMR SYSS PWS PITT | 2016-05-17 07:08 |  |  |  | 2016-05-17 07:08 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-17 05:34 |  | An Analog point is browsed in Live trend and after some time changed Minimum scale and Maximum scale , to see the change in trend window the same point have to re add |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>WS07 64 bit</p><p>OV 3.6.0</p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>User needs to hit Refresh button to&nbsp;refresh the top_limit and bottom_limit values used in Trend App.</p> <p>&nbsp;</p> <p>The observation is consistent with way it is&nbsp;designed to work.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Browsed an LA point &quot;AR-OPH-360&quot; </p><p>Changed the Minimum scale and Maximum scale&nbsp; from 4,60 to 5,85.</p><p>Observed that after few minutes also this&nbsp;was not updated.</p><p>Then re added the point to Trend then changes are observed.</p><p>Please find attached the image .</p> |  | U7 |  |  | FINDING | [6 empty] | 97058
36520 | FINDING | Unable to browse data from 16th CSLS from SIS Diagnostics | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:46 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:46 |  |  |  | 2017-02-24 07:46 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-17 06:11 |  | <div>We have 16 CSLSes configured in the system. We are able view 16 CSLS in view Live devices. Also engineer all 16 CSLSes from developer studio.&nbsp;</div>But unable to browse data from 16th CSLS from SIS Diagnostics. Most of the data is in <b>&quot;Status Unknown!&quot;</b> state.&nbsp;<div>(The only data available is Name, logic solver id, configured scan rate, update time, shadow block control task, proof testing enabled, proof testing interval, proof testing alert due, Overall CRC, IO Channels CRC, Assigned and Key Lock Enabled)<br><div>16th CSLS (CSLS0016) is in configured, commissioned and registered state.&nbsp;</div></div><div><br></div><div>(Please refer to attached screenshots)</div> | Resolved |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>In a system with 16 CSLS, open SIS diagnostics application.</li><li>Browse the 16th CSLS.</li></ol> |  | U7 |  |  | FINDING | [6 empty] | 109271
36521 | FINDING | CHARMS Logic Solver and Virtual CHARMS Logic Solver data is not appearing in SIS diagnostics application home page | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:47 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:47 |  |  |  | 2017-02-24 07:47 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-17 06:26 |  | CHARMS Logic Solver and Virtual CHARMS Logic Solver data is not appearing in SIS diagnostics application home page. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software | Resolved |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  |  | Implementation |  |  | DB Server 100+win 2012 R2 with Ovation 3.6.0 U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Click on SIS diagnostics application icon.</li><li>SIS Diagnostics home page&nbsp;window appears.</li><li>CHARMS Logic Solver and Virtual CHARMS Logic Solver&nbsp;data is not appearing in home page.</li><li>Only legacy SIS data is appearing.</li><li>In Error and warning section also&nbsp;CHARMS Logic Solver and Virtual CHARMS Logic Solver&nbsp;data is missing</li><li>We have an Ovation 3.6.0&nbsp;setup having Legacy SIS, CSLS and VCSLS and below is the setup information.</li></ol><ul dir=ltr><ul><li><div>Legacy SIS - (Drop23/73 and Drop27/77) having total 60 simplex and 2 pairs of redundant&nbsp;1508 logic Solver&nbsp;</div></li><li><div>CHARMS Logic Solver - Drop30/80 having total 16 CSLS and CHARMS IOs</div></li><li><div>Virtual CHARMS Logic Solver - Drop1/11 having total 16 Virtual CSLS.</div></li></ul></ul><p><strong>Observation:</strong> CSLS and VCSLS data is missing from&nbsp;SIS diagnostics home page .</p><p><strong>Attachment:</strong> Please find the attachment for reference.</p><p><br></p><p><br></p> |  | U7 |  |  | FINDING | [6 empty] | 109273
36534 | FINDING | In 1508 Legacy SIS, Algorithms points are going into BAD if Controls sheet is inserted in any Control Module other than Control Module 1. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2016-05-18 04:21 | [11 empty] | USPITTFSService | 2016-05-18 04:21 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 04:21 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">In 1508 Legacy SIS, Algorithms points are going&nbsp; into BAD if Control sheet is inserted in any Control Module other than Control Module 1.</span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <p>DB Server Drop100+win 2012 R2 with Ovation 3.6.0 U7</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">1.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Insert a new Control sheet in Control Module 2, 3 and 4.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">2.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Verify that Control Module 1 doesn't have any Control Sheet or having a blank sheet.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">3.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Load the Logic Solver and respective Controller Drop.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">4.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Open signal Diagram for Control Sheet inserted in step1.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><span style="">5.<span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Algorithms outputs are going into BAD quality.</span></p><font face="Times New Roman" size=3> </font> |  | U7 |  |  | FINDING | [6 empty] | 97147
36535 | FINDING | In 1508 Legacy SIS, SNR data bit 8 to bit 13 is not showing correct value for SDS node point name under PI application, | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 04:26 | [11 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 04:26 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 04:21 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">In 1508 Legacy SIS, SNR data bit 8 to bit 13 is not showing correct value for SDS node point name under PI application, </span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <p>DB Server Drop100+win 2012 R2 with Ovation 3.6.0 U7</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Open PI application for SDS Node point.</li><li>Check the bit 8 to bit 13 for left and right SNR.</li><li>SD node point doesn't show the correct value for SNR.</li><li>to Verify powered off SNR and plug out the fiber cable from SNR to generate error.</li><li>But there is no changes in SNR bit 8 to 13 and no changes in SDS current digital Value bit.</li></ol><p>observation: SNR data is not appearing in SDS node point name.</p><p>Attachment: Please find the attachment &quot;Missing SNR Status in SDS node point name in PI application.png&quot;.</p> |  | U7 |  |  | FINDING | [6 empty] | 97150
36543 | FINDING | Device Status and stand by device status of CSLSes is not available in SIS Diagnostics | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:49 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:49 |  |  |  | 2017-02-24 07:49 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-18 05:59 |  | <div>We have a system configured with 16 CSLSes.</div>Device Status and stand by device status of all 16 CSLSes is not available in SIS Diagnostics. (Please refer to the attached screenshot)<div>It is possible to browse the CSLS in live list device and point information, data is available for all 16 CSLSes regarding which CSLS is in control in both of them. (Please refer to the attached log from PI)</div><div><br><div><br></div></div> | Resolved in final 360<br> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Pandey, Vijay EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Open SIS Diagnostics application.</li><li>Browse all CSLS and Check the Device Status and Stand by Device status.&nbsp;</li></ol> |  | U7 |  |  | FINDING | [6 empty] | 109274
36545 | FINDING | SDS, Logic Solver and SNR data is not appearing in SIS Diagnostics tool. | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:50 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:50 |  |  |  | 2017-02-24 07:50 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 07:17 |  | In Ovation 3.6.0 U7, SDS, Logic Solver and SNR data is not appearing in SIS Diagnostics tool. | Resolved in final 360<br> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | [5 empty] | Implementation |  |  | <p>Ovation 3.6.0 U7</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Click on SIS diagnostics application icon.</li><li>SIS Diagnostics home page&nbsp;window appears.</li><li>Click on&nbsp;&quot;DIAGNOSTICS&quot; button, available on right top corner of application.</li><li>User can see the Router, SIS Switches and Drops data&nbsp;in respective location.</li><li>Check&nbsp;SDS, Logic Solver&nbsp;and SIS Net repeater data and&nbsp;respective data is not appearing in respective location.</li><li>For SDS &quot;SDS Device not responding&quot;-&quot; Diagnostics tool failed to establish communication with SDS&quot; message appeared in SDS section under General.</li><li>For Logic Solver &quot;No Communication&quot; - &quot;SDS could not connect with LS&quot; message appeared in&nbsp;LS section under Configuration.</li><li>For SNR &quot;No Communication&quot; message appeared in&nbsp;SNR section under General.</li></ol><p>Legacy SIS - (Drop23/73 and Drop27/77) having total 60 simplex, 2 pairs of redundant&nbsp;1508 logic Solver&nbsp; and 2 pairs of SNR</p><p>NOTE: We are able to upgrade firmware of SDS, LS and SNR and in PI application able to see SDS, LS data, able to ping SDS also.</p><p><strong>Observation:</strong> SDS, LS and SNR data is missing from SIS Diagnostics tool.</p><p><strong>Attachment:</strong> Please find the attached ZIP file having&nbsp;snapshots of Router, SIS Switches, Controller Drop, SDS, LS, SNR&nbsp;for reference.</p><p><br></p><p><br></p> |  | U7 |  |  | FINDING | [6 empty] | 109275
36548 | FINDING | In SIS Diagnostics tool scroll option should be there in home page to see all errors and warnings. | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:19 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:19 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-18 08:01 |  | <p>In SIS Diagnostics tool scroll option should be there in home page to see all errors and warnings.</p><p>In Current home page&nbsp;user can see few errors and&nbsp;few warnings only</p><p>It will be good for user if scroll option will be there for errors and warnings respectively.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  | Implementation |  |  | Ovation 3.6.0 U7 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <font face="Times New Roman" size=3> </font><ol type=1><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-size:10pt;">Click on the SIS diagnostics application icon.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-size:10pt;">SIS Diagnostics home page&nbsp;window appears.</span></li><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-size:10pt;">User can see few errors and warnings&nbsp;on the&nbsp;home page.</span></li><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-size:10pt;">It will be good for the user if scroll option will be there for errors and warnings respectively.</span></li><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><span style="font-size:10pt;">Please find the attached snapshot for reference where total 91 errors and 7 Warnings and user can't see all.</span></li></ol><span style="font-size:10pt;"><p style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><br></p></span><ol type=1><font face="Times New Roman" size=3> </font></ol><font size=3> </font> |  | U7 |  |  | FINDING | [6 empty] | 98186
36555 | FINDING | Error downloading | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-27 07:28 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-27 07:28 |  |  |  | 2016-05-27 07:28 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-05-18 17:12 |  | <p>Upon Ovation Install to a Base station in U8, The Download shows Error:</p> <p>&nbsp;</p> <p>&nbsp;&nbsp;&nbsp; &nbsp;Unable to open %WDPF_HOME%/mmi/config/PackedGroupDesc.xml</p> <p>&nbsp;</p> <p>The directory C:\Ovation\MMI deos not exist on a Base Station.</p> <p>&nbsp;</p> <p>if the download is aborted, some other required files are not downloaded to the Base Station.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>Per JAM - 5/19/2016 -</p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">That problem does not need fixed. &nbsp;The file in question was only there on server to test an SDR.&nbsp; This file is used by 1 WEC customer in 3.5.1.&nbsp;&nbsp; </span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Arial&quot;,&quot;sans-serif&quot;;COLOR:#1f497d;">In your system you can delete the file on server or just create the directory</span></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U8 |  |  | FINDING | [6 empty] | 97927
36556 | FINDING | Test case 5.4 of TR 3.6.0_SRF1725_SVTP_rev1.2_CG.docx needs to be updated to exclude AMS, GPADCS and ISB | Joshi, Parmesh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-18 23:45 | [11 empty] | USPITTFSService | 2016-05-18 23:45 | [7 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-05-18 23:45 |  | <p>Test case 5.4 of TR 3.6.0_SRF1725_SVTP_rev1.2_CG.docx contains testing of&nbsp;applications :&nbsp;AMS, GPADCS and ISB.</p><p>However,&nbsp;in AMS and GPADCS applications, the Point description and Set/Reset fields are not reflecting anywhere. While in ISB, the Ovation points are not directly used in the toolkit. Hence testing of these applications are NA and needs to be removed from SVTP.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U7 |  |  | FINDING | [6 empty] | 97228
36558 | FINDING | Print option does not print Alarm list as seen in Print Preview option | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-05-27 11:21 | [11 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-05-27 11:21 |  |  |  | 2016-05-27 11:21 |  |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-05-19 05:54 |  | &nbsp;Print option does not print Alarm list as seen in Print Preview option.<br><div><br></div><div>1. For A3 size page(11&quot;x 17&quot;) &nbsp;printing shifts towards left side and left most 2 columns in alarm list &nbsp;are seen cut ,&nbsp;even if the print is given with 'Scale to fit page' option.&nbsp;</div><div>2. For A4 size page(8.5&quot;x11&quot;) printing shifts towards bottom side and 2 rows in alarm list are seen cut,even if the print is given with 'Scale to fit page' option.&nbsp;</div><div><br></div><div><br></div> |  |  |  |  | 0 |  |  |  | As mentioned below i export the alarm list into PDF format and take print out of that format and also tried with different printer model( available for A4 only), found that&nbsp;printed document look correct&nbsp;there was some issue with&nbsp;the local printer configuration.<div>Now alarm list print looks correct, so closing the finding.</div> | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Net#26 EWS<div>drop 139 (W7-SP1-64-bit)</div> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Open Alarms application from ovation applications.<div>2. Click alarm menu button, select print and choose print option.</div><div>3. Click on print option.</div><div>OR<br></div><div>1. Open Alarms application from ovation applications.<div>2. Click alarm menu button, select print and choose Print Preview option. Review the alarm list appears correctly.</div><div>3. Click on print option.</div></div><div><br></div><div>Output is printed sheet but without proper scaling and full details are not getting printed correctly in both &nbsp;A3 and A4 size sheets.</div><div>Scanned copy of both the A3 and the A4 size printouts is attached for reference.&nbsp;</div> |  | U8 |  |  | FINDING | [6 empty] | 97941
36559 | FINDING | Test sections of Hardening removal in TR 3.6.0_Hardening_SVTP_rev1.3_CG.xlsx needs to be changed and a new section of Reboot systems is to be added | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-19 05:58 | [11 empty] | USPITTFSService | 2016-05-19 05:58 | [7 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-05-19 05:58 |  | <p>In TR 3.6.0_Hardening_SVTP_rev1.3_CG.xlsx, under &quot;Removing&quot; tab the test sections are marked as 7.x.x. However, these sections mentioned in the Hardening document OW360_10&nbsp;is mentioned as 12.4.x. The same needs to be changed. </p><p>Also, a new test section 12.4.7 is to be added. This is related to Reboot of the entire system.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U7 |  |  | FINDING | [6 empty] | 97238
36567 | FINDING | Last copied object is getting pasted in all GBNT editors if GBNT is opened on multiple remote log in sessions. | Johnson, Kathy EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Johnson, Kathy EMR SYSS PWS PITT | 2016-06-30 10:10 | [11 empty] | Johnson, Kathy EMR SYSS PWS PITT | 2016-06-30 10:10 | 68879 |  |  | 2016-05-23 08:56 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-20 01:13 |  | <p>GBNT session is opened on a DBS machine locally. Another session of GBNT is opened on the &nbsp;same DBS thru remote log in session.</p><p>It is observed that&nbsp; an object copied on DBS locally gets pasted on the GBNT session which is opened on the same DBS thru remote login session.</p><p>Similarly an object copied on remote login session gets pasted in GBNT which is opened locally.</p><p>Therefore, in multiple GBNT remote login sessions copy and paste operation is not working correctly, as the last copied object is getting pasted in all&nbsp; the sessions.</p><p>This creates utter confusion among the users of multiple sessions.</p><p><br></p><p>PS :-&nbsp;&nbsp;&nbsp;&nbsp; This issue &nbsp;is observed in older ovation releases also.(e.g.3.5.x)</p> |  |  |  | To test this you must have multiple users logged into the DBS at the same time , simultaneously doing GBNT copy/paste operations. Verify that each user's paste data is what that user copied. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.X |  | <p>OV 3.6.0</p><p>OV 3.5.X</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Issue Recreated | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>A sessionId (name) will be appended to the local pastefile on disk used to perform a copy/paste operation. Thereby, when multiple users are running GBNT on the same computer and doing simultaneous copy/paste operations, they have unique sessionId's, and now will have unique pastefile names on disk, and will not overwrite one anothers copy/paste data.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Opened a graphics on GBNT at DBS thru locally.</p><p>Anther graphics is opened on GBNT thru remote login of the DBS at the same time.</p><p>An object on the GBNT window is copied to paste on the same graphics at local session.</p><p>Same time another object is copied on the GBNT window of remote login session.</p><p>Then its is observed that last copied object is pasting on both GBNT window.</p><p><br></p><p><br></p> |  | U8 |  |  | FINDING | [6 empty] | 99162
36578 | FINDING | CRC value of CHARMS IO in dump CRC file is not matching with the CRC value of CHARMS IO in SIS Diagnostics tool | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:19 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:19 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-22 08:24 |  | CRC value of CHARMS IO in dump CRC file is not matching with the CRC value of CHARMS IO in SIS Diagnostics tool. This has been observed for all CHARMS type configured.<div>For Example:</div><div>CRC value for LS DO 24 VDC ETA CHARMS at slot CHM3-02 in SIS Diagnostics tool is : 19486 (Please refer attached <i>SIS Diag_CHARM_CRC_U9.png</i>)&nbsp;</div><div><div>CRC value for LS DO 24 VDC ETA CHARMS&nbsp;at slot CHM3-02 in Dump CRC is&nbsp;: 4185255043 (Please refer attached<i> Dump_CRC_U9_Test.html</i>)</div><div><br></div></div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Open SIS Diagnostics tool and browse CHARMS in a CSLS and check its CRC.</li><li>Take Dump CRC of the same CSLS as above.</li><li>Compare the CRC value of CHARMS in Dump CRC file and in SIS Diagnostics tool.&nbsp;</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98185
36580 | FINDING | Shift button movement, adding control pin & aligning of algos in control macro sheet is not smooth | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-25 05:49 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-25 05:49 | [7 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-23 03:23 |  | <p>Following functionalities are not smooth in control macro bulider</p><p><br></p><p>1. While creating the control macros shift button plotter is deviating from the pointer location.</p><p>2. Adding the control pins in control macro sheet is very difficult</p><p>3.Placing and aligning algos in control macros sheets are not smooth.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV 3.6.0 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>The functionality appears to work as expected.&nbsp; </p><p>Yes functionality is working , however it is not smooth.</p><p>In control macro builder while pressing the shift key to locate the cursor it is slightly moving from the exact location</p><p>Getting difficulty in adding extra control pin at algos in control macro builder.</p> |  | U8 |  |  | FINDING | [6 empty] | 97688
36581 | FINDING | Signnal line selection with single double click is not possible , only by drag option signal line can select | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-24 23:06 | [11 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-24 23:06 | [7 empty] | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-23 03:30 |  | Signal line selection with&nbsp; single double click is not possible , only by drag option signal line can select |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U8 |  |  | FINDING | [6 empty] | 97657
36582 | FINDING | Software installation manual (OW360_10) needs some modification | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-06-07 01:20 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-06-07 01:20 |  |  |  | 2016-06-07 01:20 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-23 06:09 |  | <p>Software installation manual (OW360_10) needs&nbsp;following modification :-</p><p><br></p><p>1.&nbsp;After step1&nbsp;in section 4.2 (page 39) a pop-up message appear on the screen&nbsp;to&nbsp;Select the language (please refer attached screen shot WS12-R2_install.jpg)</p><p>&nbsp;&nbsp;&nbsp;&nbsp;This step should also included in manual. Same is also applicable for WIN7 installation ( After step1 of section 5.2 (page 53))</p><p>&nbsp;&nbsp;&nbsp; </p><p>2. Step 2 of Section 11.1.1&nbsp;(Page no 122) it mentioned that </p><p align=LEFT></p><p> <font size=2>&nbsp;&nbsp; &quot;Select </font><b><font face="Arial,Arial" size=2><font face="Arial,Arial" size=2>Start &gt; Control Panel &gt; Programs &gt; Programs and Features &gt; Uninstall a Program </font></font></b><font size=2>(for Windows 7 and Server 2008 R2 systems)&quot;</font></p><p><font size=2>(a)&nbsp;the words &quot;Programs&quot; should be remove as&nbsp;it &nbsp;has no significance</font></p><p><font size=2>(b)&nbsp;&nbsp;<font face=Arial><strong>Uninstall a Program </strong>should be replace with <strong>Uninstall or Change&nbsp;a Program </strong>as in control panel link appear as <strong>Uninstall or Change&nbsp;a Program</strong>&nbsp;</font></font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>3. After step12&nbsp;in section 11.2.2 (page 125) &quot;Restart Required&quot; pop-up window appear to reboot computer. This steps is missing in the manual.</font></p><p><font face=Arial size=2>&nbsp;&nbsp; It should&nbsp;be included.</font></p><p><br></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>&nbsp;&nbsp;<br></font></p><p><font size=2><font face=Arial>&nbsp;&nbsp;<strong>&nbsp;</strong>&nbsp;</font>&nbsp;</font></p><p>&nbsp;</p> |  |  |  | See Sections 11.1.1 and 11.2.2 for fixes. | 0 |  |  |  | <p>MS :&nbsp;Reviewed the&nbsp;installation manual (OW360_10) placed in V:\Tests\3.6.0\DOCS_for_Validation and observed that all</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; the issue has been fixed as mentioned&nbsp;in Resolution field of this finding.</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Hence I am closing this finding.&nbsp;</p> | 0 |  | Ovation for Windows/General/Documentation | Updated the Software Installation Manual with precise steps for loading Ovation. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Garg, Amit AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  | <p>Ovation 3.6.0</p><p>Software installation manual (OW360_10)</p> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>LC 05/24/2016: Made corrections to:</p><p>- Step 2 of Section 11.1.1&nbsp;(a and b). </p><p><font face=Arial size=2>- Section 11.2.2&nbsp; added &quot;Restart Required&quot; pop-up window.<br>- Did NOT make correction to item # 1about </font>Selecting the language because it is already in the manual. This was approved by a Development Engineer.&nbsp; I can send you email to support this. The email said, &quot;<font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>In the finding (36582), you can ignore step 1… because as you said, it is clearly mention to choose language, time, etc.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;"><font size=3>As far as Step 2, he is correct. Change the document to reflect his comment.</font></span></p><p>See OW360_10 in V:\Tests\3.6.0\DOCS_for_Validation for these corrections.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the Software&nbsp;installation manual (OW360_10)</p><p>2. Review the section 4.2 and 11.1.1 as mentioned the description field of this finding</p> |  | U9 |  |  | FINDING | [6 empty] | 98316
36588 | FINDING | Achilles Level 1 Certification test did not pass. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-05-23 14:19 | [11 empty] | USPITTFSService | 2016-05-23 14:19 | [7 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-05-23 14:19 |  | The ICMP Monitor 1 reported. warnings for the following tests:<br><br>IP Grammar - Header Fields<br>ICMP Storm<br>ICMP Grammar<br>ICMP Type/Code Cross Product<br>UDP Unicast Storm<br>UDP Grammar<br><br>The results are attached.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U9 |  |  | FINDING | [6 empty] | 97522
36594 | FINDING | Error appears while opening Ovation control builder help from Start-> All Programs-> Ovation Engineering Tools | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-05-24 03:12 | [11 empty] | USPITTFSService | 2016-05-24 03:12 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-05-24 03:12 |  | <p>It has been observed that Ovation Control Builder Help gives error &quot;The application failed to start because it could not find or load the Qt platform plugin 'windows' &quot; while opening it from below mentioned locations:</p><ul><li>Start-&gt; All Programs-&gt; Ovation Engineering Tools-&gt;Ovation Control Builder Help</li><li>Ovation Engineering Tools folder on desktop-&gt; Ovation Control Builder Help</li></ul> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>GEC Lab,</p><p>DBS220, </p><p>EWS195</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Try to open control builder help from below mentioned locations:</p><ol><li>Start-&gt; All Programs-&gt; Ovation Engineering Tools-&gt;Ovation Control Builder Help</li><li>Ovation Engineering Tools folder on desktop-&gt; Ovation Control Builder Help</li></ol><p>Please refer the attached snapshot.</p> |  | U9 |  |  | FINDING | [6 empty] | 97570
36595 | FINDING | Point Review Current filter settings bar is not displaying all the selected drops. | Augustine, Lisa EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Augustine, Lisa EMR SYSS PWS PITT | 2016-05-25 09:22 | [11 empty] | Augustine, Lisa EMR SYSS PWS PITT | 2016-05-25 09:22 | [7 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-24 04:57 |  | Point Review Current filter settings bar is not displaying all the selected drops, if the number of drops are more. In gec val lab 52 drops are available on unit0 after selecting all the drops only 27 drops are displaying on Point Review Current filter settings bar. |  |  |  |  | 0 |  |  |  | The tooltip for the selected drops will be updated to list all of the drops selected for the review&nbsp;filter.&nbsp; This&nbsp;fix will be added to the Ovation 3.6.0 Feature Pack. It will not be added to the initial 3.6.0. | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation3.6.0_U9</p><p><br></p> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1)Launch the point review application.</p><p>2)Select all the drops (drops should be greater than 27)</p><p>3)Verify these selected drops on Point Review Current filter settings bar.</p><p>Screenshot is also attached for your reference</p> |  | U9 |  |  | FINDING | [6 empty] | 97727
36596 | FINDING | Software installation manual (OW360_10) needs some modification | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-06-07 01:42 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-06-07 01:42 |  |  |  | 2016-06-07 01:42 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-24 06:42 |  | <p>Software installation manual (OW360_10) needs&nbsp;following modification :-</p><p><br></p><p><font face=Arial size=2>1.&nbsp; Replace text &quot;OK&quot; with &quot;Close&quot; in step 6 of section&nbsp;7.3.8. (page 78).</font></p><p><br></p><p><font face=Arial size=2>2.&nbsp; In step 3&nbsp;of section&nbsp;6.2.3 (page 57)&nbsp;replace text &quot;100 TX&quot; with &quot;100 Mbps&quot; .</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>3. Replace the text &quot;License key&quot; with &quot;Add License&quot; in step 20, 21 and 22&nbsp;of section 11.2.2 (page 125)</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>4. In step 26 of section 11.2.2 (page 126) &quot;Domain Server IP address&quot; is required which is not mentioned&nbsp;in manual&nbsp;</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>5. &nbsp;In step 29 (e) of section 11.2.2 (page126) along with the IP address &quot;Computer Name &quot; is also required,</font></p><p><font face=Arial size=2>&nbsp;&nbsp; &nbsp;which is n</font><font face=Arial size=2>ot mentioned in the manual</font></p><p><br></p><p>6.&nbsp; <font face=Arial size=2>After step&nbsp;32 of section 11.2.2 (page 126)&nbsp; &quot;Set up Complete&nbsp;Wizard&quot; window&nbsp;appears instead of instead of step 33 (Security Message )&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</font> </p><p><br></p><p>7&nbsp;<font face=Arial size=2> After step 35 of section 11.2.2 (page 127) &quot;Consistency Analysis Summary&quot; window as mentioned in step 36 does not appear</font>&nbsp;</p> | Updated Software Installation Manual to clarify installation procedures. |  |  | <p>See Sections mentioned in Resolution field.</p> | 0 |  |  |  | <p>MS :&nbsp;Reviewed the&nbsp;installation manual (OW360_10) placed in V:\Tests\3.6.0\DOCS_for_Validation and observed that all</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; the issue has been fixed as mentioned&nbsp;in Resolution field of this finding.</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Hence I am closing this finding.</p> | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Garg, Amit AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  | Manual : OW360_10 |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>LC 05/24/2016: Updated the following:</p><p><font face=Arial size=2>&nbsp; 1. Step 6 of section&nbsp;7.3.8.</font></p><p><br></p><p><font face=Arial size=2>2.&nbsp; Section 6.2.3 (page 57)&nbsp;replace text.</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>3. Steps 20, 21 and 22&nbsp;of section 11.2.2.</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>4.Step 26 of section 11.2.2 added &quot;Domain Server IP address.&quot;&nbsp;</font></p><p><font face=Arial size=2><br></font></p><p><font face=Arial size=2>5. &nbsp;In step 29 (e) of section 11.2.2 added IP address &quot;Computer Name.&quot;</font></p><p><font face=Arial size=2>&nbsp;&nbsp; &nbsp;which is n</font><font face=Arial size=2>ot mentioned in the manual</font></p><p><br></p><p>6.&nbsp; <font face=Arial size=2>After step&nbsp;32 of section 11.2.2 replaced with &quot;Set up Complete&nbsp;Wizard&quot; window.&nbsp;&nbsp;&nbsp;&nbsp;</font> </p><p><br></p><p>7&nbsp;<font face=Arial size=2> After step 35 of section 11.2.2 removed &quot;Consistency Analysis Summary&quot; window.</font></p><p><font face=Arial size=2>Changes are available in OW361_10 in </font></p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the manual OW360_10</p><p>2. Review the section&nbsp; 6.2.3,7.3.8 and 11.2.2 as described in description field of finding</p><p><br></p> |  | U9 |  |  | FINDING | [6 empty] | 98319
36601 | FINDING | Shape/Macro is getting resized after rotating it | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Johnson, Kathy EMR SYSS PWS PITT | 2016-05-25 13:01 | [11 empty] | Johnson, Kathy EMR SYSS PWS PITT | 2016-05-25 13:01 |  |  |  | 2016-05-25 13:01 |  |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | 2016-05-24 23:23 |  | Place any macro/shape in vertical/horizontal position. Rotate it horizontally or vertically.Then it is observed that the size is changed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OV 3.6.0</p><p>OV3.5.x</p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Validation |  | <p>Instead of looking at the virtual width and height of the item as displayed in the source syntax - look at the physical size of the items in each photo. They are the same size. Virtual coordinates are displayed in the source syntax. at draw time, virtual coordinates are converted to physical screen[pixel] coordinates, and those are the same. When we rotate a rectangle 90 degrees we do not simply swap the virtual width and height. We internally swap the pixel width and height - which you cannot check for since the pixel coords are not displayed.&nbsp; The shapes/macros&nbsp;are not different sizes and the rotate function is working correctly.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Place a macro in graphic in horizontal position. Attached the image grp1.</p><p>Here the size of the shape is 3451&nbsp;&nbsp;&nbsp;&nbsp; X&nbsp;&nbsp;&nbsp; 1758</p><p>Then rotate vertically .Attache the image grap2</p><p>Now the size is 1032&nbsp;&nbsp;&nbsp; X&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 5946</p><p><br></p> |  | U9 |  |  | FINDING | [6 empty] | 97743
36602 | FINDING | Main Header in Contents tab of Controller Diagnostics gives error | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2016-05-27 01:22 | [11 empty] | USPITTFSService | 2016-05-27 01:22 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-05-25 01:46 |  | <p>Main Header in Contents tab of Controller Diagnostics gives error message as in attached snapshot.</p> <p>All other topics are displayed without any error.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | Ovation 3.6.0_U6 (DBS Drop100)E |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Open Controller Diagnostics and click on help.</li> <li>Go to Contents tab and double click main header named 'Controller Diagnostics'</li> <li>Error message is seen as in attached screenshot. All other topics open correctly.</li></ol> | EPM Validation | U9 |  |  | FINDING | [6 empty] | 97900
36603 | FINDING | SIS diagnostics is unable to get data for CSLSes if Partner controller drop is in control | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:52 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:52 |  |  |  | 2017-02-24 07:52 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-25 02:48 |  | SIS diagnostics is unable to get data for CSLS if Partner controller drop is in control. &quot;Status unknown!&quot; is shown for all CSLSes. &nbsp;The behaviour is observed in both cases when Primary is switched off and when Primary is in backup state.&nbsp;<div>The SIS Diagnostics tool shows the Partner controller in Back up State even if is in Control State. (Please refer to attached screenshots)</div><div>Also if Partner comes in control when SIS diagnostics tool is already running then SIS diagnostics hold the previous data and does not update the data.<br></div><div><br><div><br></div></div> | Resolved in final 360<br> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Bring Partner Controller in Control.</li><li>Check the data on SIS Diagnostics tool.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 109276
36604 | FINDING | software installation manual (OW360_10) manual need some modification | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:45 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-02-16 15:45 |  |  |  | 2017-02-16 15:45 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-25 05:08 |  | Some points needed to be modified in OW360_10 manual (kept at&nbsp; <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a>)<br>1. On Page 53 section:6.2.2 after step 8 if step 9 is followed then a popup appears (see attached screenshot IPCONFIG.jpg) , if we click yes to that popup then changes made in earliar steps of section:6.2.2 gets lost. Hence in order to avoid that after step 8 we need to close that window and than again open the NIC properties window |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | OW360_10 kept at <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a> <br> |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | LC 05/25/2016:&nbsp; Create SDR. Issue will be fixed in a feature pack. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the OW360_10 kept at <a href="file://\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation">\\uspit-fp04\val\Tests\3.6.0\DOCS_for_Validation</a> </p><p>2. Review page 53 to find the observation mentioned in Description filed of this finding</p> |  | U9 |  |  | FINDING | [6 empty] | 108987
36606 | FINDING | Software installation manual (OW360_10) manual need some modification | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Casteel, Linda EMR SYSS PWS PITT | 2016-07-28 15:47 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-07-28 15:47 |  |  |  | 2016-07-28 15:47 |  |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | 2016-05-25 05:28 |  | <p>Software installation manual (OW360_10) manual need&nbsp;below modification :-</p><p>Step17&nbsp;&quot;Prerequisite check&quot;&nbsp;of section 7.2&nbsp; (page 70) failed&nbsp;if DNS server is not selected in step 6 of section 7.2.</p><p>(Please refer attached screen shot Active Directory Error.jpg)</p><p>&nbsp;So along with Active Directory Domain service,&nbsp; DNS server should also be selected at step 6 (page 65) to complete AD DS installation&nbsp;</p><p>(Please refer attached screen shot DNS_option.jpg)&nbsp;&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Garg, Amit AUTOSOL PWS NOIDA | [9 empty] | Implementation |  |  | Manual :OW360_10 |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Sahay, Madhukar EMR SYSS PWS NOIDA | Validation |  | <p>LC 05/25/2016:&nbsp; Create SDR. Issue will be fixed in a feature pack.</p><p>LC 07/28/2016: Per the SME in Product Development, the manual is correct as is. You do not need to select DNS server.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the manual OW360_10</p><p>2. Review the step 6 and step 17 of section 7.2</p> |  | U9 |  |  | FINDING | [6 empty] | 100429
36616 | FINDING | Issues with redundant Virtual Controllers | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:17 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-06-07 13:17 |  |  |  | 2016-06-07 13:17 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-05-25 15:37 |  | <p>Redundant Virtual Controllers are not all performing as expected.&nbsp; Some redundant virtual controllers in the validation lab will not stay on the highway and continuously reboot, leaving no VC in control for periods of time.&nbsp; This is not occurring with all redundant VCs, but have not been able to track down the cause. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0 U8 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | IC 6/7/16&gt; closed finding, track as SDR 36730. | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Create redundant VCs and observe. Seems to occur more frequently in VCs with consecutive drop numbers. |  | U8 |  |  | FINDING | [6 empty] | 98347
36619 | FINDING | SIS Diagnostics does not update the MAC addresses of CSLS pair if they are swapped | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:18 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:18 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 01:26 |  | If CSLS pair is swapped. &nbsp;CSLS on left moved to right and CSLS on right moved to left the Mac addresses do update in SIS Diagnostics tool.&nbsp;<div>But the the serial number of the CSLS pair does get updated.</div><div>(Please refer to the attached screenshots)</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Check the mac Addresses &nbsp;and serial numbers of CSLS pair in SIS Diagnostics tool.</li><li>Swap the CSLS pair.</li><li>Check the mac Addresses &nbsp;and serial numbers of CSLS pair in SIS Diagnostics tool.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98183
36620 | FINDING | Occasionally the OvSisDiagnostics service stops and "Problem contacting Diagnostics service" message is received when SIS Diagnostics is opened | Zochowski, Michal AUTOSOL DX WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:53 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2017-02-24 07:53 |  |  |  | 2017-02-24 07:53 |  |  |  | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 01:31 |  | Occasionally the OvSisDiagnostics service stops and &quot;Problem contacting Diagnostics service&quot; message is received when SIS Diagnostics is opened.<div>The behaviour has been observed 2 times in 2 days (48 Hours).</div><div>Note: After reboot of machine SIS diagnostics tool is running.</div> | Resolved in final 360<br> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | Ovation 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Ran SIS diagnostics tool.</li><li>Unable to open SIS diagnostics tool. Error received &quot;Problem contacting Diagnostics service&quot;.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 109277
36621 | FINDING | SIS Diagnostics tool should also give data about the CHARMS attribute and Terminal Block | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:18 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:18 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 01:56 |  | SIS Diagnostics tool should also give data about the CHARMS attribute and Terminal Block.<div>Currently SIS Diagnostics tool does not give any information about the attributes of CHARMS and type of Terminal Block it is connected.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <ol><li>Check the data for CHARMS in SIS diagnostics tool.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98181
36622 | FINDING | Reconcile Functionality is not working for SIS Control Sheets | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-26 02:53 | [11 empty] | USPITTFSService | 2016-05-26 02:53 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-26 02:53 |  | <p>Reconcile Functionality is not working for SIS Control Sheets. (SIS CHARMs as well as Legacy SIS). </p> <p>&nbsp;</p> <p>Note:Changes to be reconciled are reflected in the Ovation Developer Studio when the Reconcile option is selected after Right Click on the Controller Drop in which Control Sheet is present. While no changes are reflected when the Control Sheet is opened in the Control Builder.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U9 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Signal Diagram and make some changes in the Tuning Parameters.</p> <p>2. Right Click on the Controller Drop in which the Control Sheet is present and right click on Reconcile.</p> <p>3. Reconcile the changes made to the Control Sheet.</p> <p>4. Open the Control Sheet in Control Builder.</p> <p>&nbsp;</p> <p>Note: Reconcile Parameter is configured as TRUE in Configuration of Control Builder.</p> |  | U9 |  |  | FINDING | [6 empty] | 97784
36623 | FINDING | Information about Reconcile Operation for SIS Control Sheets is missing in the user manual for SIS CHARMs | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:33 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:33 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-26 03:05 |  | <p>Information about Reconcile Operation for SIS Control Sheets is missing in the user manual for SIS CHARMs.</p> <p>User manual should contain information about Reconcile Functionality for SIS Control Sheets and the consecutive effect on CSLS load.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <span style="FONT-SIZE:9pt;FONT-FAMILY:'Segoe UI','sans-serif';COLOR:black;"><font size=2>Ov3.6.0_U9 on DBS drop100 (OS: Windows Server 2012 R2)&nbsp;</font></span> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U9 |  |  | FINDING | [6 empty] | 111012
36624 | FINDING | OW360_30 , OW360_36 , CON_36_01 manuals needs some modifications regarding loading of backup Controller. | Gola, Megha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sahay, Madhukar EMR SYSS PWS NOIDA | 2017-08-04 01:57 | [11 empty] | Sahay, Madhukar EMR SYSS PWS NOIDA | 2017-08-04 01:57 | 77649 |  |  | 2017-08-04 01:57 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-05-26 03:46 |  | <p>Below section of manual <strong>OW360_30</strong>&nbsp; need modification&nbsp; </p><p>On page 85 section:8.3.5 in point 6, page 102 section:9.4.3 in point 6, page 193 section:16.4 in point 6 and page 221 section:17.6.7 in point 5 it is mentioned that secondary controller should be loaded first but the controller which is in control should be loaded first, hence it is needed to be changed.</p><p><br>Below section of manual <strong>OW360_36</strong>&nbsp; need modification</p><p>On page 48 section: 4.1.23 and page 78 section: 4.2.24 it is not mentioned which controller should be loaded first hence a note is needed to be added, that the controller which is in control should be loaded first.</p><p><br></p><p>Below section of manual <strong>CON_36_01</strong>&nbsp; need modification</p><p>&nbsp;In the topic &quot;To load a Controller (for an Ethernet link controller&nbsp; module),&quot; it states that you should first load the controller that is not in control&nbsp;which is incorrect. Controller which is in control should be loaded first.</p><p><br></p> |  |  |  | MG (May 27, 2016):&nbsp; This will be&nbsp;fixed in an Ovation 3.6.0 feature pack. Create SDR for this.<div>MG (Aug 1, 2017): The issue has been fixed and is available in the FP3 U3 build. &nbsp;Check the pages mentioned in the description field in the Ovpt studio help for U3 build. The first two items are available in this build and the information about the&nbsp;third item is updated by Mukesh Maggu.</div><div>MM (Aug 2, 2017): The&nbsp;third item&nbsp;will be&nbsp;updated by Mukesh Maggu when&nbsp;he will&nbsp;update the ELC manual in the next release after discussing this issue with Al and David (the developers).<br></div> | 0 |  |  |  | <p>Verified fixes of first two items in online help of FP3 U3 and entered SDR 40082 to track third item.</p><p>I am closing this finding.</p> | 0 |  | Ovation for Windows/General/Documentation | MG (May 27, 2016):&nbsp; This will be&nbsp;fixed in an Ovation 3.6.0 feature pack. Create SDR for this.<div>MG (Aug 1, 2017): The issue has been fixed and is available in the FP3 U3 build. &nbsp;Check the pages mentioned in the description field in the Ovpt studio help for U3 build. The first two items are available in this build.</div><div>MM (Aug 2, 2017): The&nbsp;third item&nbsp;will be&nbsp;updated by Mukesh Maggu when&nbsp;he will&nbsp;update the ELC manual in the next release after discussing this issue with Al and David (the developers).<br></div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Maggu, Mukesh EMR SYSS PWS NOIDA | [7 empty] | Implementation | 3.6.0 FP3 U3 |  | OW360_30 , OW360_36 , CON_36_01&nbsp; manual |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | MG (May 27, 2016):&nbsp; This will be&nbsp;fixed in an Ovation 3.6.0 feature pack.<div>MG (Aug 1, 2017): The issue has been fixed and is available in the FP3 U3 build.&nbsp;The first two items are available in this build and the information about the&nbsp;third item is updated by Mukesh Maggu.</div><div>CG (8/1) - Finding assigned to Madhukar for retesting in FP3 U3 build.</div> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Open the OW360_30, OW360_36 and&nbsp;CON_36_01 manuals&nbsp;</p><p>2. Review pages mentioned in the description field&nbsp;to find the observation.</p> |  | U9 |  |  | FINDING | [6 empty] | 116955
36625 | FINDING | User can select SIS CHARMS Secure Points as a Global Secure Parameter reference in Legacy SIS if Ovation Setup having both SIS CHARMS and Legacy SIS | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-06-08 07:37 | [11 empty] | Raciborski, Mikolaj AUTOSOL PSS WRSW | 2016-06-08 07:37 | [7 empty] | Saklani, Rajnish EMR SYSS PWS NOIDA | 2016-05-26 03:53 |  | <p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">User can select SIS CHARMS Secure Points&nbsp;for Global Secure Parameter reference in Legacy SIS, whereas Global Secure Parameter reference are used only for data transfer within different SDS Logic Solvers.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">In Input Point name under Property Editor of Global Secure Parameter reference, SIS CHARMS&nbsp;Secure parameter is appearing and user can select that.</span></p><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">This issue is specific to a system having Legacy SIS as well as SIS CHARMs.</span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | DB Server Drop100 win 2012 R2 with Ovation 3.6.0 U9 having Legacy SIS under Drop 23/73 and Drop27/77, CHARMS under Drop30/80 and Virtual CHARMS under Drop1/11 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Insert a new Control Sheet in any Control Module of any Legacy SIS Logic Solver.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Create an SIS&nbsp;logic having a global Secure parameter reference.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Click on Global Secure parameter reference algo and go to property editor and select Input point name.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">User can select SIS CHARMS Secure points from drop down.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Select the Secure Parameter point name&nbsp;created in SIS&nbsp;CHARMS</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Save the Control Sheet.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Error Message appeared as &quot;Invalid Global Secure Parameter reference&quot;.</span></li><li><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Please refer attachment for reference. In attachment D1_VCSLS3_CM1_SP1 and D1_VCSLS02_OUT2 point are secure parameter created in Virtual CHARMS and D30-CS01-LSDO2-OUTD point is Secure parameter created in CHARMS.</span></li></ol><p><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"><b><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">Observation:</span></b><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;"> Only these Secure Parameters which are configured in Legacy SIS logic Solver&nbsp;under different SDS should appear for Global Secure Parameter&nbsp;in Global Secure parameter input point name in Property Editor.</span><font face="Times New Roman" size=3> </font></span></p><p><font face="Times New Roman" size=3> </font><br></p> |  | U9 |  |  | FINDING | [6 empty] | 98390
36626 | FINDING | When mouse is hovered around an error on CSLS the message mentions SDS instead of LSN | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:10 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:10 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 05:02 |  | When mouse is hovered around an error related to communication on CSLS the message mentions SDS instead of LSN. THe message states:<div>&nbsp;&quot;<i>There is no communication with SDS device. Unable to determine status of diagnostic attribute</i>&quot;</div><div>SDS is not valid for SIS CHARMS, it should mention about LSN.&nbsp;</div><div>(Please refer to attached screenshot)<br></div><div><div><br></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | Ovation 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Hover Mouse around a Communication error message in CSLS.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98165
36628 | FINDING | Data displayed for CHARMS Controller needs to be modified in SIS Diagnostics tool | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:17 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:17 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 06:17 |  | Data displayed for CHARMS Controller needs to be modified in SIS Diagnostics tool.<div>For CSLS Controller the data for secondary Network is not available in the SIS diagnostics tool.<br><div>For CSLS Controller there is no need for multi cast IP as it used in SIS Legacy, hence this data should not appear.</div></div><div>(Please refer to the attached screenshot)</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Browse the CHARMS controller in the SIS diagnostics tool in check the above mentioned data.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98178
36629 | FINDING | License manager mentions 'Commuter License Allowed' instead of 'Computer License Allowed' | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | McMaster, James External Artech | 2016-05-26 07:19 | [11 empty] | McMaster, James External Artech | 2016-05-26 07:19 |  |  |  | 2016-05-26 07:19 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-05-26 06:22 |  | License manager mentions 'Commuter License Allowed' instead of 'Computer License Allowed' |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0_U9 |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | It is supposed to be &quot;Commuter&quot;.&nbsp; This is for a potential feature where someone could sign out a&nbsp;license and use offline. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1) Open License Manager</p><p>2) Click on Feature</p><p><br></p><p>Observation: </p><p>Right pane displays 'Commuter License Allowed'.</p><p><br></p><p>Please find the screenshot attached.</p> |  | U9 |  |  | FINDING | [6 empty] | 97818
36631 | FINDING | Partner redundant CHARMS disappears from SIS Diagnostics tool when removed from the slot as it is "undefined" in Ovation Developer Studio | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:17 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:17 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-26 06:53 |  | Partner redundant CHARMS disappears from SIS Diagnostics tool when removed from the slot as it is &quot;undefined&quot; in Ovation Developer Studio.<div>There is no option define the Partner redundant CHARMS in Ovation Developer studio. The Partner CHARMS appears as undefined in SIS Diagnostics tool. Also it disappears from SIS Diagnostics tool when the charms is removed from slot physically.</div><div>The data for Partner Redundant CHARMS should not disappear from SIS Diagnostics tool when it is removed from slot as same behaviour is not Observed after removing Primary Redundant CHARMS from the slot.</div><div>(Please refer to the attached screenshots) &nbsp;</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  | Ovation 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Configure redundant CHARMS.</li><li>Browse the CHARMS data in SIS Diagnostics tool.</li><li>Remove the Partner redundant Charms from the slot.</li><li>Browse the CHARMS data in SIS Diagnostics tool.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98177
36636 | FINDING | Test case 5.1.15 (c, d) need to be removed from the CB_SVTP_rev_2.8.doc SVTP. | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-05-26 22:57 | [11 empty] | USPITTFSService | 2016-05-26 22:57 | [7 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-05-26 22:57 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri size=3>Test case 5.1.15 (c, d) need to be removed from the CB_SVTP_rev_2.8.doc SVTP because</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><font face=Calibri><span style=""><font size=3>&nbsp;</font></span><font size=3>Both test cases are belonging to graphics and this SVTP belong to control Builder.</font></font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U9 |  |  | FINDING | [6 empty] | 97882
36642 | FINDING | Icon for CSLS is same as icon for SIS Legacy Logic Solver in SIS Diagnostics tool | Zochowski, Michal AUTOSOL DX WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:16 | [11 empty] | Zochowski, Michal AUTOSOL DX WRSW | 2016-06-02 13:16 | [7 empty] | Saini, Shiva AUTOSOL PWS NOIDA | 2016-05-27 04:53 |  | Icon for CSLS is same as icon for SIS Legacy Logic Solver in SIS Diagnostics tool.<div>The Icon for CSLS should be different.</div><div>(Please refer to the attached screenshot)</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0 + U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Saini, Shiva AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 5 - Enhancement Request | [5 empty] | <ol><li>Browse SIS Legacy solver and CSLS in SIS Diagnostics tool</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 98175
36643 | FINDING | AMS DM13.0 does not support HART Analog Input & HART Two-state Output for Legacy SIS. | Capani, Innocenzo AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-05-27 10:20 | [11 empty] | USPITTFSService | 2016-05-27 10:20 | [7 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-27 06:05 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">AMS DM13.0 does not support HART Analog Input &amp; HART Two-state Output for Legacy SIS.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Configured <span style="color:black;">HART Analog Input &amp; HART Two-state Output in Legacy SIS (D27_SDS01_LS02) device.</span></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">HART device are: SIS HART Temperature transmitter 3144P, HART Valve DVC 6200.<br style=""> <br style=""> </span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="font-family:&quot;Times New Roman&quot;,&quot;serif&quot;;font-size:12pt;">Observation- On AMS, upon performing Rebuild Hierarchy, we can see the SIS Losic Solver and specific slot no. where the HART devices are configured but we cannot see or scan devices. No error appeared. Screenshot of AMS window is attached.<br style=""> <br style=""> </span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Hutchison, Steven EMR SYSS PWS PITT | Raciborski, Mikolaj AUTOSOL PSS WRSW | Capani, Innocenzo AUTOSOL PWS PITT |  |  | Implementation |  |  | AMS13.0+Hot Fix, DBS Drop100 (Ws12R2), Ov3.6.0_U9,SIS Controller drop 27/77 (OCR400), Logic Solver (1508),SIS HART Temperature transmitter 3144P, HART Valve DVC 6200 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | U9 |  |  | FINDING | [6 empty] | 97940
36644 | FINDING | In Legacy SIS , the SIS Sensor Alarm (ALRM) sheet only working with Control Module04 in Logic Solver (1508). | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-06-01 23:46 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-06-01 23:46 |  |  |  | 2016-05-27 09:21 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-27 06:13 |  | In Legacy SIS, the SIS Sensor Alarm (ALRM) sheet only working with Control Module04 in Logic Solver (1508). |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW |  |  |  |  | Implementation |  |  | DBS drop100 (Ws12R2), SIS Controller Drop27/77 (OCR400G02),Logic Solver (1508) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | <p>Works as Design</p><p>Only one ALRM sheet is permitted per logic solver.&nbsp; It is irrational to have more than on ALRM sheet per logic solver.</p><p>The last one found is processed.&nbsp; There was one in CM04, so CM01, CM02, and CM03 were ignored.</p><p><br></p><p>PP:05/02/2016-We have 1st created ALRM sheets in only CM01 but it is not working then deleted this ALRM sheet from CM01 then again created in CM02 but it is also not working.</p><p>Then at last created ALRM sheet in CM04 &amp; now it is working.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:rgb(31, 73, 125);">1. Inserted new control sheet on control module01 (D27-&gt;LS01-&gt;CM01).</span></p><p><span style="color:rgb(31, 73, 125);">2. </span><span style="color:rgb(31, 73, 125);">Given Sheet name is <b>Sensor_alarm</b> &amp; Sheet number is <b>ALRM</b>.</span></p><p><span style="color:rgb(31, 73, 125);">3. </span><span style="color:rgb(31, 73, 125);">Now sheet is opened successfully &amp; then Compiled the sheet successfully.</span></p><p><span style="color:rgb(31, 73, 125);">4. </span><span style="color:rgb(31, 73, 125);">Now Loaded the logics solver successfully.</span></p><p><span style="color:rgb(31, 73, 125);">5. </span><span style="color:rgb(31, 73, 125);">Opened the ALRM sheet in signal diagram &amp; it is open successfully.</span></p><p><span style="color:rgb(31, 73, 125);">6. <font face=Calibri>The opened sheet is blank. Please find attached snapshot.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);"><br></span></font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span><font size=3><font face=Calibri><b><span style="color:rgb(31, 73, 125);">Note</span></b><span style="color:rgb(31, 73, 125);">: Same above observation is also observed in Control Module02 &amp; Control Module 03.</span></font></font><font face="Times New Roman" size=3> </font></p> |  | U9 |  |  | FINDING | [6 empty] | 98110
36650 | FINDING | Description of SIS Events condition need to be modified for some Module Events in Online Help. | Maggu, Mukesh EMR SYSS PWS NOIDA | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:32 | [11 empty] | Maggu, Mukesh EMR SYSS PWS NOIDA | 2017-04-11 00:32 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2016-05-31 00:14 |  | <p>Description of SIS Events condition need to be modified for some Module Events in Online Help.</p> <p>Module Events listed under SIS Events Type give description of some of the Module Events common for LSAVTR and LSDVTR Algorithm. For some Events, LSAVR needs to be replaced with LSDVTR.</p> <p>Please see the attached screenshot as <em>SIS Event_DVTR.png</em></p> <p><em></em>&nbsp;</p> <p><em>Note: This section in Online Help is under SIS Events --&gt; SIS Events Types --&gt; Module Events</em></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ov3.6.0_U9 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Documentation | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | U9 |  |  | FINDING | [6 empty] | 111011
36651 | FINDING | Cb loader program run command needs some correction | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2017-06-19 06:18 | [11 empty] | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2017-06-19 06:18 | 76415 |  |  | 2017-06-19 06:18 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-31 01:48 |  | The command to run the Cb loader program is <span class=Apple-style-span style="font:/normal Arial;color:rgb(0, 0, 0);text-transform:none;text-indent:0px;letter-spacing:normal;word-spacing:0px;white-space:normal;border-collapse:separate;orphans:2;widows:2;"><span class=Apple-style-span style="text-align:left;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:13px;"><p class=listcontinue style="margin:6pt 0cm;padding:0pt;width:auto;height:auto;text-align:left;color:rgb(0, 0, 0);text-transform:none;line-height:normal;text-indent:0cm;letter-spacing:normal;clear:none;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:10pt;font-style:normal;font-variant:normal;text-decoration:none;word-spacing:normal;vertical-align:baseline;float:none;display:block;white-space:normal;background-color:inherit;"><strong>\Ovation\CtrlBldr\cbLoader catalog \OvPtSvr\&lt;system name of local data server&gt;\on-line while in manual it is printed as</strong></p><span class=Apple-style-span style="font:/normal Arial;color:rgb(0, 0, 0);text-transform:none;text-indent:0px;letter-spacing:normal;word-spacing:0px;white-space:normal;border-collapse:separate;orphans:2;widows:2;"><span class=Apple-style-span style="text-align:left;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:13px;"><p class=listcontinue style="margin:6pt 0cm;padding:0pt;width:auto;height:auto;text-align:left;color:rgb(0, 0, 0);text-transform:none;line-height:normal;text-indent:0cm;letter-spacing:normal;clear:none;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:10pt;font-style:normal;font-variant:normal;text-decoration:none;word-spacing:normal;vertical-align:baseline;float:none;display:block;white-space:normal;background-color:inherit;"><strong class=strong style="padding:0pt;color:rgb(0, 0, 0);font-family:Arial, verdana, arial, helvetica, sans-serif;font-weight:bold;vertical-align:baseline;display:inline;background-color:inherit;">\Ovation\CtrlBldr\cbLoader catalog \OvPtSvr\&lt;local remote alias name&gt;\on-line</strong></p><p class=listcontinue style="margin:6pt 0cm;padding:0pt;width:auto;height:auto;text-align:left;color:rgb(0, 0, 0);text-transform:none;line-height:normal;text-indent:0cm;letter-spacing:normal;clear:none;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:10pt;font-style:normal;font-variant:normal;text-decoration:none;word-spacing:normal;vertical-align:baseline;float:none;display:block;white-space:normal;background-color:inherit;"><br></p></span><p class=listcontinue style="margin:6pt 0cm;padding:0pt;width:auto;height:auto;text-align:left;color:rgb(0, 0, 0);text-transform:none;line-height:normal;text-indent:0cm;letter-spacing:normal;clear:none;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:10pt;font-style:normal;font-variant:normal;text-decoration:none;word-spacing:normal;vertical-align:baseline;float:none;display:block;white-space:normal;background-color:inherit;"><br></p></span><p class=listcontinue style="margin:6pt 0cm;padding:0pt;width:auto;height:auto;text-align:left;color:rgb(0, 0, 0);text-transform:none;line-height:normal;text-indent:0cm;letter-spacing:normal;clear:none;font-family:Arial, verdana, arial, helvetica, sans-serif;font-size:10pt;font-style:normal;font-variant:normal;text-decoration:none;word-spacing:normal;vertical-align:baseline;float:none;display:block;white-space:normal;background-color:inherit;"><br class=Apple-interchange-newline></p></span></span><br class=Apple-interchange-newline> | <p><br></p><p>AA (05-31-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 20.5.2</u> of the manual has been modified. The sentence&nbsp;modified is as follows:</p><p align=LEFT></p><p><br></p><font size=2><p><font face="Times New Roman" size=3></font></p><p style="margin:3pt 0in 3pt 0.25in;page-break-after:avoid;"><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">\Ovation\CtrlBldr\cbLoader catalog \OvPtSvr\&lt;</span></strong><b><span style="color:black;"><font face=Arial>system name of local data server</font></span><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">&gt;\on-line</span></strong></b></p><p><font face="Times New Roman" size=3></font></p></font><p><br></p><p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span><p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p><p><br></p><p><strong>The name of the pdf is OW360_80.pdf</strong></p> |  |  |  | 0 |  |  |  | LB-06/19/17:Verified on Ovation3.6.0_FP3_U1 and observed that the problem got fixed. | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Documentation | <p><br></p><p>AA (05-31-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 20.5.2</u> of the manual has been modified. The sentence&nbsp;modified is as follows:</p><p align=LEFT></p><p><br></p><font size=2><p><font face="Times New Roman" size=3></font></p><p style="margin:3pt 0in 3pt 0.25in;page-break-after:avoid;"><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">\Ovation\CtrlBldr\cbLoader catalog \OvPtSvr\&lt;</span></strong><b><span style="color:black;"><font face=Arial>system name of local data server</font></span><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">&gt;\on-line</span></strong></b></p><p><font face="Times New Roman" size=3></font></p></font><p><br></p><p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span><p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p><p><br></p><p><strong>The name of the pdf is OW360_80.pdf</strong></p><p><br></p><p><br></p><p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p><p>The updated manual is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP3/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OV360FP3U1 |  | <p>Ovation3.6.0_U9</p><p>Control builder Help - OW360_80</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p><br></p><p>AA (05-31-16): The sentence related to the Finding has been added to the Ovation Control Builder User Guide for 3.6.0 (OW360_80). <u>Topic 20.5.2</u> of the manual has been modified. The sentence&nbsp;modified is as follows:</p><p align=LEFT></p><p><br></p><font size=2><p><font face="Times New Roman" size=3> </font></p><p style="margin:3pt 0in 3pt 0.25in;page-break-after:avoid;"><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">\Ovation\CtrlBldr\cbLoader catalog \OvPtSvr\&lt;</span></strong><b><span style="color:black;"><font face=Arial>system name of local data server</font></span><strong><span style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">&gt;\on-line</span></strong></b></p><p><font face="Times New Roman" size=3> </font></p></font><p><br></p><p>This update will be available in the printed Ovation Control Builder User Guide for 3.6.0 (OW360_80). This will be visible in the Control Builder online help in the next release. The updated pdf is kept at :<u></u></p><span lang=EN></span><p><font size=3></font><a href="file://uspit-fp04/VAL/Tests/3.6.0/DOCS_for_Validation"><u><font color="#0000ff" size=3><font color="#0000ff" size=3><span lang=EN>\\uspit-fp04\VAL\Tests\3.6.0\DOCS_for_Validation</span></font></font></u></a></p><p><br></p><p><strong>The name of the pdf is OW360_80.pdf</strong></p><p><br></p><p><strong><br></strong></p><p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p><p>The updated manual (OW360_80V2) is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP3/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the Control builder Help - OW360_80 file and verify the Cb loader program run command .<p>Screenshot is also attached for your reference.</p> |  | U9 |  |  | FINDING | [6 empty] | 114515
36652 | FINDING | UNPACK16 algorithm PBPT pin can also connect RM,RN,DP points | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Casteel, Linda EMR SYSS PWS PITT | 2016-07-28 15:56 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2016-07-28 15:56 |  |  |  | 2016-07-28 15:56 |  |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | 2016-05-31 01:53 |  | <strong><font face=Arial size=2>User can also connect RM,RN,DP points to PBPT pin of UNPACK16 algorithm. but the help file shows that user can connect LP point&nbsp;on PBPT pin of Unpack16 algorithm.</font></strong> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Bush, Kirt T EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>Ovation3.6.0_U9</p><p>Control builder Help - OW360_80</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Documentation | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Baghel, Lekhraj Singh AUTOSOL PWS NOIDA | Validation |  | <p>AA (05-31-16): Reassigning this finding to Linda. The finding is related to the Standard Algorithm User Guide&nbsp; (OW360_R110).</p><p>LC 07/28/2016:&nbsp; Per the SME in Product Development, UNPACK16 only takes LP and DP record types as inputs (for PBPT parameter). A note was added to the manual stating this. Not mention of RM or RN will be given.</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | 1)Open the Control builder Help -&nbsp;Algorithm online help&nbsp;file and verify&nbsp;the UNPACK16 algorithm PBPT pin details&nbsp;.<p>Screenshot is also attached for your reference.</p> |  | U9 |  |  | FINDING | [6 empty] | 100433
36657 | FINDING | Legacy SIS (1508) documentation for LSDVC Algorithm Determining the value of PVD section needs to be updated. | Casteel, Linda EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Casteel, Linda EMR SYSS PWS PITT | 2017-04-07 14:14 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2017-04-07 14:14 |  |  |  | 2017-04-07 14:14 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-31 05:31 |  | Documentation for LSDVC Algorithm Determining the value of PVD section needs to be updated.<div>Current Documentation:</div><div><i>PVD normally gets its value from RDBK, if the quality of RDBK is Bad, PVD has the same value as OUT.</i><br></div><div><div>Needs to be Updated as:</div><div><em>PVD normally gets its value from RDBK, if the RDBK is not connected, PVD has the same value as OUT. </em></div><div><em>Please find attached snapshot of &quot;LSDVC_help.jpg&quot;.</em></div></div><div><div>Reason:</div><div>In the Delta V manual it is mentioned:</div></div><div><i>The status of PV_D is that of RDBK_IN_D unless its status is Bad NotConnected, in which case the status of PV_D is the same as OUT_D.</i><br></div><div>Ovation does not have Bad Not Connected Quality.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Jain, Swati EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT |  |  |  | Implementation |  |  | <p>SIS Controller 27//77 (OCR400G02), Logic Solver 02 (1508), DBS drop100 (WS12R2),&nbsp;HART Valve DVC&nbsp;6200, Ov3.6.0_U9, LSDVC Algorithms.<br></p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | LC 04/07/2017: Checked by Marek Konkol. Book republished. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Go to Determining the value of PVD section for LSDVC algorithm in the manual.</li><li>Check the above mentioned statement.</li></ol> |  | U9 |  |  | FINDING | [6 empty] | 110910
36658 | FINDING | In Legacy SIS (1508), HART Two-state Output used in LSDVC algorithms is showing BAD when OFCUR is set to 0 mA | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-03 13:45 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-03 13:45 | [7 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-05-31 05:34 |  | <p>In Legacy SIS (1508), HART Two-state Output used in LSDVC algorithms is showing BAD when OFCUR is set to 0 mA.</p><p>Please find attached snapshot of LSDVC_Output_BAD.jpg.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | Hutchison, Steven EMR SYSS PWS PITT |  |  | Implementation |  |  | SIS Controller 27//77 (OCR400G02), Logic Solver 02 (1508), DBS drop100 (WS12R2),&nbsp;HART Valve DVC&nbsp;6200, Ov3.6.0_U9 |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configured CH16 of Logic Solver (1508) as HART Two-state Output channel.</p><p>2. Created a new control sheet in control module 03 of logic Solver 02.</p><p>3.&nbsp;add &nbsp;LSDVC algorithm&nbsp;&amp; assign HART 2-state IO output channel as D27_SDS01LS02/CH16.</p><p>4. Connected outputs pins in LSDVC algorithms as required.</p><p>5. Loaded the Logic Solver &amp; then SIS Controller successfully.</p><p>6. Opened sheet in Signal diagram &amp; then&nbsp;click on&nbsp;advanced Tuning, now open SIS Tuning.</p><p>7. Changed OFCUR field from 4 mA to 0 mA.</p><p>8. it is observed that the LSDVC algorithms is showing BAD.</p><p><br></p><p><br></p> |  | U9 |  |  | FINDING | [6 empty] | 110602
36877 | FINDING | SPO 1.7.3, ISB 2.5.1, AMS 13.1.1, VL 13.1 not getting installed on a windows 10 operating system machine | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 11:43 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 11:43 |  |  |  | 2016-10-28 15:59 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-06-30 04:31 |  | <p>While installing SPO 1.7.3 on a windows 10 machine, install shield wizard&nbsp;gives an error as per the attached snapshot &quot;.Net3.5_3.jpg&quot;.</p><p><br></p><p>It has been observed that&nbsp;<strong>.NET Framework 3.5</strong> feature needs to be installed on&nbsp;a Windows10 machine before installing <strong>SPO 1.7.3</strong> Add-on software on the windows 10 operating system machine.</p><p><br></p><p>Please follow below mentioned steps to install .NET Framework 3.5 on a Windows 10 machine.</p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3><br></font></span></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>1. Insert Windows 10 OS installation media in the CD/DVD drive of the machine.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>2. Open command prompt window.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>3. Type the following line in the Command Prompt and press enter:&nbsp; </font></span></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;"><b><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>DISM /Online /Enable-Feature /FeatureName:NetFx3 /All /LimitAccess /Source:installationMediaDrive:\sources\sxs</font></span></b></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 0pt;"><font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);">Where</span><b><span style="color:rgb(31, 73, 125);"> installationMediaDrive </span></b><span style="color:rgb(31, 73, 125);">is the drive where your Windows 10 OS installation media resides.</span></font></font></p><p style="margin:0cm 0cm 0pt;"><font size=3><font face=Calibri><span style="color:rgb(31, 73, 125);">4. Please refer the attached snapshots.</span></font></font></p><p><br></p><p><br></p><p>IC 11/23/16&gt; per SK 11/23/16 email : </p><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>It has been observed that&nbsp;<strong><span style="font-family:&quot;Calibri&quot;,sans-serif;">.NET Framework 3.5</span></strong></font><font size=3> feature needs to be installed on&nbsp;a Windows10 machine before installing following Add-on Software:</font></span></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">SPO1.7.3 : reported through F# 36877</span></p></li><li style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">I.S.B 2.5.1 : &nbsp;No Finding reported, &nbsp;worked with workaround of F#36877</span></p></li><li style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">AMS 13.1.1 : No Finding reported, &nbsp;worked with workaround of F#36877</span></p></li><li style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">AMS VL 13.1 : No Finding reported, &nbsp;worked with workaround of F#36877</span></p></li></ol><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 8pt;"><span style="color:rgb(55, 96, 146);font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>&nbsp;</font></span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | <p>GEC Lab,</p><p>Drop 156 (OS: Windows 10)</p> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>IC 10/28/16&gt; added note to SPO 1.7.3 and Ov 3.6.0 DIRs.<br>IC 11/28/16&gt; added note to ISB 2.5.1 DIR. Adedd note to Ovation 3.6.0 DIR for AMS DM &amp; VL. </p><p><br></p> | 14 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Please follow the steps mentioned in Description box of this finding. |  | Win 10 |  |  | FINDING | [6 empty] | 105778
36894 | FINDING | Current Lumension 8.2.0.24 does not support drops loaded with Win 10 OS as client. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:18 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:18 |  |  |  | 2016-10-28 15:18 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2016-07-04 01:21 |  | <p>With the current installed version 8.2.0.24, we can't add a new client&nbsp;of Win 10 OS drop. It does not support Win 10.</p><p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;" class=MsoNormal><font size=3><font face=Calibri>&nbsp;For LAV clients installation on Windows 10 drops, please find below the steps we followed.</font></font></p><p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt;" class=MsoNormal><font size=3 face=Calibri>&nbsp;</font><span style=""><span style=""><font size=3 face=Calibri>1.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri><font size=3>Installed lmsetupx64.exe on the client drop#140 of Net#26 successfully.</font></font></p><p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;" class=MsoListParagraph><span style=""><span style=""><font size=3 face=Calibri>2.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font face=Calibri><font size=3>On the LAV server drop 47, open Lumension EMSS window-.Tools-&gt;Download Agent Installer-&gt;Agent –OS shows the lists of all OS available in which Windows 10 is not listed.</font></font></p><p><font size=3 face="Times New Roman"> </font></p><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;" class=MsoListParagraph><span style=""><span style=""><font size=3 face=Calibri>3.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span></span><font size=3><font face=Calibri>Please find enclosed the snapshot dai-lav-drop47.jpg.</font></font></p><p><font size=3 face="Times New Roman"> </font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Joshi, Parmesh EMR SYSS PWS NOIDA | Tripathi, Sandeep AUTOSOL PWS NOIDA | [7 empty] | Implementation |  |  | Win 10 |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | IC 9/15/16&gt; correct, LAV 8.2 does not support WIn 10. DIR.<br>IC 10/28/16 &gt; added note to the 3.6.0 DIR, Win 10 section. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p style="margin:0in 0in 0pt;" class=MsoNormal><font size=3><font face=Calibri> For LAV clients installation on Windows 10 drops, please find below the steps we followed.</font></font></p><p><font size=3 face="Times New Roman"></font></p><p style="margin:0in 0in 0pt;" class=MsoNormal><font size=3 face=Calibri> </font><span style=""><span style=""><font size=3 face=Calibri>1.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;"> </span></span></span><font face=Calibri><font size=3>Installed lmsetupx64.exe on the client drop#140 of Net#26 successfully.</font></font></p><p><font size=3 face="Times New Roman"></font></p><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;" class=MsoListParagraph><span style=""><span style=""><font size=3 face=Calibri>2.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;"> </span></span></span><font face=Calibri><font size=3>On the LAV server drop 47, open Lumension EMSS window-.Tools-&gt;Download Agent Installer-&gt;Agent –OS shows the lists of all OS available in which Windows 10 is not listed.</font></font></p><p><font size=3 face="Times New Roman"></font></p><p style="margin:0in 0in 0pt 0.5in;text-indent:-0.25in;" class=MsoListParagraph><span style=""><span style=""><font size=3 face=Calibri>3.</font><span style="font:7pt/normal &quot;Times New Roman&quot;;font-size-adjust:none;font-stretch:normal;"> </span></span></span><font size=3><font face=Calibri>Please find enclosed the snapshot dai-lav-drop47.jpg.</font></font></p><p><font size=3 face="Times New Roman"></font></p> |  | Win 10 |  |  | FINDING | [6 empty] | 104738
36895 | FINDING | Current Kaspersky10 SP1 (MR1) does not support drops loaded with Win 10 OS as client. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:15 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:15 |  |  |  | 2016-10-28 15:15 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-07-04 23:26 |  | <p>It has been observed that current Kaspersky 10 SP1 (MR1) antivirus client software can not be installed on a drop having Windows 10 operating system installed.</p><p><br></p><p>While installing Kaspersky 10 SP1 (MR1) antivirus client software on a Windows 10 machine it shows an error as &quot;<strong>This app can't run on this PC</strong> Kaspersky Endpoint Security doesn't work on this version of windows&quot;.</p><p><br></p><p>Please&nbsp;refer the attached snapshot &quot;<strong>KAV1.jpg</strong>&quot;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Foose, David A AUTOSOL PWS PITT | [7 empty] | Implementation |  |  | <p>Windows 10 machine,</p><p>Kaspersky 10SP1 (mr1) client software</p> |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>This is already covered in SDR 35532, Documentation, DIR and various other locations. Please consult before opening redundant findings/SDR.<br><br>IC 7/5/16 &gt; D Foose (above) is probably correct. Please leave this open until we double check DIR at release time. Thx.</p><p>IC 10/28/16 &gt; added note to Ov 3.6.0 DIR, WIn 10 section. </p> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1. Install Kaspersky 10&nbsp;SP1 (MR1) client software on a windows 10 machine as per the steps mentioned in CON_050 manual.</p><p>2. While installation of the Kaspersky 10 SP1 (MR1) client software it shows an error as &quot;<strong>This app can't run on this PC</strong> Kaspersky Endpoint Security doesn't work on this version of windows&quot;.</p><p>3. Please&nbsp;refer the attached snapshot &quot;<strong>KAV1.jpg</strong>&quot;</p> |  | Win 10 |  |  | FINDING | [6 empty] | 104737
36898 | FINDING | PWTTS - Error messages popup when connect Profibus device in Engineering tool | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Swartz, Mark EMR SYSS PWS PITT | 2017-06-26 11:55 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2017-06-26 11:55 |  |  |  | 2017-06-26 11:55 |  |  |  | Phan, Quang EMR ENT TECH AUS | 2016-07-05 09:58 |  | <p>When configure profibus device initially and try to connect device in Engineering tools, an error message popup stating:</p><p>&quot;Maximum number of servers registered for this device reached&quot;</p><p>Was able to connect device after retry.</p><p><br></p><p>On different occasion,&nbsp;randomly go in Engineering tool and try to connect device, different error message popup stating:</p><p>&quot;??? string resource no found ???&quot;</p><p>Retry will get the same error message</p><p><br></p><p>System infor:</p><p>Win Server 2012 R2 Std</p><p>DBS with Ovation 3.6.0 U9, AMS 13.0 build 288</p><p>OCR400 Controller</p><p>Simplex Profibus module</p><p>Device used: Control Techniques Unidrive M700 and Powerdrive F300 both support DPV0 and DPV1</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | DeLancey, Brian J. EMR SYSS PWS PITT | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | [6 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Other |  | The connection limit includes any active connections which may be via AMS Device Manager.&nbsp; | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | See attached for details |  | U9 |  |  | FINDING | [6 empty] | 114816
36901 | FINDING | PWTTS - Configure profibus device via Network scan method cause Developer Studio to freeze. | Swartz, Mark EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Phan, Quang EMR ENT TECH AUS | 2016-07-06 10:04 | [11 empty] | Phan, Quang EMR ENT TECH AUS | 2016-07-06 10:04 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-07-06 10:03 |  | Perform a Network Scan at port level on Profibus module and was able to see device. &nbsp;However, when attempt to create device, Developer Studio freezes. &nbsp;It will remain freeze until application is killed via Task Manager. &nbsp;See attached for details.<div><br></div><div>Add device via drag and drop method is working fine. &nbsp;However, it will run into issue with communication lost as filed in Finding# 36898</div><div><br></div><div><div>System info:</div><div>Win Server 2012 R2 Std</div><div>DBS with Ovation 3.6.0 U9, AMS 13.0 build 288</div><div>OCR400 Controller</div><div>Simplex Profibus module</div><div>Device used: Control Techniques owerdrive F300 both support DPV0 and DPV1</div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | DeLancey, Brian J. EMR SYSS PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Perform a network scan on Profibus segment and click create device when device shows up. |  | U9 |  |  | FINDING | [6 empty] | 99295
36927 | FINDING | VCH support (WRTap Driver) for Win10 is not available. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:58 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-10-28 15:58 | OW360_57_V2 |  |  | 2016-10-28 15:58 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-07-11 05:14 |  | <p>VCH support for Windows 10 is not available.</p> <p>Ovation 3.6.0 DVD contains WRTap driver installer for Windows7, Windows Server 2008 and Windows Server 2012 (64bit version of all of these OS), but WRTap driver installer is not available for Windows 10.</p> | <p>AA (05-08-2016): I have made the required changes to the Virtual Controller User Guide for Ovation 3.6.0 (OW360_57_V2). <span style="background:yellow;font-size:10pt;"><font color="#000080" face="Times New Roman"><strong>The file location for Windows 10 OS has been specified along with Windows Server 2012.&nbsp;</strong></font></span>Topic 4.4.2 has been modified.</p><p>The updated VCH user guide is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/Win10/Docs">\\uspit-fp04\VAL\Tests\3.6.0\Win10\Docs</a></p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Documentation | <p>AA (05-08-2016): I have made the required changes to the Virtual Controller User Guide for Ovation 3.6.0 (OW360_57_V2). <span style="background:yellow;font-size:10pt;"><font color="#000080" face="Times New Roman"><strong>The file location for Windows 10 OS has been specified along with Windows Server 2012.&nbsp;</strong></font></span>Topic 4.4.2 has been modified.</p><p>The updated VCH user guide is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/Win10/Docs">\\uspit-fp04\VAL\Tests\3.6.0\Win10\Docs</a></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Lal, Ramesh External | Silvaggio, Gregory W EMR SYSS PWS PITT | [5 empty] | Implementation | OW360_57_V2 |  | <p>Drop171, Windows 10 64 Bit</p> <p>Ovation 3.6.0 Net#36</p> |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Documentation | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>AA (03-08-2016): Reassigning the finding. I will be&nbsp;working on the VCH User Manual for Windows 10 WRTap driver.&nbsp;</p> <p><br></p> <p>AA (05-08-2016): I have made the required changes to the Virtual Controller User Guide for Ovation 3.6.0 (OW360_57_V2). I have attached an email that Greg sent regarding the WRTap driver installation on Windows 10, based on this email I have made the changes. The updated VCH user guide is kept at: <a href="file://uspit-fp04/VAL/Tests/3.6.0/Win10/Docs">\\uspit-fp04\VAL\Tests\3.6.0\Win10\Docs</a></p> <p><br></p> <p><span style="background:yellow;font-size:10pt;"><font color="#000080" face="Times New Roman"><strong>The file location for Windows 10 OS has been specified along with Windows Server 2012.&nbsp;</strong></font></span>Topic 4.4.2 has been modified as follows:</p> <p><br></p> <p><font face="Times New Roman" size=3><br></font></p> <p style="margin:6pt 0in;"><span style="background:yellow;"><font face=Arial size=2>Use the Ovation Installation DVD to install the WRTap driver. The file location is as follows:</font></span></p> <ul> <li><font face="Times New Roman" size=3></font><span style="background:yellow;">For Windows Server 2012 or Windows 10 operating system, the location is </span><span style="background:yellow;"><strong><font color="#000080" face="Times New Roman">&lt;DVD&gt;\WRTapDriver\Serv2012</font></strong></span></li> <li><font face="Times New Roman" size=3></font><span style="background:yellow;font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;">For Windows Server 2008 or Windows 7 operating system, the location is </span><span><span style="background:yellow;font-size:10pt;"><strong><font color="#000080" face="Times New Roman">&lt;DVD&gt;\WRTapDriver\Win7_Serv200</font></strong></span></span></li></ul> <p><span style="background:yellow;font-size:10pt;"><font color="#000080" face="Times New Roman"><strong></strong></font></span>&nbsp;</p> <p><span style="background:yellow;font-size:10pt;"><font color="#000080" face="Times New Roman"><font color="#1e1e1e" face="Segoe UI" style="background-color:rgb(255, 255, 255);">ASG (Sept-16-2016): Verified document (placed at <a href="file://\\uspit-fp04\VAL\Tests\3.6.0\Win10\Docs">\\uspit-fp04\VAL\Tests\3.6.0\Win10\Docs</a>) contains location of WRTap driver for Windows 10, hence closing the finding.</font></font></span></p><font color="#000080" face="Times New Roman"> <p><strong><br></strong></p></font>IC 10/28/16&gt; added note to Ov 3.6.0 DIR, closed finding. | 18 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | Win 10 |  |  | FINDING | [6 empty] | 104739
37098 | FINDING | TRVP and TRVPTUNE algorithms need merged into 3.6.0 | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-07-29 09:10 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-07-29 09:10 |  |  |  | 2016-07-29 09:10 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-07-29 08:17 |  | closing finding because an sdr is more appropriate. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | 3.6.0_U9 |  |  | FINDING | [6 empty] | 100465
37143 | FINDING | OCR1100 Controller Uses Hard-Coded 100Mb/Full for N2 port | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-08-03 06:57 | [11 empty] | USPITTFSService | 2016-08-03 06:57 | [7 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-08-03 06:57 |  | OCR1100 Controller Uses Hard-Coded 100Mb/Full for N2 port, however it should use the value contained in the flags field contained in &quot;etc/hostinfo.1&quot;. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | 3.6.0 |  |  | FINDING | [6 empty] | 100642
37225 | FINDING | G04 OCR1100 on OV360 doesnot respond after first download and reboot | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 7 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-10-19 22:51 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-10-19 22:51 | 69712 |  |  | 2016-08-25 06:04 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-08-09 05:51 |  | <p>OCR1100 G04 module&nbsp;doesnot respond after first download and reboot. </p> <p>Details in steps to re-create tab.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA360-002-0816 |  | <p>Ovation 3.6.0;</p> <p>OVA360-002-0718;</p> <p>OCR1100 - G04;</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | PS: 25AUG2016: The issue reported is confirmed to be fixed. Hence finding state is changed to Closed. | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">Drop36/86 is an OCR1100-G01 controller on Ovation 3.6.0(running status verified to be healthy)</span></span></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">OVA360-002-0718 patch is installed on DBS Drop100 (Net#36)</span></span></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">Now the controller module is changed to G04(Baytrail).</span></span></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">&nbsp;&nbsp;&nbsp; </span></span></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000"><font size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1&gt;<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp; </span></span></span><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;">Changed Drop36 to G04 -&gt; Changed the MAC details-&gt; Inserted a clear 1GB Flash-&gt; Power ON controller.</span></font></font></p> <p class=MsoListParagraph style="MARGIN:0cm 0cm 0pt 36pt;TEXT-INDENT:-18pt;"><font color="#000000"><font size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">2&gt;<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp; <font size=3 face=Cambria>Ovation e</font></span></span></span><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;">rror log, logs entries for the new details of G04 module;</span></font></font></p> <p class=MsoListParagraph style="MARGIN:0cm 0cm 0pt 36pt;TEXT-INDENT:-18pt;"><font color="#000000"><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"></span></font><font color="#000000"><font size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">3&gt;<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp; </span></span></span><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;">After successfull download of Drop36&nbsp;; Hard boot controller.<b><i></i></b></span></font></font></p> <p class=MsoListParagraph style="MARGIN:0cm 0cm 0pt 36pt;TEXT-INDENT:-18pt;"><font color="#000000"><font size=3><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><span style="">4&gt;<span style="FONT:7pt &quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp; </span></span></span><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;">Here after controller drop reboots; communication is lost after approx. 6-7pings.</span></font></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><b><i><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><font color="#000000" size=3>&nbsp;Step wise snapshots are attached for reference.</font></span></i></b></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><span style="FONT-FAMILY:&quot;Cambria&quot;,&quot;serif&quot;;"><font color="#000000" size=3>&nbsp;This is re-created on both networks on Ovation 3.6.0 (Net#36 and Net#26)</font></span></p> |  | OVA360002-0718 |  |  | FINDING | [6 empty] | 104182
37236 | FINDING | Group Policies are not getting Updated on Win10 EWS for Hardened Network. | Thirunavukkarasu, Utthandi EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-09-28 14:50 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-09-28 14:50 |  |  |  | 2016-09-28 14:50 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2016-08-10 03:08 |  | <p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Group policy update (gpupdate /force) is not running on Win10 machine in&nbsp;hardened network.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Microsoft has an issue that Windows 10 Hardens the UNC paths to the 'SYSVOL' &amp; 'NETLOGON' by default with no setting in the registry. There is a workaround to Disable the UNC hardening until the hotfix is released by Microsoft.</span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><strong>Workaround:</strong></span></p><p>To Disable the UNC hardening for the SYSVOL and NETLOGON, it is required to run these commands </p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><p><br></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">%COMSPEC% /C reg add HKEY_LOCAL_MACHINE\SOFTWARE\Policies\Microsoft\Windows\NetworkProvider\HardenedPaths /v &quot;<a><font color="#0000ff">\\*\SYSVOL</font></a>&quot; /d &quot;RequireMutualAuthentication=0&quot; /t REG_SZ</span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">%COMSPEC% /C reg add HKEY_LOCAL_MACHINE\SOFTWARE\Policies\Microsoft\Windows\NetworkProvider\HardenedPaths /v &quot;<a><font color="#0000ff">\\*\NETLOGON</font></a>&quot; /d &quot;RequireMutualAuthentication=0&quot; /t REG_SZ</span></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;">After these commands, Group Policies will be updated.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><font face="Times New Roman" size=3><strong> </strong>Note: This information needs to be added&nbsp;in the&nbsp;DIR for a Win10 hardened network.</font></p></span><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software | <p>From SK 9/23/16 email: </p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>Did following steps:</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);"><font face=Calibri size=3>&nbsp;</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(31, 73, 125);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);">Deleted reg keys in following location for Win10 clients on which workaround was done (HKEY_LOCAL_MACHINE\SOFTWARE\Policies\Microsoft\Windows\NetworkProvider\HardenedPaths):</span></p><ol style="list-style-type:lower-alpha;"><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);"><a><span style="color:rgb(31, 73, 125);text-decoration:none;">\\*\SYSVOL</span></a></span></p></li><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);"><a><span style="color:rgb(31, 73, 125);text-decoration:none;">\\*\NETLOGON</span></a> </span></p></li></ol></li><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);">After deleting Registry entry, Rebooted those Win10 machines.</span></p></li><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);">Without Sept patch on DBS +DCdrop220(Servr 2012 R2), &nbsp;gpupdate /force fails on &nbsp;Win10 drops.</span></p></li><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);">Installed &nbsp;patches for Sept 2016 on DBS+DC drop220(attached are the list of Sept patch on DBS+DCdrop220).</span></p></li><li style="color:rgb(31, 73, 125);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:rgb(31, 73, 125);">Running Gpupdate /force on Win 10 drop &nbsp;succeeds. </span></p></li></ol><p><font face="Times New Roman" size=3> <br></font></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Kakroo, Tanisha EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | IC 9/28/16 &gt; per Dev emails, KB3161561 casues the issue. MS Sept 2016 security patch resolves the issues.<br>Val confirmed this to be the case on 9/23/16 with Dev approval. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | Win10 |  |  | FINDING | [6 empty] | 103343
37282 | FINDING | ELC.1.3.0 Protocol Analyzer tool & GPADCS OPC config editor tool is not opening on Win10 machine. | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-23 09:07 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-23 09:07 |  |  |  | 2016-10-28 16:11 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-08-16 13:06 |  | <p>It has been observed that Protocol Analyzer Tool of ELC 1.3.0 software does not open on Win10 systems and gives Microsoft .NET error. (please refer attached snapshot for more details)</p><p><br></p><p>However, on installing .NET Framework 3.5 (as per below steps) on Win10 system, ELC.1.3 protocol analyzer tool can be accessed:<br>1. Insert Windows 10 OS installation media in the CD/DVD drive of the machine.<br>2. Open command prompt window.<br>3. Type the following line in the Command Prompt and press enter:<br><strong>DISM /Online /Enable-Feature /FeatureName:NetFx3 /All /LimitAccess /Source:installationMediaDrive:\sources\sxs</strong><br>Where installationMediaDrive is the drive where Windows 10 OS installation media resides.<br>4. After this command executes successfully .Net Framework3.5 feature will get enabled on that machine.</p><p><br></p><p>IC 11/23/16&gt; this issue also occurred with GPADCS OPC per SK email: <font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Opening GPADCS OPC config editor tool also gave same error as in F#37282 :<br></font></span><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>1) GPADCS OPC config&nbsp; editor &nbsp;Tool: No Finding reported, &nbsp;worked with workaround F#37282.</font></span></p><p><font face="Times New Roman" size=3> </font><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Windows 10 Operating System<br>ELC1.3.0<br>Ovation 3.6.0<br>Drop127 (EWS) |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | IC 10/28/16 &gt; added note to ELC 1.3.0 and Ov 3.6.0 DIRs. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1. Loaded the ELC 1.3.0 software on drop127 (EWS- OS: Win10)<br>2. Opened the Protocol Analyzer tool from start menu and Microsoft .NET error appeared. |  | Win 10 |  |  | FINDING | [6 empty] | 105679
37350 | FINDING | A start delay is required to be set for GPADCS Service for the GPADCS machine to reboot narmally | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-22 15:15 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-22 15:15 |  |  |  | 2016-11-22 15:15 |  |  |  | Lal, Ramesh External | 2016-08-24 03:20 |  | <p><font face="Times New Roman" size=3> If Data Agent is being used by GPADCS a start-delay (typically 300 ms )is required to be set for GPADCS Service in order for the machine to reboot normally,&nbsp; This is because w<font size=2>hen GPADCS first starts in ‘Run’ mode, it tries to connect to the Data Agent source <span lang=EN-US style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:10pt;">Therefore, giving the GPADCS service a delay allows any Data Agent, Ovation, or other service that GPADCS depends upon, enough time to start first before GPADCS starts itself.</span></font></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Add-Ons/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Add-Ons | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Lal, Ramesh External | Validation |  | <p>IC 11/22/16&gt; per Ron Frencho 8/22/16 email, WAD:<font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,sans-serif;"><font size=3>The user’s guide addresses this issue so I believe that we can mark this issue Works as Designed (WAD):<br></font></span><b><span style="font-size:11.5pt;"><font face="Times New Roman">5.4 Specifying a service start-up delay <br></font></span></b><span style="font-size:10pt;"><font face="Times New Roman">The Start-up delay is primarily designed for when the computer is rebooted and the GPADCS service first begins executing. When GPADCS first starts in ‘Run’ mode, it tries to connect to the Data Agent source. <br></font></span><span style="font-size:10pt;"><font face="Times New Roman">A common data agent is OPC. OPC is also a Windows service. There are no interdependencies between the OPC service and the GPADCS service. The reason for this is simple: OPC may not be the Data Agent. Another Data Agent may be being used, such as Remserver or PI. <br></font></span><span style="font-size:10pt;"><font face=Calibri>Therefore, giving the GPADCS service a delay allows any Data Agent, Ovation, or other service that GPADCS depends upon, enough time to start first before GPADCS starts itself. In most cases, a delay of 60 seconds is sufficient.</font></span></p><p><font face="Times New Roman" size=3> </font><br><br></p><p><br></p><p><br></p><p><br></p><p><br></p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | Win10 |  |  | FINDING | [6 empty] | 105627
37357 | FINDING | G04 OCR1100 controller details are not visible in Controller Diagnostics | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2016-10-21 00:51 | [11 empty] | Lal, Ramesh External | 2016-10-21 00:51 |  |  |  | 2016-10-03 06:17 |  |  |  | Lal, Ramesh External | 2016-08-24 23:31 |  | <p>OCR1100-G04 is configured as Primary Controller (Drop24) and OCR1100-G01 is configured as Backup Controller (Drop74). When OCR1100-G01 (Drop74) is in control the&nbsp;Controller Diagnostics shows&nbsp; details of Drop74 only, there are no data for&nbsp;&nbsp;OCR1100-G04&nbsp; (Drop24). Similarly, when OCR1100-G04 (Drop24) is in control then also there are no details for Drop24.</p><p>Please refer attached snapshots for two scenarios: 1. Drop24 in Control, 2. Drop24 in backup</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360002-19Sept |  | OCR1100 G04/OCR1100 G01&nbsp;Controllers |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure OCR1100-G04&nbsp; as Primary Controller (Drop24)</p><p>2.&nbsp;Configure OCR1100-G01 as Backup Controller (Drop74). </p><p>3. Open Controller Diagnostics keeping Drop24 in control. View details in Controller Diagnostics</p><p>4. Open Controller Diagnostics keeping Drop24 in backup. View details in Controller Diagnostics</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 104290
37392 | FINDING | Universal Restore of Windows10 machine to another model (from Dell 9020 to Dell 9010) is not possible since full support for 64Bit Windows10 not available for Dell 9010 | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-09-26 15:52 | [11 empty] | USPITTFSService | 2016-09-26 15:52 |  |  |  | 2016-09-26 15:51 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-08-30 04:53 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000">Universal restore of Windows10 machine to different model (from Dell 9020 to Dell 9010) is not successful because add-on NIC card (Broadcom netxtreme gigabit ethernet) is not getting detected due to non availability of drivers.</font></font></font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | Costlow, Kim EMR SYSS PWS PITT | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Singhal, Harshita AUTOSOL PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | Prasad, Parmatma EMR SYSS PWS NOIDA |  |  | Implementation |  |  | EWS (Dell 9020 to Dell 9010) on Ovation 3.6.0 |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | IC 9/26/16&gt; since the 9010 Broadcom NIC does not reliably appear after installing Windows 10,&nbsp;we will recommend in the 3.6.0 DIR that the 9010 NOT be used with the Windows 10 OS. &nbsp; | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000">Performed following steps with observations as mentioned:</font></font></font></span></p> <ol> <li> <div class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000"><span style=""><font size=3><font face=Calibri><font color="#000000">In Device Manager, Broadcom NIC is not displayed (neither as installed device nor as device without drivers). </font></font></font></span>Used Dell 9010 Drivers DVD to update drivers, but Broadcom NIC does not appear in Network Adaptors list.</font></font></font></span></div></li> <li> <div class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000">Downloaded drivers from Dell website for Dell 9010 machine by entering its Service Tag number of the machine and installed&nbsp;them on machine, but still Broadcom NIC does not come up (the drivers are for 64 bit version of Windows 7, Windows 10 drivers are not available).</font></font></font></span></div></li> <li> <div class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000">Downloaded “Dell Command ¦ Deploy OptiPlex 9010 Windows 10 Driver Pack” from below link, but it has Broadcom NIC drivers for 32bit version of Windows10 and not for 64 bit Windows10:<br><a href="http://www.dell.com/support/home/us/en/04/Drivers/DriversDetails?driverId=RD5G1">http://www.dell.com/support/home/us/en/04/Drivers/DriversDetails?driverId=RD5G1</a></font></font></font></span></div></li> <li> <div class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style=""><font size=3><font face=Calibri><font color="#000000">Tried by formatting the 9010 machine and installed only Windows10 on it. Broadcom NIC does not come up even after updating drivers as mentioned in above steps.</font></font></font></span></div></li></ol> | EPM Validation | Win 10 |  |  | FINDING | [6 empty] | 103121
37415 | FINDING | Windows 10 Virtual Controller Host becomes unresponsive after installing services | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-10-31 08:19 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-10-31 08:19 |  |  |  | 2016-10-31 08:19 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-09-01 09:36 |  | <p>On a Windows 10 2016 machine, the procedure was followed to configure a VCH.&nbsp; The wrtap driver was installed.&nbsp; Ovation was installed.&nbsp; At this point, network connectivity was fine. The VCH was able to be downloaded and loaded, drop could be pinged, etc.&nbsp; The database was distributing fine.&nbsp; </p><p>We ran wrtap64.bat to install the services. After reboot, the VCH lost network connectivity. Download, load, ping, etc all failed. </p><p>We removed Ovation and the wrtap driver and reinstalled again to verify&nbsp;proper procedure.&nbsp; The same issue arose. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0 on Windows 10 2016 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | With Windows 10 and 2012, the Microsoft bridge is inheriting the MAC address from the&nbsp;wrtap driver rather than the physical NIC. When there are multiple VCH machines on the same network, this creates the problem as there are now duplicate MAC address on the network. The documentation has been updated to instruct the installer to manually configure the MAC address of the wrtap device to match the MAC address of the physical NIC. This ensures that the VCH machines will have unique MAC addresses across the network. | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Configure a VCH on Windows 10 3.6.0. |  | Win 10 |  |  | FINDING | [6 empty] | 104753
37467 | FINDING | OHI connection failover recovery not working properly on Windows 10 Operating system | Capani, Innocenzo AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-09-28 13:22 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-09-28 13:22 |  |  |  | 2016-09-28 13:22 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-09-05 03:31 |  | <p>While performing&nbsp;Test Case 5.7.1.4 (OHI connection failover recovery)&nbsp;of SVTP&nbsp;<strong>&quot;<span lang=EN-US style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;-ms-layout-grid-mode:line;">3.6.0_WIN10_SystemTests_SVTP_rev2.G&quot;, </span></strong><span lang=EN-US style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;-ms-layout-grid-mode:line;">It has been observed that OHI driver (on Win10 OS) is not working properly in below mentioned scenarios.</span></p><ol><li><span lang=EN-US style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;-ms-layout-grid-mode:line;">If EWS system (Win10 OS) is rebooted while OHI2 cable is connected and OHI1 cable is removed, Then after reboot Ovation database&nbsp;did not&nbsp;distribute to 100% and Ovation Applications did not work properly. This Scenario can be recreated in 4 out of 5 times. Please refer the attached excel sheet (refer s.no. 6 &amp; 7)&nbsp;and snapshot for details.</span></li><li><span lang=EN-US style="font-family:&quot;Arial&quot;,&quot;sans-serif&quot;;font-size:10pt;-ms-layout-grid-mode:line;">If EWS system (Win10 OS) is rebooted while both OHI1 and OHI2 cables are not connected. Then after reboot if any of the OHI1 or OHI2 cables&nbsp;connected, system did not comes on domain and Ovation database did not distribute to 100%. Please refer attached excel sheet (refer s.no. 10,13,14)&nbsp;for details.&nbsp;</span></li></ol><p>OHI1 Ethernet Adapter- Intel (R) Ethernet Connection I217-LM</p><p>OHI2 Ethernet Adapter- Broadcom NetXtreme Gigabit Ethernet</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Garg, Amit AUTOSOL PWS NOIDA | [6 empty] | Implementation |  |  | EWS Drop158, Windows 10 Operating system, OHI driver for Win10 |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>Please&nbsp;disable the following on Backup NIC also and then retest.</p><p><br></p><p>IC 9/28/16 &gt; issue tracked as SDR #37648. Fix is planned in OVA360009. </p><p><br></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 8pt;"><font face=Arial size=3>Modify the settings on the primary NIC. From the Network Connections page open the status for the </font><a><font face=Arial size=3>primary NIC </font></a><span style="line-height:107%;font-size:8pt;"><a name=_msoanchor_1 id=_anchor_1><font face=Arial>[SK1]</font></a><span><font face=Arial>&nbsp;</font></span></span><font face=Arial size=3>and click Properties. Click the Configure button under the NIC name. Click the Advanced tab. In the list of properties, find all of the following or anything that might be equivalent:</font></p><p><font face="Times New Roman" size=3> <br></font></p><ul style="list-style-type:disc;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">ARP offload</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">IPv4 checksum offload</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">Large Send offload (IPv4)</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">Large Send offload (IPv6)</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">NS offload</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">TCP checksum offload (IPv4)</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">TCP checksum offload (IPv6)</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">UDP checksum offload (IPv4)</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">UDP checksum offload (IPv6)</p><p style="color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:8pt;">Select and disable each of them.</p></li></ul><p><font face="Times New Roman" size=3> ST(09/07/2016): Above settings have already done at the time of OHI driver installation. To cross check, Again checked these settings for Primary NIC which are as per your suggestions mentioned above, but issue is still the same.<br></font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3>The secondary NIC should have no services or protocols bound to it, only Ovation Highwy Interface. Please check this. To change use OHI Utility to remove secondary NIC from the configuration. Use the network control panel applet to remove all bindings except the Ovation Highway Interface from the secondary NIC Use OHI Utility to add the secondary NIC to the configuration.</font></p><p><font face="Times New Roman" size=3><br></font></p><p><font face="Times New Roman" size=3>ST (09/09/2016): As part of OHI installation, we have already unchecked all the bindings except Ovation Highway Interface from the OHI2. Please find the attached remote login details for further investigation.</font></p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><p><font face="Times New Roman" size=3> <br></font></p> | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | To reproduce the scenario please follow steps as per attached Excel sheet. |  | Win 10 |  |  | FINDING | [6 empty] | 103322
37471 | FINDING | By default OHI2 comes in control after rebooted drop comes up. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Burgoon, Frank AUTOSOL PWS PITT | 2016-09-06 09:30 | [11 empty] | Burgoon, Frank AUTOSOL PWS PITT | 2016-09-06 09:30 |  |  |  | 2016-09-06 09:30 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-09-05 04:25 |  | <p>Whenever the drop is rebooted with both primary and secondary cables plugged in,&nbsp;secondary OHI i.e.&nbsp;OHI2 comes in control in following cases:</p><p>Case 1. Both cables plugged in and OHI1 is in control and OHI2 in backup&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><p>Case 2. Both cables plugged in and OHI2 is in control and OHI1 in backup&nbsp;&nbsp;&nbsp;</p><p>Its inferred that by default secondary OHI comes in control&nbsp;whatever may be the case after reboot.&nbsp;&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Tripathi, Sandeep AUTOSOL PWS NOIDA | [6 empty] | Implementation |  |  | <font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><table width=122 style="width:92pt;border-collapse:collapse;" border=0 cellspacing=0 cellpadding=0><colgroup><col width=122 style="width:92pt;"><tbody><tr height=101 style="height:75.75pt;"><td width=122 height=101 style="border:0px black;width:92pt;height:75.75pt;background-color:transparent;"><p><font face=Calibri><font size=3>Net#36<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span></font><span style=""><font size=3>&nbsp;&nbsp;&nbsp;&nbsp; </font></span></font></p><p><font face=Calibri><span style=""></span><font size=3>EWS drop158</font></font></p><p><font face=Calibri><font size=3>Optiplex9020(Intel(R) Ethernet Connection I217-LM&nbsp;NIC-Primary OHI</font></font></p><p><font face=Calibri><font size=3>Broadcom NetXtreme Gigabit Ethernet&nbsp;NIC-Secondary OHI)&nbsp;(W10- 64-bit)</font></font></p></td></tr></tbody></table> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | This behavior is not unexpected and is valid. Works as designed. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Plugin the cables for both OHI1 and OHI2.</p><p>2. reboot the drop.</p><p>3. After reboot secondary OHI will be in control.</p> |  | Win 10 |  |  | FINDING | [6 empty] | 102236
37594 | FINDING | G04 OCR1100 controller reports wrong time stamp for alarms (1/1/1970) | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2016-10-21 00:49 | [11 empty] | Lal, Ramesh External | 2016-10-21 00:49 | 70732 |  |  | 2016-10-17 04:16 |  |  |  | Lal, Ramesh External | 2016-09-21 04:55 |  | <p>The Alarm time stamp reported by OCR1100 G04 controller is always 1/1/1970 whereas OCR1100 G01 Controller reports correct time for alarms</p><p>Similarly In Point Info the time shown in U4 and U6&nbsp; field is 1/1/1970 with OCR1100 G04 whereas for OCR1100 G01 controller the time is shown correctly</p><p>If we do Putty in OCR1100 GO4 controller is shows Jan 1 1970 whereas OCR1100 G01 controllers shows correct time.</p><p>Please refer attached snapshots.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360002_October_12 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360002_October_12 |  |  | FINDING | [6 empty] | 104289
37596 | FINDING | G04 OCR1100: SureService Ovation System Registration tool dosn't report correct info for OCR1100-G04 controller | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2016-11-04 01:33 | [11 empty] | Lal, Ramesh External | 2016-11-04 01:33 |  |  |  | 2016-11-04 01:33 |  |  |  | Lal, Ramesh External | 2016-09-21 06:00 |  | <p>On Ovation 3.6.0, &nbsp;OCR1100 G04 is configured as Primary Controller Drop24 and OCR1100 G01 is configured as Partner Drop74. While running SureService Ovation System Registration tool it is observed that the tool doesn't report correct details for Drop24 (OCR1100 G04) whereas for Drop74 (OCR1100 G01) details reported are correct. Sample of messages for Drop24 are as below:</p><p>&quot;Exception caught while getting Drop info: Could not find any recognizable digits&quot;</p><p>&quot;Serial Number:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; yyyyyyyyy</p><p>Electronic Index:&nbsp;&nbsp;&nbsp;&nbsp; ----------- &quot;</p><p><br></p><p>&nbsp;&nbsp; Please refer attached snapshot.</p> |  |  |  |  | 0 |  |  |  | 11/04/16: RL - Verified in pilot production module (Drop6) and found O.K. Finding closed. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | DBS Drop220 (Win Server 2012 R2), Controller Drop24 (OCR1100 G04) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | The &quot;prototypes&quot; were not programmed with Serial Numbers or Electronic Index numbers. &nbsp;Can you tell if these controllers are &quot;prototypes&quot; or are the &quot;production&quot; units from the factory? | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Configure OCR1100 G4 </p><p>Run SureService System Registration tool&nbsp; and observe the details reported for OCR1100 G04</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 105002
37597 | FINDING | G04 OCR1100: Start up message for OCR1100 G04 is reported as OCR1100 G01 in Ovation Error log. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 14:22 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2016-11-28 14:22 |  |  |  | 2016-11-28 14:22 |  |  |  | Lal, Ramesh External | 2016-09-21 06:35 |  | <p>After Flash clear, Download and hard boot of OCR1100 G04&nbsp;controller (Drop24)&nbsp;it comes up on the highway. At this time Ovation error log displays the message:</p><p>&nbsp;&nbsp;&nbsp;&nbsp; &quot;drop24&nbsp;&nbsp;&nbsp;&nbsp; Drop Started: OCR1100 G01&quot;</p><p>Same message is reported when controller comes up on highway after drop clear.</p><p>The controller type should be reported as OCR1100 G04</p><p>Please refer attached snapshot.</p><p><br></p><p>cg (11/15) - same issue observed on G04 pilot modules on Ovation 3.5.0 and 3.5.1 also.</p> | <p>cg (11/2) - Create SDR and add note in DIR.</p><p>cg (11/16) - SDR#38015 created to track this finding.</p> |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Pandey, Vijay EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | DBS Drop220 (Win Server 2012 R2), OCR1100G04 controller |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Lal, Ramesh External | Validation |  | GWS&gt; This will be fixed in a generic controller patch. &nbsp;An SDR will be written (the SDR will be the same SDR for the 3.5.1 and 3.5.0 version of this finding)<div><span class="triage-details hub-title-right" style="color:rgb(140, 140, 140);padding-left:4px;font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:16px;float:right;white-space:nowrap;box-sizing:border-box;">10 of 19</span><div class=info-text-wrapper style="overflow:hidden;font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:18px;white-space:nowrap;position:relative;-ms-text-overflow:ellipsis;box-sizing:border-box;"><a class=caption style="color:rgb(0, 122, 204);text-decoration:none;cursor:pointer;box-sizing:border-box;" href="https://uspit-tfs-v.emrsn.org/tfs/Quality/FINDING/_workitems/edit/37652">FINDING 37652:</a><span class=info-text style="padding-left:4px;box-sizing:border-box;">OCR1100 G04 is wrongly mentioned as OCR1100 G01 in Ovation Error Logs, in case hard reboot operation is performed on OCR1100 G04 Controller.</span></div></div><p><br></p><p>IC 11/28/16&gt; SDR'd, DIR'd and closed finding. SDR 38015 will now track this issue. </p> | 11 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Clear the Flash, Download and hard boot OCR1100 G04 controller. Observe Ovation Error log for the relevant message.</p><p>Clear OCR1100 G04 controller and observe Ovation Error log for the relevant message.</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 105798
37606 | FINDING | Redundant Virtual Controllers eventually fail with local memory error. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:27 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2025-03-19 07:27 |  |  |  | 2025-03-19 07:27 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-09-21 15:07 |  | I have two sets of redundant VCs on the 3.6.0 Emily system.&nbsp; I tested and passed&nbsp;SDR 36730 using these VCs as the original problem was not occurring.&nbsp; In monitoring these two sets of VCs, over time, I have seen both pairs have both VCs be in fault mode.&nbsp;This&nbsp;appears to happen on a reboot of&nbsp;the host machine.&nbsp;Please see attached for the error buffers from a redundant pair. The only way to clear the fault is to clear both VCs. |  | No Action Required |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.6.0 + OVA360001 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Configure redundant VCs (these are on same host). After they are running, reboot host. |  | OVA360001 |  |  | FINDING | [6 empty] | 229007
37609 | FINDING | G04 OCR1100 : Controller Type is seen as OCR1100 G01 in controller diagnostics | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-11-10 05:38 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-11-10 05:38 | 71230 |  |  | 2016-11-10 05:38 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-09-22 04:37 |  | G04 OCR1100 : Controller Type is seen as OCR1100 G01 instead of OCR1100 G04 in controller diagnostics. |  |  |  | This must be tested using &quot;Pilot&quot; OCR1100 G04. &nbsp;The &quot;Prototype&quot; units do not have the EID's programmed, and the EID is what is used to determine what &quot;group number&quot; the OCR1100 is. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | As long as the Manufacturing Index on the OCR1100 starts with the number 245 (represented internally in hex&nbsp;as &quot;FC&quot; in the&nbsp;Index string), the group number will now be pulled from this Index. Otherwise, the old method that differentiates only&nbsp;between copper (G01) and fiber (G02) will be used. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Lal, Ramesh External | [7 empty] | Implementation | OVA360FP1U0 |  | <p>Ovation 3.6.0;</p> <p>OVA360-002-0921;</p> <p>OCR1100 - G04;</p> <p>Drop6(Pilot Prototype Module)</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>Controller Diagnostics now correctly displays the&nbsp;OCR1100 group number.</p> <p>&nbsp;</p> <p>PS 18Oct16: Ovation 3.6.0: Drop6 (pilot module)</p> <p>OVA360002-10172016104630 loaded and controller was downloaded; none of the files were available in download preview window, controller still seen as G01 in controller diagnostics. </p> <p>In addition to this, performed Download-Clear-Load but the issue is still the same: Controller Type is seen as OCR1100 G01 instead of OCR1100 G04 in controller diagnostics.</p> <p>Hence finding status changed to Open: Fail Retest</p> <p>&nbsp;</p> <p><strong>PS 24Oct16:</strong> Ovation 3.6.0: Drop6 (pilot production module):<strong> Patch OVA360002-1021; </strong>The module is now seen as OCR1100 - G04. Hence finding is Closed as FIXED.</p> <p>&nbsp;</p> <p><strong>PS 28Oct16:</strong> Ovation 3.6.0: Drop6 (pilot production module):<strong> Patch OVA360002-1026; </strong>The module is now seen back as OCR1100 - G01. Hence finding state is changed to <strong>Open failed Retest.</strong></p> <p><strong></strong>&nbsp;</p> <p><strong>PS 10Nov16:</strong> Ovation 3.6.0: Drop30 (pilot production module):<strong> OV360FP1_U0; </strong>The module is now seen as OCR1100 - G04. Hence finding is Closed as FIXED.</p> <p><strong></strong>&nbsp;</p> | 24 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Step1&gt; Load Patch OV360-002-0921</p> <p>Step2&gt; Open Controller Diagnostics</p> <p>Step3&gt; Click on controller pair Drop6(G04)/Drop56(G01)</p> <p>Step4&gt; Drop6 (OCR1100 G04) appears as (OCR1100 G01)</p> |  | OVA360002-0921 |  |  | FINDING | [6 empty] | 105253
37610 | FINDING | G04 OCR1100 : OS Version is incorrect in controller diagnostics | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-11-02 08:39 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-11-02 08:39 | 70699 |  |  | 2016-11-02 08:39 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-09-22 04:43 |  | <p>The OS Version of G04 is 6.9.4.7&nbsp;but this is incorrectly shown as 6.9.4.6.</p> <p>&nbsp;</p> <p>VxWorks version&nbsp;of G04 OCR1100 Drop6 is&nbsp;<strong>VxWorks (for Intel(R) Atom Processor SYMMETRIC IO) version 6.9.4.7.</strong></p> |  |  |  | How are you determining what OS version is expected on the controller? | 0 |  |  |  | <p>Now, the VxWorks version of the controller is changed to 6.9.4.6. The putty versions appear as: </p><p><br></p><p><strong>DROP6 (G04)</strong></p><p>login as: administrator<br><a href="mailto:administrator@drop6's">administrator@drop6's</a> password:</p><p>-&gt; version<br><strong>VxWorks (for Intel(R)_Atom_Processor_SYMMETRIC IO) version 6.9.4.6.</strong><br>Kernel: WIND version 2.13.<br>Made on Oct 25 2016 07:07:09.<br>Boot line:<br>gei(1,0)host:vxWorks h=169.254.0.100 e=169.254.0.1 f=0x88C0 s=/ata0/boot/startup.scr<br>value = 96 = 0x60 = '`'<br>-&gt;</p><p><strong>DROP56 (G01)</strong></p><p>login as: administrator<br><a href="mailto:administrator@drop56's">administrator@drop56's</a> password:</p><p>-&gt; version<br><strong>VxWorks (for Atom 200/N270/300/Z5xx) version 6.9.4.6.</strong><br>Kernel: WIND version 2.13.<br>Made on Oct&nbsp; 4 2016 03:05:16.<br>Boot line:<br>gei(1,0)host:vxWorks h=169.254.0.100 e=169.254.0.1 f=0x88C0 s=/ata0/boot/startup.scr<br>value = 96 = 0x60 = '`'<br>-&gt;</p> | 0 |  | Ovation for Windows/Controller/General/Software | The existing application code&nbsp;expects a specific number of spaces in the OS version string. Unfortunately, we are not currently allowed to change the application code for this.&nbsp;The fix to the kernel code adds underscores when there are too many spaces so as to not upset the application code. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Lal, Ramesh External | Silvaggio, Gregory W EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [5 empty] | Implementation | OVA360002_26October |  | <p>Ovation 3.6.0;</p> <p>OVA360-002-0921;</p> <p>OCR1100 - G04;</p> <p>Drop6(Pilot Prototype Module)</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>The version string is now parsed properly.</p> <p><span style="font-size:10pt;"><strong><font face="Times New Roman"></font></strong></span>&nbsp;</p> <p><span style="font-size:10pt;"><strong><font face="Times New Roman">PS 24Oct16:</font></strong></span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;"> Ovation 3.6.0: Drop6 (pilot production module):<strong> Patch OVA360002-1021; </strong>OS Version of Drop6 (6.9.4.7) still appears as (6.9.4.6). Hence finding is Open as Failed Retest.</span></p><p><span style="font-size:12px;">&nbsp;</span><br></p><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;"> <p><strong>PS 28Oct16:</strong> Ovation 3.6.0: Drop6 (pilot production module):<strong> Patch OVA360002-1026; </strong><font face="Times New Roman">OS Version of Drop6 (6.9.4.7) still appears as (6.9.4.6).</font>&nbsp;Hence finding state is changed to <strong>Open failed Retest.</strong></p><p><strong><br></strong></p><p><strong><br></strong></p><p><span style="font-size:13.33px;">GWS 11/1/2016 &gt; This is working as expected. &nbsp;The O.S. Version is expected to be 6.9.4.6</span></p><p><span style="font-size:13.33px;">PS 11/2/2016: The O.S. Version is 6.9.4.6 matches both in VxWorks and Controller Diagnostics. Hence Closed as fixed.</span><strong><br></strong></p></span> | 18 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Step1&gt; Load Patch OV360-002-0921</p> <p>Step2&gt; Open Controller Diagnostics</p> <p>Step3&gt; Click on controller pair Drop6(G04)/Drop56(G01)</p> <p>Step4&gt; OS Version of Drop6 (6.9.4.7) appears as (6.9.4.6)</p> |  | OVA360002-0921 |  |  | FINDING | [6 empty] | 104838
37617 | FINDING | SDR 37372: Fuses is misspelled in the Module Type (OVA360) | Morris, Gilbert L AUTOSOL PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Morris, Gilbert L AUTOSOL PWS PITT | 2016-10-13 09:30 | [11 empty] | Morris, Gilbert L AUTOSOL PWS PITT | 2016-10-13 09:30 | 70569 | [6 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-09-22 15:12 |  | SDR 37372<br><br>The Module Type description is misspelled:&nbsp; <span style="font-style:italic;">Digital Output 5-60 VDC w/ Ch STO, relay pnl comm and ext <span style="font-weight:bold;">fusses</span></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360006 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | This typo will be corrected in patch OVA360006. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | After installing patch OVA360006 check to ensure that the typo in the module type description has been corrected.&nbsp; This should effect any currently configured as well as new inserts. |  | OVA360005-09082016100050 |  |  | FINDING | [6 empty] | 103940
37627 | FINDING | SDR 36379: Nuisance drop faults when sending SOE messages to scanner : RR36525 Failed | Ritchie, Mark AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-10-24 02:03 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-10-24 02:03 | 70670 |  |  | 2016-10-24 02:03 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-09-26 01:02 |  | <p>RR 36525 fails with patch OVA360-001-0922.</p> <p>&nbsp;</p> <p><u>Observations prior to installation of patch 360-001:</u></p> <p>The Ovation Error log immediately floods with the below message:</p> <p>Controller Error: SOE Subsystem Error: SOE could not send message to logger(s): 0x1 : 0x3 : 0x0 : 0x0<br>Controller Error: Could not connect to event logger.</p> <p>&nbsp;</p> <p><u>Observation post–installation of the patch 360-001:</u></p> <p>The Ovation Error log immediately floods with the same message.</p> <p>&nbsp;</p><p><br></p><p><br></p> <p>Hence RR is failed.</p> |  |  |  | GWS&gt; Please provide the sequence of tests which you performed. &nbsp;How many scanners were configured, and how many scanners were available (not powered off or disconnected from the network) when you executed the test that produced the error messages. | 0 |  |  |  | The error log does not flood with the earlier messages . Hence finding is closed. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Silvaggio, Gregory W EMR SYSS PWS PITT | [8 empty] | Implementation | OVA360001 3Oct |  | <span lang=EN-US style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000" size=2 face="Segoe UI">OVA360-001-09222016143405</font></span> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | <div>Clarifying the behavior of the error reporting for this nuisance drop fault:</div><div><br></div>Changed error parameter from 0 to 1 as to distinguish a partial send error from a complete send error.<div><br></div><div><div><span style="color:rgb(34, 34, 34);">The second parameter (0xN) &nbsp;is a mask:</span></div><div><span style="color:rgb(34, 34, 34);">0x1 = Couldn't connect to logger 1</span></div><div><span style="color:rgb(34, 34, 34);">0x2 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 2</span></div><div><span style="color:rgb(34, 34, 34);">0x4 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 3</span></div><div><span style="color:rgb(34, 34, 34);">0x8 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 4</span></div><div><span style="color:rgb(34, 34, 34);"><br></span></div><div><span style="color:rgb(34, 34, 34);">0x3 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 2</span></div><div><span style="color:rgb(34, 34, 34);">0x5 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 3</span></div><div><span style="color:rgb(34, 34, 34);">0x6 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 2 &amp; 3</span></div><div><span style="color:rgb(34, 34, 34);">0x7 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 2 &amp; 3</span></div><div><span style="color:rgb(34, 34, 34);">0x9 = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xA = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 2 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xB = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 2 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xC = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 3 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xD = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 3 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xE = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 2 &amp; 3 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);">0xF = Couldn't&nbsp;</span><span style="color:rgb(34, 34, 34);">connect&nbsp;</span><span style="color:rgb(34, 34, 34);">to logger 1 &amp; 2 &amp; 3 &amp; 4</span></div><div><span style="color:rgb(34, 34, 34);"><br></span></div><div><span style="color:rgb(34, 34, 34);"><br></span></div><div><br></div><div>(When the third parameter is a 0x0, this is a complete send error, the expected delay for this message is 28 seconds:</div><div><br></div><div>Try 1 = 1 second</div><div>Try 2 = 2 seconds</div><div>Try 3 = 3 seconds</div><div>Try 4 = 4 seconds</div><div>Try 5 = 5 seconds</div><div>Try 6 = 6 seconds</div><div>Try 7 = 7 seconds</div><div><br></div><div><span style="color:rgb(34, 34, 34);">Controller Error: SOE Subsystem Error: SOE could not send message to logger(s): 0x1 : 0xN : 0x0 : 0x0</span><br style="box-sizing:border-box;color:rgb(34, 34, 34);"><span style="color:rgb(34, 34, 34);">Controller Error: Could not connect to event logger.</span><br></div><div><br></div><div><br></div><div><div>(When the third parameter is a 0x1, this is a partial send error, the expected delay for this message is 21 seconds:</div><div><br></div><div>Try 1 = 1 second</div><div>Try 2 = 2 seconds</div><div>Try 3 = 3 seconds</div><div>Try 4 = 4 seconds</div><div>Try 5 = 5 seconds</div><div>Try 6 = 6 seconds</div><div><br></div><div><span style="color:rgb(34, 34, 34);">Controller Error: SOE Subsystem Error: SOE could not send message to logger(s): 0x1 : 0xN : 0x1 : 0x0</span><br style="box-sizing:border-box;color:rgb(34, 34, 34);"><span style="color:rgb(34, 34, 34);">Controller Error: Could not connect to event logger.</span></div></div></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | As mentioned in SDR36379 Validation field. |  | OVA360-001 |  |  | FINDING | [6 empty] | 104362
37636 | FINDING | SDR34963-RR 35870 for 3.6.0 failed, Historical SIS event message still gives incorrect message for unlocking CSLS if Hardware KEY lock enabled. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-09-27 01:12 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-09-27 01:12 | [7 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2016-09-27 01:10 |  | <p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>SDR34963-RR 35870- failed</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>SDR 34963 &quot;Ov-3.5.2 + OVA352001-Historical SIS event message gives incorrect message for unlocking CSLS if Hardware KEY lock enabled.&quot;</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-1: Hardware Lock Key on CSLS05 base is in </font><b><font size=3>Locked</font> </b><font size=3>Position + [</font><b><font size=3>Enable Key-Lock</font></b><font size=3>] check box is checked,&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-2: Loaded the CSLS.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-3: Perform [<b>Unlock</b></font><font size=3>] operation on the CSLS via studio.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Steps to reproduce:</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-1: Hardware Lock Key on CSLS base is in </font><b><font size=3>Locked</font> </b><font size=3>Position + [</font><b><font size=3>Enable Key-Lock</font></b><font size=3>] check box is checked,&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-2: Loaded the CSLS.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Step-3: Perform [<b>Unlock</b></font><font size=3>] operation on the CSLS via studio</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><b><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Observation:</font></span></b></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Studio gives error </font><b><i><font size=3>Command sending error: ('2097180') 'LS_UNLOCK_INHIBITED'.</font> </i></b><font size=3>This is expected.</font></span></p><p><font face="Times New Roman" size=3> </font></p><p><span style="color:black;font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;"><font size=3>Historical SIS events gives messages<b><i> “CSLS is Unlocked”</i></b></font><i><font size=3>.</font> </i><font size=3>This is incorrect and unexpected.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><font face=Calibri size=3><p><br></p><font face=Calibri size=3><p><br></p><p><br></p></font><p><br></p></font><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <p>OV3.6.0+OVA360001</p><p>Drop30/80: Charms Controller</p><p>CSLS05</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face=Calibri size=3>Step-1: Hardware Lock Key on CSLS05 base is in <b>Locked </b>Position + [<b>Enable Key-Lock</b>] check box is checked,&nbsp;<span>&nbsp;&nbsp;&nbsp;&nbsp;</span></font></p><p><font face=Calibri size=3>Step-2: Loaded the CSLS.</font></p><p><font face=Calibri size=3>Step-3: Perform [<b>Unlock</b>] operation on the CSLS via studio.</font></p><p><font face=Calibri size=3>Steps to reproduce:</font></p><font face=Calibri size=3><p><font face=Calibri size=3>Step-1: Hardware Lock Key on CSLS05 base is in <b>Locked </b>Position + [<b>Enable Key-Lock</b>] check box is checked,&nbsp;<span>&nbsp;&nbsp;&nbsp;&nbsp;</span></font></p><p><font face=Calibri size=3>Step-2: Loaded the CSLS05.</font></p><p><font face=Calibri size=3>Step-3: Perform [<b>Unlock</b>] operation on the CSLS05 via studio</font></p><font face=Calibri size=3><p style="margin:0in 0in 0pt;"><b>Observation:</b></p><p>Studio gives error <b><i>Command sending error: 'LS_UNLOCK_INHIBITED'. </i></b>This is expected.</p><p>Historical SIS events gives messages <em><strong>Drop30 &lt;LSEvent:30.D30-CSLS005: 30.D30-CSLS005&gt;:&nbsp;&nbsp; CSLS is Unlocked</strong></em></p></font><p>This is&nbsp;&nbsp;unexpected.<br></p></font> |  | OVA360001 |  |  | FINDING | [6 empty] | 103128
37641 | FINDING | SDR34966-RR 37113 for 3.6.0 failed partially, Drop name and CSLS name are not resolved for all of the events. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-10-06 00:45 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-10-06 00:45 |  |  |  | 2016-10-06 00:45 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-09-27 08:04 |  | <p>Point#1 mentioned in the SDR still fails, i.e. </p> <p>Drop name and CSLS name are not resolved for all of the events. For some Events, they appear in desired format while for some they do not.<br></p> <p>Example </p> <p>09/27/2016 18:19:43&nbsp;DROP30&nbsp;&lt;SifAlert: 30.7: CM2&gt;:&nbsp;&nbsp;Cleared:&nbsp;Trip consensus in an AVTR or DVTR block<br></p> <p>Please refer to attached zip file &quot;SDR34966_HistoricalReview.zip&quot; for more details.</p> <p>&nbsp;</p> <p>&nbsp;</p> <p>ASG 10/06/16 &gt; SDR#37710 raised for Point#1.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360001 |  |  | FINDING | [6 empty] | 103666
37642 | FINDING | SDR34721-RR 37115 for 3.6.0 failed, Zero Error code is still returned by the Load operation of Controller is shown in the end of SIS Events | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-09-27 08:07 | [11 empty] | USPITTFSService | 2016-09-27 08:07 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-09-27 08:07 |  | <p>Still Zero Error code is returned by the Load operation of Controller is shown in the end of SIS Events.</p> <p>&nbsp;</p> <p>09/26/2016 11:39:14&nbsp;DROP30&nbsp;&lt;OtherSisEvent: DROP30&gt;:&nbsp;&nbsp;Controller Load: Started 0<br>09/26/2016 11:39:15&nbsp;DROP30&nbsp;&lt;OtherSisEvent: DROP30&gt;:&nbsp;&nbsp;Controller Load: Ended 0<br></p> <p>&nbsp;</p> <p>Please refer to attached &quot;SDR34721_HistoricalReview.txt&quot; file for details.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | <p>OV3.6.0+OVA360001</p> <p>Drop30/80: Charms Controller</p> <p>CSLS05</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360001 |  |  | FINDING | [6 empty] | 103180
37649 | FINDING | SDR 37119: SIS Events performs slow and takes too many resources on the scanner fails | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-10-19 14:21 | [11 empty] | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-10-19 14:21 |  |  |  | 2016-10-19 14:21 |  |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | 2016-09-27 14:01 |  | <p>While testing SDR 37119: SIS Events performs slow and takes too many resources on the scanner&nbsp; its observed that SIS event services are going to high CPU usage(sometimes 100 also).</p><p>Tracking through Monitoring CPU usage on OPH scanner drop.</p><p><br></p><p>SK: According to Mikolaj temporarily hitting of CPU usage as 100%&nbsp; is normal, hence closing finding based on this.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | on Net#36 , Ov3.6.0 Drop159(Win7) OPH scanner |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Shailendra EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><br></p> |  | OVA36001 |  |  | FINDING | [6 empty] | 104163
37655 | FINDING | G04 OCR1100: Controller switched to “Failed mode” after configuration of Device followed by download | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-08 23:41 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-08 23:41 |  |  |  | 2016-11-08 23:41 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-09-28 07:04 |  | <p>As reported in F#37654 for OV351-G04-OCR1100; similar issue is observed on OV360.</p> <p>&nbsp;</p> <p>After configuration of device, on performing download the controller switched to “Failed mode”.<br><br>The Controller cannot be Cleared from Developer Studio. The only option to bring the controller to healthy state is to either&nbsp;format the flash, or log into the controller and use the command “deleteAllFiles” and the reboot.</p> <p>&nbsp;</p> <p>The printErrorBuffer displays the controller boots up in Failed mode due to “Controller Error : Coordinator Subsystem Error” followed by “Could not sync with ssv_task”. </p> <p>Attached <strong>G04-OV360-Drop6-Error.txt</strong>&nbsp;for details of the putty session.</p> <p>&nbsp;</p> <p>PS: This issue was observed previously while hooking up the controller Drop6/56&nbsp;on Net#26.&nbsp;Similar&nbsp;sequence was noticed for configuration of DEVICE 1. </p> <p>Attached <strong>Drop6_ssv.txt</strong>&nbsp;for details of the putty session then.<br>&nbsp;<br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Lal, Ramesh External | Silvaggio, Gregory W EMR SYSS PWS PITT | [6 empty] | Implementation |  |  | <p>Ovation 3.6.0;</p> <p>OVA360-002-0921;</p> <p>OCR1100 - G04;</p> <p>Drop6(Pilot Prototype Module)</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | This is not an issue with the G04 OCR1100. &nbsp;You must issue a &quot;clear command&quot; after adding an IO driver. &nbsp;This &quot;unable to clear from studio&quot; aspect will be fixed in another patch for all the controller types, not just the G04 OCR1100.<div><br></div><div>cg (11/9) - SDR#37967 created&nbsp;to track&nbsp;this issue. Hence finding closed.<br></div><div><br></div><div><br></div><div><div>msg[0] = THU JAN 01 00:00:00 1970 : interrupt: &lt;134&gt; IOIC Driver: main firmware ready. duplex</div><div>msg[1] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 0&nbsp;</div><div>msg[2] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 1&nbsp;</div><div>msg[3] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 2</div><div>msg[4] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 3&nbsp;</div><div>msg[5] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 4&nbsp;</div><div>msg[6] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Initializing SHC 5&nbsp;</div><div>msg[7] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Final SHC init status 003f&nbsp;</div><div>msg[8] = THU JAN 01 00:00:14 1970 : &lt;134&gt; Init_SHC : Starting SHC daemon - SHC_HWY</div><div>msg[9] = THU JAN 01 00:00:18 1970 : &lt;131&gt; coord: IO Library : dpram file load error, device 1 is now installed. &nbsp;0x0 : 0x0 : 0x0 : 0x0</div><div>msg[10] = THU JAN 01 00:00:18 1970 : &lt;129&gt; Controller Error : Coordinator Subsystem Error : Coordinator Support Error : 0x6 : 0x4 : 0x0 : 0x0</div><div>msg[11] = THU JAN 01 00:00:18 1970 : &lt;129&gt; Controller Error : Coordinator Subsystem Error : Coordinator PCL Error : 0x1 : 0xa : 0x1 : 0x0</div><div>msg[12] = THU JAN 01 00:00:20 1970 : &lt;135&gt; gni3rdm : Switching to server 192.168.12.245 duplex &nbsp;value bits 0x0 alarm bits 0x0</div><div>msg[13] = THU JAN 01 00:00:22 1970 : &lt;133&gt; Drop Started : OCR1100 G01</div><div>msg[14] = THU JAN 01 00:00:47 1970 : &lt;134&gt; REDUND_PROC ERROR : Could not sync with ssv_task</div><div>msg[15] = THU JAN 01 00:00:47 1970 : &lt;134&gt; REDUND_PROC MSG : Switching to Failed mode</div><div>msg[16] = THU JAN 01 00:00:48 1970 : &lt;133&gt; Copy to Backup : Receiving handshake messages from drop56</div><div>msg[17] = THU JAN 01 00:02:03 1970 : &lt;131&gt; SSH Login Attempt : Login Failed for user: administrator</div><div>msg[18] = THU JAN 01 00:02:03 1970 : &lt;129&gt; Controller Error : Subsystem Group 2 Error : Controller Shell : 0x1 : 0x0 : 0x0 : 0x0</div><div>msg[19] = THU JAN 01 00:02:10 1970 : &lt;132&gt; SSH Login Attempt : Login Succeeded for user: administrator</div><div>msg[20] = THU JAN 01 00:02:18 1970 : &lt;129&gt; Update Backup : After 120 seconds, ddbTableInfo did not become available</div><div>msg[21] = THU JAN 01 00:02:26 1970 : &lt;129&gt; SHELL INPUT : printErrorBuffer 20</div><div>msg[22] = THU JAN 01 00:03:58 1970 : &lt;129&gt; SHELL INPUT : deleteAllFiles</div><div>msg[23] = THU JAN 01 00:10:09 1970 : &lt;129&gt; Controller Error : Subsystem Group 2 Error : Controller Shell : 0x1 : 0x0 : 0x0 : 0x0</div><div>msg[24] = THU JAN 01 00:10:10 1970 : &lt;129&gt; SHELL INPUT : exit</div></div> | 10 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Step1&gt; Configure&nbsp;IO Device&nbsp;in the&nbsp;controller (here Modbus-R)</p> <p>Step2&gt; Add IO Driver (here Modbus-R)</p> <p>Step3&gt; Download the controller. </p> <p>Step4&gt; Controller goes in Failed mode.</p> |  | OVA360002-0921 |  |  | FINDING | [6 empty] | 105155
37673 | FINDING | RR37581/SDR20908: Achilles Level 1 test failed | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 9 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-11-02 07:57 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2016-11-02 07:57 | 71487 | [6 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-09-29 12:51 |  | RR37581/SDR20908:&nbsp; Controller failed during Achilles Level 1 testing.&nbsp; Files are attached.<br><br>Discrete Monitor changed to Warning during tests.&nbsp; Files are attached.<br><br>Clarification:&nbsp; The controller did not fail during testing with the new OVA360001.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP1U1 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | Remove firewall rules after a predefined expiration period.<div>Added rate-limited suppression on error log messages from DBXMIT and ADMD.</div> | 14 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360001-09222016143405 |  |  | FINDING | [6 empty] | 104836
37684 | FINDING | G04 OCR1100: N2 port switches from Active state to Available state when OCR1100-G04 module is rebooted. | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2016-10-21 01:13 | [11 empty] | Lal, Ramesh External | 2016-10-21 01:13 |  |  |  | 2016-10-17 04:18 |  |  |  | Lal, Ramesh External | 2016-10-03 06:58 |  | <p>On Ovation 3.6.0 system Drop24 is configured as Primary Controller (OCR1100-G04) and Drop74 as Partner Controller (OCR1100-G01). Drop24 (OCR1100-G04) is in control. Its network interface Port N2 (K0) is in Active state and N3 (K1)&nbsp;is in Available state. When OCR1100-GO4 is rebooted N2 port (K0) switches from Active state (Green in SSD ) to Available state (Yellow in SSD) and N3 port (K1) becomes Active.&nbsp;This doesn't happen always but has been seen many time. This issue is not there with OCR1100-G01 module.</p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV 3.6.0, DBS Drop220 Win Server 2012 R2, Controller OCR1100-G04 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | The difference is believed to be in the initialization of the ethernet ports. &nbsp;In the G04, there appears to be a difference in the timing of the initialization. &nbsp;Sometimes the N2 port will initialize before the N3 port, while sometimes the N3 port will initialize before the N2. &nbsp;There is no deliberate requirement for the N2 to be active vs the N3. &nbsp;The only requirement is that one is Active and the other is Available. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>- Configure Primary Controller (OCR1100-G04) and Partner Controller (OCR1100-G01)</p><p>- Reboot OCR1100-G04 controller and observe State N2 and N3 port.</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 104294
37700 | FINDING | G04 OCR1100 : Drop Point (DU) Record Field HC Bit 7 (Drop Synchronized within 1 ms of reference time) is not indicating correctly. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jha, Rahul AUTOSOL PWS NOIDA | 2016-10-26 09:44 | [11 empty] | Jha, Rahul AUTOSOL PWS NOIDA | 2016-10-26 09:44 | 70732 |  |  | 2016-10-26 09:44 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2016-10-04 07:19 |  | <p>The DU Record Field HC Bit 7 seems to be value=0, regardless of whether the controller is sync&quot;d with the NTP server.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | [9 empty] | Implementation | OVA360002_October_12 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | <p>RJ 10/17/2016: Verified that bit 7 is updating the value to 1 in OVA360002_October_12 patch. Kept the issue under monitoring.</p><p>RJ 10/26/2016: Monitored the bit 7 status of G04 controller Drop6 (Net#26)&nbsp;using historian, observed that bit 7 stays to value 1 for longer period.</p><p>Hence, finding is closed as confirmed to be fixed.&nbsp;&nbsp;</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360002-0921 |  |  | FINDING | [6 empty] | 104606
37705 | FINDING | G04 OCR1100 Controller is non-responsive though in graphics it is showing online and in Point info the status field shows "In Control". | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-02 09:45 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-02 09:45 |  |  |  | 2016-11-02 09:45 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2016-10-05 02:05 |  | <p>OCR1100G04_Controller (Drop32) is in&nbsp;non-responsive or Offline mode and it is not allowing to perform any action like Download, clear, load, reboot etc.</p><p><br></p><p>However,&nbsp;the operator&nbsp;applications have&nbsp;below information: </p><p>Graphics shows the controller is in&nbsp;online state&nbsp;</p><p>Point Info shows the status field&nbsp;as &quot;In Control&quot;. </p><p>Error log shows Drop32 is OFFLINE and Unknown State.</p><p>Controller Diagnostics does not show any details of Drop32.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | Silvaggio, Gregory W EMR SYSS PWS PITT | Lal, Ramesh External | [5 empty] | Implementation |  |  | Ov3.6.0 + OCR1100_G04 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | cg (11/2) - SS did not observe the scenario again. Hence finding closed as Anomaly per discussion with Nooch and Greg. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.Select a controller.</p><p>2.Create any point.</p><p>3.Load the point into the controller.</p><p>4.It will not allow the load operation.</p><p>5.Similarly perform the other operations like download, clear, reboot etc.</p><p>6.Please refer to the attachments for&nbsp;deeper insight.</p> |  | OVA360002-0921 |  |  | FINDING | [6 empty] | 104844
37720 | FINDING | G04 OCR1100: Input Packet and Output Packet don't update in DU record of OCR1100-G04 controller | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Lal, Ramesh External | 2016-10-21 00:52 | [11 empty] | Lal, Ramesh External | 2016-10-21 00:52 |  |  |  | 2016-10-17 07:34 |  |  |  | Lal, Ramesh External | 2016-10-07 06:03 |  | <p>In Ovation 3.6.0 Drop24 (OCR1100 -G04) is configured as Primary Controller and Drop74 (OCR1100-G01) is Partner Controller.&nbsp; It is observed that DU record IS fields (Input Packet) and OP record</p><p>(Output Packet) don't update for Drop24 (OCR1100-G04) whereas&nbsp; they update periodically for Drop74(OCR1100-G01).</p><p>Please refer the attached snapshot.</p> |  |  |  | Test that IS and OP fields are increment approximately every 10 seconds when either the Channel 0 or Channel 1 is the Active network interface. | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360002_October_12 |  | DBS Drop220 (Win Server 2012 R2), Controller Drop24(OCR1100-G04)/Drop74(OCR1100-G01) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | Updated the kernel to provide ethernet statitistics. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure Primary Controller (OCR11100-G04) and Partner Controller (OCR1100-G01)</p><p>2. Observe IS and OP fields of DU record of OCR1100-GO4 controller.</p> |  | OVA360002_October_12 |  |  | FINDING | [6 empty] | 104291
37730 | FINDING | G04 OCR1100:Netework interface mode "auto-negotiate" is shown as "100Mbps full duplex" in Ovation Error log | Zaremsky, Mark External MZCI | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2016-10-21 01:10 | [11 empty] | Lal, Ramesh External | 2016-10-21 01:10 |  |  |  | 2016-10-17 07:40 |  |  |  | Lal, Ramesh External | 2016-10-10 06:17 |  | <p>While testing N1, N3, N4 to be used&nbsp;for 3rd Party I/O for OCR1100 G04, following configuration was made:</p><p>&nbsp;Custom Network Interface &gt; NIC Interface: N3,&nbsp; Interface Mode: auto-negotiate.</p><p>&nbsp;Controller was downloaded and rebooted. When the controller comes up following message is reported in Ovation Error log:</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;Drop24&nbsp;&nbsp; Interface Status :gei2[n3] 100 Mbps full duplex&quot;</p><p>This message doesn't confirm that the interface is actually using 'auto-negotiate'&nbsp;mode because same message is reported if the &nbsp;Interface Mode configured&nbsp;is '100 Mbps full duplex'.</p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0, DBS Drop220, Controller Drop24(OCR1100-G04)/&nbsp; Drop74 (OCR1100-G01) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | The message shown in the Ovation Error Log reflects the current state\speed\duplex of the ethernet port. &nbsp;It does reflect the configured state. &nbsp; So if the port is configured for Auto-Negotiate, it will end up in any of the other modes, after the negotiation has taken place with the Ethernet Switch. &nbsp;<div><br></div><div>Another way to test the controller when it is configured for Auto-Negotiate is to directly connect the port on the Controlller (i.e. N1) to a windows machine (i.e. a laptop) using a Crossover Cable. &nbsp;You can then change the Speed\Duplex on the windows machine and verify that the controller mode negotiates properly. &nbsp;See attachment &quot;mode.png&quot; for an example.</div> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>-Configure Controller Drop24(OCR1100-G04)/&nbsp; Drop74 (OCR1100-G01)</p><p>- Configure Custom Network Interface &gt; NIC Interface: N3,&nbsp; Interface Mode: auto-negotiate.</p><p>-&nbsp; Download, reboot controller and observe the Ovation Error log</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 104292
37742 | FINDING | G04 OCR1100: Third Party device will not communicate if N1 Port of OCR1100-G04 is configured for Interface Mode = Default (none). | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-18 04:43 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2016-11-18 04:43 |  |  |  | 2016-11-18 04:43 |  |  |  | Lal, Ramesh External | 2016-10-12 05:31 |  | <p>On Ov 3.6.0 system&nbsp;Third party device Modbus-R is configured in Drop24 (OCR1100-GO4)&nbsp; and is communicating (N1 port and Calta Modbus Simulator is used for testing). The Custom Network Interface for this configuration is:</p><p>NIC Interface = N1, Interface Mode =100Mbps full duplex.</p><p>Ovation Error log reports Interface Status: gei0 [N1]:100 Mbps full duplex.</p><p>If Interface Mode is&nbsp;not defined i.e. left blank (default&nbsp; ? )&nbsp;then also Ovation Error log reports 'Interface Status: gei0 [N1]:&nbsp;up 100 Mbps full duplex' but Device stops communicating.</p><p>In this case also Device should communicate else Ovation Error log should report 'Interface Status:gei0[N1]:down'.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0, DBS drop220 Win Server2012 R2, Drop24(OCR1100-G04/Drop74(OCR1100-G01) |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Lal, Ramesh External | Validation |  | <div>This is working as expected. &nbsp;When the&nbsp;<span style="font-size:12px;">interface mode = none, the ethernet port is disabled. &nbsp;</span><span style="font-size:12px;">The flags field in hostinfo.1 is set to 0x0:</span></div><div><span style="font-size:12px;"><br></span></div><div><div><div># Version 1</div><div>#name unit<span class=Apple-tab-span style="white-space:pre;"> </span>IPAddress &nbsp; &nbsp; &nbsp;<span class=Apple-tab-span style="white-space:pre;"> </span>netmask &nbsp; &nbsp; &nbsp; &nbsp;<span class=Apple-tab-span style="white-space:pre;"> </span>flags</div><div>#---------<span class=Apple-tab-span style="white-space:pre;"> </span>--------- &nbsp; &nbsp; &nbsp;<span class=Apple-tab-span style="white-space:pre;"> </span>------- &nbsp; &nbsp; &nbsp; &nbsp;<span class=Apple-tab-span style="white-space:pre;"> </span>-----</div><div>gei 0 <span class=Apple-tab-span style="white-space:pre;"> </span>192.168.2.205 &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>255.255.254.0 &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>0x0</div><div>gei 1 <span class=Apple-tab-span style="white-space:pre;"> </span>192.168.2.5 &nbsp; &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>255.255.255.0 &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>0x4</div><div>gei 3 <span class=Apple-tab-span style="white-space:pre;"> </span>192.168.125.1 &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>255.255.255.0 &nbsp; <span class=Apple-tab-span style="white-space:pre;"> </span>0x4</div></div></div><div><br></div><div>The lowest digit of &quot;flags&quot; i.e. 0 or 4, controls the mode of the ethernet port. &nbsp;The modes are defined as:</div><div><div>EIOC_MODENONE<span class=Apple-tab-span style="white-space:pre;"> </span>&nbsp; &nbsp; &nbsp; &nbsp; (0)<span class=Apple-tab-span style="white-space:pre;"> </span>/* interface down */</div><div>EIOC_MODE10HDX<span class=Apple-tab-span style="white-space:pre;"> </span>&nbsp; &nbsp; &nbsp; &nbsp; (1)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 10 mbps half duplex */</div><div>EIOC_MODE10FDX<span class=Apple-tab-span style="white-space:pre;"> </span>&nbsp; &nbsp; &nbsp; &nbsp; (2)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 10 mbps full duplex */</div><div>EIOC_MODE100HDX<span class=Apple-tab-span style="white-space:pre;"> </span>(3)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 100 mbps half duplex */</div><div>EIOC_MODE100FDX<span class=Apple-tab-span style="white-space:pre;"> </span>(4)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 100 mbps full duplex */</div><div>EIOC_MODEAUTO<span class=Apple-tab-span style="white-space:pre;"> </span>(5)<span class=Apple-tab-span style="white-space:pre;"> </span>/* Auto Negotiate */</div><div>EIOC_MODE1000HDX<span class=Apple-tab-span style="white-space:pre;"> </span>(6)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 1000 mpbs half duplex */</div><div>EIOC_MODE1000FDX<span class=Apple-tab-span style="white-space:pre;"> </span>(7)<span class=Apple-tab-span style="white-space:pre;"> </span>/* 1000 mpbs full duplex */</div></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>-Configure Modbus-R Device and its driver</p><p>- In Custom Network Interface configure NIC Interface = N1, Interface Mode =100Mbps full duplex.</p><p>- Verify Calta communicates with Ovation pints</p><p>-In Custom Network Interface configure NIC Interface = N1, Interface Mode = - (leave it blank)</p><p>-Verify that Calta stops communicating.</p> |  | OVA360002-19Sept |  |  | FINDING | [6 empty] | 105498
37744 | FINDING | Test procedure 3.6.0_G04_CONTROLLER_SVTP_rev5.7 needs changes | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-10-12 05:50 | [11 empty] | USPITTFSService | 2016-10-12 05:50 | [7 empty] | Lal, Ramesh External | 2016-10-12 05:50 |  | <p>Test procedure 3.6.0_G04_CONTROLLER_SVTP_rev5.7 needs following changes:</p><p>Test cases 5.21.4 k) - q) should be deleted and added&nbsp;in Test 5.21.5. These tests can be performed only when both N2 and N3 ports are defined as Dual Highway Interface connection.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Lal, Ramesh External | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360-002 |  |  | FINDING | [6 empty] | 103878
37746 | FINDING | RR37707/SDR37624: No files appear in Controller Diagnostics for tRVP module. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2016-10-12 13:06 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-10-12 13:06 |  |  |  | 2016-10-12 13:06 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-10-12 12:01 |  | RR37707/SDR37624:&nbsp; No files appear in Controller Diagnostics for tRVP module.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Firmware/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OVA360007-09232016123945 |  |  | FINDING | [6 empty] | 103905
37782 | FINDING | RR 37707; SDR 37624; OVA360007: A TRVP module reboot from Diagnostics displays an error | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2016-10-27 12:01 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2016-10-27 12:01 | 71365 |  |  | 2016-10-27 12:01 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-10-18 11:28 |  | RR 37707; SDR 37624; OVA360007<br>A module reboot results in a failure (refer to attachment).<br>OCR1100 Controller 1/51 (EMILY).<br><br>Update:&nbsp; The module reboot does actually occur, so the Category is being changed to 4 and the Title is being updated slightly.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Firmware/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lupu, Mircea F AUTOSOL PWS PITT | [9 empty] | Implementation | OVA360007_26October |  |  |  | Ovation for Windows | Ovation | Controller/Firmware | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360007-09232016123945 |  |  | FINDING | [6 empty] | 104694
37799 | FINDING | G04 OCR1100 : controller "ss_rpc: ready to be download" message is not seen everytime in error log | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-12-13 22:17 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-12-13 22:17 | 71486 |  |  | 2016-12-13 22:17 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-10-20 01:01 |  | <p>When we hook up a fresh G04 OCR1100 controller on a network (OV360) or format&nbsp;flash of the controller.</p> <p>The ready to download meassages are not received on Error Log everytime. </p> <p>&quot;ss_rpc: spawning...&quot; </p> <p>&quot;ss_rpc: ready to be download&quot; </p> <p>&nbsp;</p> <p>User can wait for couple of minutes and try downloading files. Which works fine. (This message is seen approximately once in 15 times.)</p> |  |  |  | <p><span style="font-size:12px;">GWS 11/1/2016 &gt;Please retest for this using the &quot;production&quot; controllers, as opposed to the &quot;prototype&quot; controllers. &nbsp;This issue may be related to unprogrammed MAC &nbsp;addresses.</span></p><p><span style="font-size:12px;">PS 11/1/2016 : Drop6 (the issue reported for) is production module only.&nbsp; </span></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Lal, Ramesh External | Silvaggio, Gregory W EMR SYSS PWS PITT | Zaremsky, Mark External MZCI | [5 empty] | Implementation | OVA360FP1_U1 |  | <p>Ovation 3.6.0;</p> <p>OVA360002-1017;</p> <p>OCR1100 - G04;</p> <p>Drop6(Pilot&nbsp;production Module)</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>Inserted an ifconfig(0) statement to &quot;tickle&quot; the driver before calling the simplySyslog which sends the &nbsp;message.</p> <p>&nbsp;</p> <p>PS 14Dec16: Verified OV360FP1_U1 for this fix by repeating the steps multiple times and found to be correct. Hence Closing the finding as Fixed.</p> | 10 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Step1&gt; Hook up a fresh G04 OCR1100 controller on a network (OV360). </p> <p>Step2&gt; Fresh flash is inserted in the controller. </p> <p>Step3&gt; IP details are provided in the Dev. Studio. Ping is verified.</p> <p>Step4&gt; The Error Log refers to the Ethers address and other details as seen below.</p> <p><img src="http://tfs.emersonprocess.com/tfs/Quality/WorkItemTracking/v1.0/AttachFileHandler.ashx?FileNameGUID=07f0a378-fbcc-4a97-841b-311c62510331&amp;FileName=tmpF913.png" width=889></p> <p>Step5&gt; After few seconds it is expected to receive messages on the Error Log from the configured drop (here Drop6) as:</p> <p><img src="http://tfs.emersonprocess.com/tfs/Quality/WorkItemTracking/v1.0/AttachFileHandler.ashx?FileNameGUID=5c7c3a23-f02d-4883-919c-eb5c783b60b9&amp;FileName=tmp2E57.png" width=410><br>But, this message is not seen all the times.&nbsp;</p> <p>Step6&gt; Wait for 5-10minutes and download the controller. All the files are verified to be downloaded.</p> <p>Step7&gt; And after a power cycle the controller is available for use.&nbsp;</p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106528
37806 | FINDING | PWTTS - (Comanche FF Test) Rosemount 848T Rev 7 report lost COMM | Plymire, Alvan AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Phan, Quang EMR ENT TECH AUS | 2017-06-05 14:13 | [11 empty] | Phan, Quang EMR ENT TECH AUS | 2017-06-05 14:13 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-10-20 11:07 |  | <p>During Comanche FF regression test, there are 2 different Rosemount 848T Rev7 commissioned on 2 different Simplex module.&nbsp; </p><p>Both devices report lost COMM for a brief moment (75 seconds) then commissioned back.&nbsp; </p><p>This happen randomly, sometime after 2 hours, sometime after 10 hours.</p><p>See attached for sample of data captures when it failed (serial data from module and NiBus trace on segment)</p><p><br></p><p>See Rosemount ClearQuest issue PRD00127933 (Austin #6 - A non-responding field device causes occasional &quot;NO COMM&quot; alerts in other devices.)</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | DeLancey, Brian J. EMR SYSS PWS PITT | Tielens, Craig External CRT Consulting | Reed, Gene EMR SYSS PWS HSTN | Capani, Innocenzo AUTOSOL PWS PITT | [6 empty] | Implementation |  |  | <p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">System info:</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">PWTTS Test System 1</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">OCR1100 G01 controller</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">DBS - WinServer 2012 R2 with Ovation 3.6 build U9 and AMS 13.1.1 (release candidate)</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">OPS - Win7</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">Simplex FF module 1 : 848T Rev 7 commissioned with 2 FFAI and 1 FFISELX blocks configured on control sheet</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">Simplex FF module&nbsp;2 : 848T Rev 7 commissioned with&nbsp;FFMAI block&nbsp;configured on control sheet</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Commission a Rosemount 848T Rev 7 on a simplex FF module.&nbsp; Configure some function block from device on control sheet.&nbsp; Let system soak at least overnight |  | U9 |  |  | FINDING | [6 empty] | 113782
37807 | FINDING | PWTTS - (Comanche FF Test) Miss respond from one FF device cause lost COMM on other FF devices on the same segment. | Pratley, Bob EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Rick P EMR SYSS PWS PITT | 2019-01-14 15:06 | [11 empty] | Brown, Rick P EMR SYSS PWS PITT | 2019-01-14 15:06 | [7 empty] | Phan, Quang EMR ENT TECH AUS | 2016-10-20 11:26 |  | <p>While trying to validate SDR 34027 (FF segment report LINK_ERROR), a Rosemount 848T Rev6 with modified firmware (a parameter added to intentionally not respond to request within certain time frame) was commissioned on a simplex FF segment along with other 6 devices.&nbsp; </p><p>When added parameter enabled on device, not only itself report lost COMM, it also caused 5 out of 6 other devices on the same segment report a lost COMM.</p><p>Attached is the data capture during overnight soak test.&nbsp; Note that Ni Bus trace is limited to 500,000 lines of data (roughly 2-4 hours)</p><p><br></p><p>See Rosemount ClearQuest issue PRD00126817 (Host stack stops sending all FMS requests after single device fails to respond)</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | Related to PRD00126817 - may already be fixed |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Tielens, Craig External CRT Consulting | DeLancey, Brian J. EMR SYSS PWS PITT | Reed, Gene EMR SYSS PWS HSTN | Capani, Innocenzo AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [5 empty] | Implementation |  |  | <p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">System info:</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">PWTTS Test System 1</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">OCR1100 G01 controller</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">DBS - WinServer 2012 R2 with Ovation 3.6 build U9 and AMS 13.1.1 (release candidate)</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;">OPS - Win7</p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;"><br></p><p style="margin:0px;color:rgb(0, 0, 0);text-transform:none;line-height:1.5em;text-indent:0px;letter-spacing:normal;font-family:&quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:12px;font-style:normal;font-weight:normal;word-spacing:0px;white-space:normal;orphans:2;widows:2;"><br></p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  |  | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>Modified Rosemount 848T Rev 6 commissioned on Simplex FF module along with at least 6 other Rosemount devices.&nbsp; </p><p>Disable parameter 19999 on device using Ni&nbsp;Dialog and verify segment doesn't report any device lost COMM for at least couple hours.&nbsp;</p><p>Enable parameter 19999 and let system soak overnight</p> |  | U9 |  |  | FINDING | [6 empty] | 136853
37960 | FINDING | Consistency Check on the Ov-3.6.0 1GB Network freezes at: CheckingSIS Charm step | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2016-12-13 15:28 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2016-12-13 15:28 | 71646 |  |  | 2016-12-13 15:28 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-11-07 15:26 |  | <p>Consistency Check on the Ov-3.6.0 1GB Suzi Network in Lab-5 freezes at</p> <p>&nbsp; 'Checking SIS Charm Secure Parameters' step</p> <p>---</p> <p>msb 12/13 - </p> <p>&nbsp;with OVA360FP1_U1 - </p> <p>&nbsp;&nbsp; &nbsp;Consistency Check on Network level - completed in &lt; 4 Min.</p> <p>---</p> |  |  |  | <p>The affected area is the consistency check which looks for multiple SIS Charm Secure Parameters which reference the same Ovation Point Name.</p><p>Testing should ensure that the performance of the consistency check improves on the system where this finding was generated.&nbsp; In addition, an invalid configuration should be created (e.g., multiple SIS Charm Secure Parameters referencing the same Ovation point) to ensure that the consistency check works as designed.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP1_U1 |  | <p>Suzi Network in Lab-5</p> <p>DBS - PE-T430 - Ws12R2</p> <p>Ov-3.6.0</p> <p>OVA360-FP1</p> <p>&nbsp;</p> <p>Pts on Network: 400K (300K/sec)</p> <p>Control&nbsp;Sheets: 1255</p> <p>Max DDB used: 5826</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>The query associated with the check on duplicate point references by SIS Charm Secure Parameters will be changed to improve performance on large system.</p><p>(Note that the consistency check doesn't actually freeze on the referenced system -- it just takes a long time to complete.&nbsp; Testing by development personnel on the referenced system indicated that the consistency check completed after 30-40 minutes.)</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 106520
37970 | FINDING | OV360FP1: VCH(drop171) network connection was showing as Magenta in status diagram. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-12-14 05:41 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-12-14 05:41 | 71859 |  |  | 2016-12-14 05:41 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2016-11-09 03:33 |  | <p>VCH(drop171) network connection&nbsp;status changes to&nbsp;<strong>Magenta</strong> in status diagram after&nbsp;installing OV360FP1. </p> <p>K0 and K1 field of VCH drop shows as unknown in PI(refer attached snapshot).</p> <p>---</p> <p>msb 11/09 &gt;</p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font size=3><font color="#000000">in Pgh, On the Emily network I see the same on:</font></font></span><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000" size=3>&nbsp;&nbsp;&nbsp;VCH (120) – W10, </font><font size=3><font color="#000000">VCH (121) – Ws12R2</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font size=3><font color="#000000">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Network connection iss showing as </font><span style="COLOR:red;">Magenta</span></font><font color="#000000" size=3> in status diagram. K0 and K1 field of VCH drop shows as </font><span style="COLOR:red;"><font size=3>unknown</font></span><font size=3><font color="#000000"> in PI</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font size=3>But not on:&nbsp; </font></font></span><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000"><font size=3>VCH(122) – W7</font></font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font size=3><font color="#000000">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Network connection is showing as </font><b><span style="COLOR:#00b050;">Green</span></b></font><font size=3><font color="#000000"> in status diagram. In PI, K0 = Active and K1 = Unknown</font></font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:105%;"><font color="#000000">and also not on the 2 W7 VCH drops on the Suzi network in Lab-5 - VCH(171), VCH(173)</font></span></p> <p><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:105%;"><font color="#000000">---</font></span></p> | None |  |  | Ensure network connection is working correctly then examine system status for correct display and point info Status/Network Interface Information for correct information | 0 |  |  |  | <p><font face=Calibri><font size=3><font color="#000000">Network connection is showing as Green in status diagram. In PI, K0 = Active and K1 = Unknown .</font></font></font></p><p><font face=Calibri size=3>Hence the issue is resolved . Thus closing this finding.</font></p> | 0 |  | Ovation for Windows/Operator Station/General/Software | none |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Rathi, Ankur AUTOSOL PWS NOIDA | Garg, Amit AUTOSOL PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | [5 empty] | Implementation | OVA360FP1_U1 |  | <p>Ovation 360 FP1 - VCH Drop</p> <p>Windows 10- 2016 LSTB</p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | Modify sni.dll to detect network bridge with wrtap driver and use the bridged physical NIC to retrieve info | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Check the status of network connection in status diagram and Point Information.</li> <li>Install Ovation360 FP1 on the VCH Drop (Operating Status = Windows 10)</li> <li>Check the status of network connection in status diagram and Point Information.</li></ol> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106556
38001 | FINDING | Consistency Check reports an error for a NumaLogic node. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Swartz, Mark EMR SYSS PWS PITT | 2016-11-14 15:09 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2016-11-14 15:09 |  |  |  | 2016-11-14 15:09 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-11-14 14:59 |  | Consistency Check reports the following error for a previously-configured NumaLogic node:<br><br><span style="font-style:italic;">Ethernet Remote Node Type does not match controller's Ethernet Remote Node Type configuration.</span><br><br>No such error was observed prior to the installation of Feature Pack 1.&nbsp; Refer to the attached file for Consistency Check and NumaLogic node configuration information.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>Works as designed.&nbsp; With the introduction of Ovation Ethernet Remote Nodes and its ability to support Standard Redundancy, a new constraint was necessary -- all Ethernet Remote Nodes in a controller must be of the same type.&nbsp; In order to enforce this new constraint, several new attributes were introduced in the Controller-type Drop Object.&nbsp; These new pull-down attributes&nbsp;are used to indicate the type of Ethernet Remote Nodes for which the controller will support as well as the type of Redundancy for the Remote Nodes.</p><p>For an existing Ovation system with Numalogic Ethernet Remote Nodes, the user must open the applicable Drop Object and select &quot;Legacy&quot; for the Redundancy Mode pull-down attribute, and &quot;Numalogic&quot; for the Remote Node Type pull-down attribute.</p><p><br></p><p>This information will need to be included in the Feature Pack 1 DIR.</p> | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | Ovation 3.6.0 Feature Pack 1-11022016115232 |  |  | FINDING | [6 empty] | 105318
38014 | FINDING | SRF2241 additional information needs to be updated in user manual | Jain, Swati EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | 74036 |  |  | 2016-12-16 15:07 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-11-15 22:54 |  | <p>Following information needs to be added to Ovation 3.6.0 OVA360FP1 user manual in context to SRF2241:</p> <ol> <li>Along with the points originated by Controllers, Sensor Alarm Characteristic and Sensor Alarm Priority are also applicable to points originated by Operator Stations and Virtual Controllers.</li> <li>The Sensor Alarm Characteristics and Sensor Alarm Priority can only be defined in the Studio after the “Special Processing of Sensor Alarms” checkbox is selected.&nbsp; If it is not selected then the sensor characteristics and sensor priority fields are not used.</li> <li>Filtering based on Sensor Alarm Characteristic and Sensor Alarm Priority is also applicable for Audio alarms and line by line alarm printer.</li><li><br></li></ol> | Alarm filtering and characteristics added in OvationApplications and OvPtStudio online help |  |  | SJ March 8, 2017: Updates available in Ovation 3.6.0 FP2 U1 online help. Alarm filtering and characteristics added in OvationApplications and OvPtStudio online help. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Documentation | SJ March 8, 2017: Updates available in Ovation 3.6.0 FP2 U1 online help. Alarm filtering and characteristics added in OvationApplications and OvPtStudio online help. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/Alarms | Documentation | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | SJ March 8, 2017: Updates available in Ovation 3.6.0 FP2 U1 online help. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38052 | FINDING | NIC Interface is reported in PI as 100 MBit on 1Gb Stations and Controllers | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-09 09:07 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-09 09:07 | 72288 |  |  | 2017-03-09 09:07 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-11-21 15:28 |  | <p>On&nbsp;Suzi Network&nbsp;in Pgh - Lab-5 - </p> <p>&nbsp; All&nbsp;Workstations &amp; Controllers are configured in Studio as:&nbsp;</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;Ovation Highway Interface Mode = 1 Gb / auto-negotiate</p> <p>&nbsp;</p> <p>In Point Information (See Attached DU_Records.xlsx)</p> <p>&nbsp; DBS 175 with NIC Teaming shows </p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;Interface (KM) = DAS 1GB Ethernet,&nbsp;&nbsp;Vendor (VE) = Microsoft</p> <p>---</p> <p>&nbsp; Opst 172, 174&nbsp;with OHI are showing</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; Interface (KM) = DAS&nbsp;100 Mbit Ethernet,&nbsp;&nbsp;Vendor (VE) = OHI</p> <p>&nbsp;</p> <p>&nbsp; OCR1100 controllers &amp; VCs are also showing</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; Interface (KM) = DAS&nbsp;100 Mbit Ethernet,&nbsp;&nbsp;Vendor (VE) = OHI</p> <p>---</p> <p>&nbsp; VCH 171, 173 with WRTap Bridge are showing&nbsp;</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; Interface (KM) = Generic Ethernet,&nbsp;&nbsp;Vendor (VE) = Unknown</p> <p>-------</p> <p>msb 12/13 - </p> <p>&nbsp;With OVA360FP1_U1 loaded (Change set 72144) in Pt-Info:</p> <p>&nbsp; 175 - Ws12R2 shows KM = Generic, 172 - W10 shows 100 Mbit, 174 - W7 shows 1Gb</p> <p>---</p> <p>msb - 12/15/2016 - Partially failed:</p> <p>&nbsp;reloaded OHI on 172 from the FP1 Ethernet\OHI-WIN10 directory</p> <p>&nbsp;&nbsp; 172 - W10 shows KM = 1Gb, VE = OHI, K0 = Active, K1 = Available. - OK</p> <p>&nbsp;&nbsp; 174 - W7&nbsp;&nbsp; shows&nbsp;KM = 1Gb, VE = OHI, K0 = Active, K1 = Available. - OK</p> <p>&nbsp;&nbsp; 175 - Ws12R2 - NIC Teaming shows KM = Generic, VE = Unknown, K0 = Active, K1 = Available. - Wrong</p> <p>---</p> <p>msb - 3/09/2017- OK</p> <p>&nbsp;&nbsp; 172 - W10 shows KM = 1Gb, VE = OHI, K0 = Active, K1 = Available. - OK</p> <p>&nbsp;&nbsp; 174 - W7&nbsp;&nbsp; shows&nbsp;KM = 1Gb, VE = OHI, K0 = Active, K1 = Available. - OK</p> <p>&nbsp;&nbsp; 175 - Ws12R2 - NIC Teaming shows KM = 1Gb, VE = Microsoft, K0 = Active, K1 = Available. - OK</p> | none |  |  | Examine point information DU record status tab and ensure information is correct | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software | none |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2 U0 |  | Suzi Network - 1Gb NIC Interface |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 2 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | Modify OHI driver for Windows 7 and Windows 10 to correctly detect link speeds | 12 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 109854
38056 | FINDING | Service of OPC A&E server is continuously restarting. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 10:18 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 10:18 | 71866 |  |  | 2017-01-03 10:18 |  |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2016-11-22 05:39 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.5in;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">It is observed that after installation of FP1 in OV 3.6.0,</span><span style="font-size:12pt;"><font face=Calibri> S<font face=Tahoma>ervice of </font></font></span><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">OPC A&amp;E server is continuously restarting due to which communication is not established between TCI drop and OPC A&amp;E server drop.</span></p><p style="margin:0in 0in 0pt 0.5in;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;"><br></span></p><p style="margin:0in 0in 0pt 0.5in;"><br></p><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;"><p style="margin:0in 0in 0pt 0.5in;"><font face="Times New Roman"> </font><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">To resolved this issue, Performed following steps.</span></p><p style="margin:0in 0in 0pt 0.5in;"><font face="Times New Roman"> </font><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">&nbsp;</span><font face="Times New Roman"><br></font></p><ul style="list-style-type:disc;direction:ltr;"><li style="color:rgb(0, 0, 0);font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Uninstall Feature pack 1 from drop157.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Uninstall the Ov 3.6.0 from drop157.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Reboot the system.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Install the Ov 3.6.0 and complete the desire steps.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Load the latest OVA 3.6.0 Patches.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Tahoma&quot;,sans-serif;font-size:12pt;">Reboot the system.</span></p></li></ul><p style="margin:0in 0in 0pt 0.5in;"><font face="Times New Roman"> <br></font></p></span><p style="margin:0in 0in 0pt 0.5in;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | IC 1/3/17 &gt;&nbsp;Added notes to Ov 3.6.0 FP1 DIR and OPC AES 2.0 DIR. Posted OPC AES DIR, closed finding.&nbsp;. | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Matreja, Shyam EMR SYSS PWS PITT | [7 empty] | Implementation | OVA360FP1_U1 |  | <font face="Times New Roman" size=3> </font><ul style="list-style-type:disc;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;</span>Ov Release: - Ov 3.6.0 with FP1</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;</span><span style="">&nbsp;</span>DBS Drop: - Drop100</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;</span>OCR 1100: - Drop22/72</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span>ELC Build: - ELC 1.4_U7</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;</span><span style="">&nbsp;</span>Primary ELC module Configuration: - Branch1, Slot3 (192.168.36.225)</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span>Partner ELC module Configuration: - Branch2, Slot3 (192.168.36.226)</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span>Partner TCI Drop: - Drop189</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span>TCI Version: - TCI 2.0_U4</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:14pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-size:14pt;"><span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</span>Partner OPC A&amp;E Server Drop: - Drop157</span></p></li></ul><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Note added to DIR | 0 |  |  | Agarwal, Gaurav EMR SYSS PWS NOIDA | Validation |  | <p>A new version of the OPC Alarm Event Server will also be required.</p> <p>---</p> <p>msb - 12/14 - </p> <p>&nbsp;Please check with AES200001-12132016174102 patch.</p> | 14 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 107297
38070 | FINDING | MHM-FP1: Ovation MHM UI crashes on pressing Enter, placing curser on any blank space in the UI | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-12-04 21:23 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-12-04 21:23 |  |  |  | 2016-12-04 21:23 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-11-23 04:56 |  | <p>In Ov3.6.0-FP1 MHM module is configured.&nbsp; Right click&gt; Engineer to&nbsp;open its Ovation MHM UI.</p><p>Place the curser in any blank space in the configuration area (Not in hierarchy area).</p><p>Press Enter. Ovation MHM UI crashes.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | Brown, Sean EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | Ov3.6.0-FP1_U0, DRop36/86, MHM module in Branch1, Slot1. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>prs 5Dec2016: As per Sunil- </p><p><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">&quot;When you’ve clicked on a blank space…and press Enter…the MHM UI window close…that is because the current system focus is likely set on the “OK” button. So it’s like pressing the OK button.&quot; </span></p><p style="margin:0in 0in 0pt;"><span style="color:rgb(31, 73, 125);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;"><font color="#000000">Hence closing the finding.</font></span></p><font face="Times New Roman" size=3> </font> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps are:</p><ol><li>In Ov3.6.0-FP1 MHM module is configured.&nbsp; </li><li>Right click&gt; Engineer to&nbsp;open its Ovation MHM UI.</li><li>Place the curser in any blank space in the configuration area (Not in hierarchy area).</li><li>Press Enter. Ovation MHM UI crashes.</li></ol> |  | OVA360FP1_U0 |  |  | FINDING | [6 empty] | 106114
38074 | FINDING | Setpoint algorithm R5 field won't reconcile | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-12-13 02:24 | [11 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-12-13 02:24 | 71864 |  |  | 2016-12-13 02:24 |  |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | 2016-11-23 05:11 |  | <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Setpoint algorithm R5 field won't reconcile</span> |  |  |  | Should be able to reconcile the R5 field now as per the original validation steps. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA360FP1U1 |  | OV 3.6.0 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  | Updated algParam.dat and setpoint.c. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>As per validation step of SDR 37815&nbsp;I performed following:</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>A.<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font><font size=3>INIT = YES, RECO = NO - Working fine</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>B.<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font><font size=3>INIT = NO, RECO = YES - When the controller boots up the setpoint algorithm will use the default value of the connected output point.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>Normally this is 0.0, however if the output point has an Initial Value defined, it will use that value.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>Verify that as the setpoint changes via any operator action, the value in R5 is also changing.(working fine till here)</font></font><font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Further to Verify that the :</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>1.<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font><font size=3>value in R5 can be Database Reconciled and</font></font><font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>2.<span style="">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></font><font size=3>Control Reconciled back to the database and Control Sheet.</font></font><font face="Times New Roman" size=3> </font></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3> </font><font face=Calibri><font size=3>I perform following:</font></font><font face="Times New Roman" size=3> </font></p><ul><li><div style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>Reconciled through developer studio by right click on the controller in which setpoint algorithm sheet exist but 0 differences found popup appears.</font></font><font face="Times New Roman" size=3> </font></div></li><li><div style="margin:0in 0in 0pt;"><font face="Times New Roman" size=3> </font><font face=Calibri><font size=3>On opening of control sheet also reconcile tuning parameters popup not appears(Control builder settiing has reconcile enabeled)</font></font><font face="Times New Roman" size=3> </font></div></li></ul> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106486
38080 | FINDING | MHM-FP1: MHM firmware is not available for OCR 400 controllers with OVA360FP1 Patch. | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-12-12 23:34 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-12-12 23:34 | 71912 |  |  | 2016-12-12 23:34 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-11-25 03:23 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">MHM firmware is not available for OCR 400 controllers with FP01 Patch.</span></p><p style="margin:0in 0in 0pt;"><span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">We have configured MHM device ,driver and MHM module in OCR 400 controller. When clicked on download available firmware via <span style="">&nbsp;</span>controller diagnostic window, no MHM related files can be found.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;"><br></span></p><p><br></p> |  |  |  | <p><br></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software | Added the&nbsp;environment variables for these files. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | Saxena, Pratishtha EMR SYSS PWS NOIDA | Brown, Sean EMR SYSS PWS PITT | [5 empty] | Implementation | Ovation 3.6.0 Feature Pack 1-12092016091132 |  | <p>Ovation 3.6.0 + OVA360FP1</p><p>OCR 400 Controller - Drop 40/90 (GEC)</p> |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | <p>The files are now listed properly and downloadable on&nbsp;the OCR400.</p><p><br></p><p>SDK (12/13/2016): All the MHM supporting files are listed properly in OVA360FP1_U1&nbsp;build and downloadable on the OCR 400 controller hence&nbsp;closed this finding. </p> | 13 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <span style="color:black;font-family:&quot;Segoe UI&quot;,&quot;sans-serif&quot;;font-size:9pt;">We have configured MHM device ,driver and MHM module in OCR 400 controller. When clicked on download available firmware via <span style="">&nbsp;</span>controller diagnostic window, no MHM related files can be found.</span> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106482
38082 | FINDING | 360FP1 MHM_Plots : Ovation Machine Works Application Support not available in FP1_U0 | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-12-20 05:43 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-12-20 05:43 |  |  |  | 2016-12-20 05:43 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2016-11-25 05:05 |  | Ovation Machine Works Application Support not available in FP1_U0 |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Ovation Machine Works/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Saxena, Pratishtha EMR SYSS PWS NOIDA | Kumar, Sudheer EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA360FP1_U1 |  | Ovation 3.6.0 + FP1_U0 |  | Ovation for Windows | Ovation | Operator Station/Ovation Machine Works | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | PS 20Dec16: The application is available in U1 and all types of plots can be seen. Hence closing as FIXED. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 106890
38088 | FINDING | MHM FP1 : Module record option is disable for MHM module in the controller diagnostic window. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-12-12 23:38 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-12-12 23:38 |  |  |  | 2016-12-12 23:38 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2016-11-28 03:07 |  | Module record option is disable for MHM module in the controller diagnostic window.We cannot open MHM module record through right click on MHM module in controller diagnostic window. |  |  |  | <p>Test module record appears for DEC and MHM. &nbsp;</p><p><br></p><p>SDK 12/12/2016 : Module record option is enable for MHM module in new build patch&nbsp;&quot;<span style="font-family:&quot;Calibri&quot;,&quot;sans-serif&quot;;font-size:11pt;">Ovation 3.6.0 Feature Pack 1-12092016091132&quot;</span>&nbsp;hence closed the finding.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software | <div>Dev Changeset = 71922</div><div>Int Changeset = 71923</div><div>FP1 Changeset = 71924</div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Saxena, Pratishtha EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | Brown, Sean EMR SYSS PWS PITT | [5 empty] | Implementation | Ovation 3.6.0 Feature Pack 1-12092016091132 |  | <p>Ovation 3.6.0 + OVA360FP1 + OCR 1100 and OCR 400 controller </p> |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | <span style="font-size:12px;">Added MHM &amp; DEC to list of modules with hardware address in the &quot;upper&quot; word of the HD field.</span> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 106485
38089 | FINDING | MHM-FP1: Tacometer DC offset value is not calculated correctly | Willis, John W AUTOSOL PSS KNOX | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-12-06 02:45 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-12-06 02:45 |  |  |  | 2016-12-06 02:45 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2016-11-28 07:18 |  | <p>MHM-FP1: Tacometer DC offset value is not calculated correctly.</p> <p>&nbsp;</p> <p>Tachometer is configured in MHM channel-8. Ovation points are assigned for DC, RPM and other parameters of Tachometer. controller is loaded.&nbsp;</p> <p>It is observed that DC offset value is not calculating correctly as seen in Point Review application. Please refer to the below table.</p> <p>&nbsp;</p> <p> <table style="WIDTH:140pt;BORDER-COLLAPSE:collapse;" cellspacing=0 cellpadding=0 width=186 border=0> <colgroup> <col style="WIDTH:66pt;" width=88> <col style="WIDTH:74pt;" width=98> <tbody> <tr style="HEIGHT:15.75pt;"> <td class=xl71 style="BORDER-TOP:windowtext 1pt solid;HEIGHT:15.75pt;BORDER-RIGHT:windowtext 0.5pt solid;WIDTH:66pt;BORDER-BOTTOM:windowtext 1pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=21 width=88><strong><font color="#000000" size=3 face=Arial>Given Offset</font></strong></td> <td class=xl72 style="BORDER-TOP:windowtext 1pt solid;BORDER-RIGHT:windowtext 1pt solid;WIDTH:74pt;BORDER-BOTTOM:windowtext 1pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;" width=98><strong><font size=3><font color="#000000"><font face=Arial>Received DC<span style="">&nbsp;</span></font></font></font></strong></td></tr> <tr style="HEIGHT:14.25pt;"> <td class=xl65 style="BORDER-TOP:#f0f0f0;HEIGHT:14.25pt;BORDER-RIGHT:#f0f0f0;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=19><font color="#000000" size=3 face=Arial>&nbsp;</font></td> <td class=xl66 style="BORDER-TOP:#f0f0f0;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 0.5pt solid;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>&nbsp;</font></td></tr> <tr style="HEIGHT:14.25pt;"> <td class=xl69 style="BORDER-TOP:windowtext;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 0.5pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=19><font color="#000000" size=3 face=Arial>2V</font></td> <td class=xl70 style="BORDER-TOP:windowtext;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>1.073 V</font></td></tr> <tr style="HEIGHT:14.25pt;"> <td class=xl69 style="BORDER-TOP:windowtext;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 0.5pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=19><font color="#000000" size=3 face=Arial>2.5V</font></td> <td class=xl70 style="BORDER-TOP:windowtext;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>1.53 V</font></td></tr> <tr style="HEIGHT:14.25pt;"> <td class=xl69 style="BORDER-TOP:windowtext;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 0.5pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=19><font color="#000000" size=3 face=Arial>3V</font></td> <td class=xl70 style="BORDER-TOP:windowtext;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>2.07 V</font></td></tr> <tr style="HEIGHT:14.25pt;"> <td class=xl69 style="BORDER-TOP:windowtext;HEIGHT:14.25pt;BORDER-RIGHT:windowtext 0.5pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=19><font color="#000000" size=3 face=Arial>4V</font></td> <td class=xl70 style="BORDER-TOP:windowtext;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 0.5pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>3.2 V</font></td></tr> <tr style="HEIGHT:15pt;"> <td class=xl67 style="BORDER-TOP:windowtext;HEIGHT:15pt;BORDER-RIGHT:windowtext 0.5pt solid;BORDER-BOTTOM:windowtext 1pt solid;BORDER-LEFT:windowtext 1pt solid;BACKGROUND-COLOR:transparent;" height=20><font color="#000000" size=3 face=Arial>&nbsp;</font></td> <td class=xl68 style="BORDER-TOP:windowtext;BORDER-RIGHT:windowtext 1pt solid;BORDER-BOTTOM:windowtext 1pt solid;BORDER-LEFT:windowtext;BACKGROUND-COLOR:transparent;"><font color="#000000" size=3 face=Arial>&nbsp;</font></td></tr></tbody></table></p> <p>&nbsp;</p> <p>Picture&nbsp;of Given Input Signal and Corresponding received values are attached with the finding alongwith XML file.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/MHM/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | Steele, Kevin D AUTOSOL KNOX | [7 empty] | Implementation |  |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><span style="FONT-SIZE:10pt;"><font color="#000000" face="Times New Roman">Ov3.6.0-FP1_U0, OCR1100 Drop36/86, MHM module in Branch1, Slot1.</font></span></p> |  | Ovation for Windows | Ovation | Controller/MHM | Software | Standard Release | 3.6.0 |  |  | Cannot Duplicate | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | prs 6 Dec 2016: The values for DC offset are correct. It was a local controller issue. Hence closing this finding. Thanks | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps are:&nbsp;</p> <ol> <li>Tachometer is configured in MHM channel-8. </li> <li>Ovation points are assigned for DC, RPM and other parameters of Tachometer. </li> <li>controller is loaded.&nbsp;</li> <li>It is observed that DC offset value is not calculating correctly as seen in Point Review application.</li></ol> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106197
38098 | FINDING | Hardening SVTP 3.6.0_Hardening_SVTP_rev1.3.xlsx should add testing on Win10 systems | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2016-11-29 00:09 | [11 empty] | USPITTFSService | 2016-11-29 00:09 | [7 empty] | Joshi, Parmesh EMR SYSS PWS NOIDA | 2016-11-29 00:09 |  | <p>Hardening &quot;SVTP 3.6.0_Hardening_SVTP_rev1.3.xlsx&quot;, &quot;Ovation&quot; tab&nbsp;should add sections for&nbsp;testing on Win10 systems.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <table width=64 style="width:48pt;border-collapse:collapse;" border=0 cellspacing=0 cellpadding=0><font face="Times New Roman" size=3> </font><colgroup><col width=64 style="width:48pt;"><font face="Times New Roman" size=3> </font><tbody><tr height=100 style="height:75pt;"><font face="Times New Roman" size=3> </font><td width=64 height=100 style="border:0px black;width:48pt;height:75pt;background-color:transparent;"><font face=Calibri size=3>OV 3.6.0 Win 10 Hardening</font></td><font face="Times New Roman" size=3> </font></tr><font face="Times New Roman" size=3> </font></tbody></table> |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Joshi, Parmesh EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | Win 10 |  |  | FINDING | [6 empty] | 105813
38163 | FINDING | DEC module configuration for network is improperly labeled | Swartz, Mark EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:09 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-05 16:13 |  | For the DEC module configuration, the NIC 1 and 2&nbsp;Interface mode has an option labeled 1GB / auto-negotiate.&nbsp; See attached 1gb.png.&nbsp; This should be 1GB/full duplex as in 3.5.1 and as it gets put into the configuration file (see attached EPConfig0-4870.xml). |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2 |  | Ovation 3.6.0 +FP1 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The 1GB / Full duplex is no longer an option.&nbsp; The software which generates the EPConfig.xml file will be changed to properly refer to the interface mode as &quot;1000/Auto&quot; when the user selects &quot;1GB / auto-negotiate&quot; in the configuration UI. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Configure a DEC module. |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38173 | FINDING | Ovation Developer Studio Allows addtion of SCADA3.0.0 protocols without having license | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2018-03-28 00:12 | [11 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2018-03-28 00:12 | 81927 |  |  | 2018-03-28 00:12 |  |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2016-12-06 03:00 |  | <p>It has been observed that in any Ovation 3.6.0 drop (EWS or DBS), when we try to add SCADA3 protocols (MODBUS or DNP3 etc.), it allows to add the protocol&nbsp;successfully without&nbsp;SCADA 3.0 license.</p><p><br></p> |  |  |  | <p>The affected area is the software which performs system validation checks during SCADA3 protocol addition (via Ovation Developer Studio or OvPtImport).</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Plymire, Alvan AUTOSOL PWS PITT | [8 empty] | Implementation | OVA360FP4_U2 |  | Ov3.6.0, SCADA3.0.0_U2 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | <p>The same Validations checks which are performed for ELC protocols will also be performed for SCADA 3 protocols.</p><p>ST(03/28/2017): Tested in Ov360FP4_U2 build and found OK. So closing this finding.</p> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Install SCADA3.0_U2 build on DBS or EWS&nbsp;(e.g drop100 - DBS, Ovation 3.6.0) without having SCADA 3.0 license in the system.&nbsp;</p><p>2. Open Ovation Developer Studio in drop100&nbsp;and insert SCADA3 object&nbsp;from Configuration options of the drop100.</p><p>3. Insert SCADA3 MODBUS Master protocol.</p>&nbsp;&nbsp;&nbsp; Modbus protocol added successfully without having license. |  | OVA360FP4 |  |  | FINDING | [6 empty] | 125982
38196 | FINDING | DEC Ovation System Registration reports DEC module as G04 from controller | Staab, Randy AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Perdeus, Matthew AUTOSOL PWS PITT | 2017-07-14 13:33 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-07-14 13:33 |  |  |  | 2017-07-14 13:33 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-07 10:11 |  | <p>The DEC module 5X00658G01 returns an error stating that the controller is reporting&nbsp; 5X00658G04 rather than G01. Please see attached.</p><p><br></p> |  |  |  |  | 0 |  |  |  | 360FP3U2 shows correct group. | 0 |  | Ovation for Windows/System Registration Utility/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0 + FP1 |  | Ovation for Windows | Ovation | System Registration Utility | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Run system registration on a system that has a 5X00658G01 configured. |  | OVA360FP1 |  |  | FINDING | [6 empty] | 115956
38197 | FINDING | DEC directory does not get created in controller | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-08 09:07 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-08 09:07 |  |  |  | 2016-12-08 09:07 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-07 15:57 |  | The /ata0/wdpf/dpu/data/dxc directory does not exist in the controller.&nbsp;&nbsp; The EPConfig.xml files are not able to be downloaded to the controller due to this missing directory. Withouth these files, the DEC modules will not completely boot up. |  |  |  |  | 0 |  |  |  | The controller creates this directory as needed during the download process.&nbsp; The issue is that this file is not being download during the load process. This finding is closed and a new finding 38217 was created to address the download issue. | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | Ovation 3.6.0 + FP1 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>see me if necessary. </p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106370
38216 | FINDING | Audio Alarms are not working with OVA360FP1 | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-13 20:09 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-13 20:09 | 72144 |  |  | 2016-12-13 20:09 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-08 08:34 |  | <p>Audio Alarms which were working with Ov3.6.0 are not working after installing OVA360FP1_U0.</p> <p>No audio&nbsp;is audible after configuring audio alarms for alarms.</p> <p>&nbsp;</p> <p>Tried with all the alarm priorities (1-8) and different destinations also, but not working.</p> <p>Verified with another Ovation 3.6.0 setup in GEC (which is not having OVA360FP1) and audio alarms are working fine on that setup.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA360FP1_U1 |  | Ov3.6.0 EWS Drop157 (Windows 10) updated with&nbsp; OVA360FP1 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | ASG 12/14/2016&gt; Verified that Audio alarms are working as expected after installing OVA360FP1_U1. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Configure Audio alarms for an operator station for applicable point alarm priorities.</li> <li>Download and reboot the operator station.</li> <li>Verify if audio alarms are audible. Also try opening Alarm application to verify alarms upcoming in the list and verify if audio alarms are audible.</li></ol> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106521
38217 | FINDING | DEC - The automatic download of configuration files for DEC module during the load procedure is not occuring. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-09 15:57 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-09 15:57 | 72141 |  |  | 2016-12-09 15:57 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-08 08:46 |  | During the load of the controller, the DEC configuration files should be downloaded to the controller.&nbsp; This step is not occurring. |  |  |  | <p>The affected area is in the portion of the &quot;load routine&quot; where application configuration files are implicitly downloaded to the target.&nbsp; The routine to handle the DEC module embedded platform configuration file has been added and enabled.&nbsp; The applicable binary is OvPtSysApi.dll (for the database server).</p><p>No specific test recommendations other than what has been described in the &quot;Steps to Reproduce&quot;.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Costlow, Kim EMR SYSS PWS PITT | [9 empty] | Implementation | OVA360FP1 |  | Ovation 3.6.0 + FP1 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The implicit download of the DEC configuration file was inadvertently left out of the 3.6.0 branch of software.&nbsp; The underlying support exists, but not the actual call from the &quot;load routine&quot;. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Configure DEC module and modify module configuration with network information, etc.&nbsp; Load the controller. Check intermediate query file for this controller or check the /ata0/wdpf/dpu/data/dxc directory to see that file was not downloaded. |  | OVA360FP1 |  |  | FINDING | [6 empty] | 106438
38225 | FINDING | 'Set All' option for 4th position of characteristic field in alarm window is not working. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Garg, Amit AUTOSOL PWS NOIDA | 2017-03-01 02:34 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2017-03-01 02:34 | 72744 |  |  | 2017-03-01 02:34 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-12-09 01:54 |  | <p>Set All option available in the characteristics field of the&nbsp;filter tab in alarm window is not working for the 4th characteristic position.</p><p>snapshot is attached for your reference.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2 U0 |  | <p>OV3.6.0</p><p>Drop153 W7 64b</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Configure alarm to filter by characteristics from developer studio.</p><p>2. Open the alarm window and click on the characteristics option in the Filter tab.</p><p>3. Navigate to the 4th position of the characteristic field.</p><p>4. click on the clear all option all the fields will be deselected.</p><p>5. Now click on the Set All option, Fields will not be get selected.</p><p><br></p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 109481
38226 | FINDING | Default settings for characteristics positions does not work if numerical default values are used in alarm configuration. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Garg, Amit AUTOSOL PWS NOIDA | 2017-03-01 02:42 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2017-03-01 02:42 | 72744 |  |  | 2017-03-01 02:42 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-12-09 02:21 |  | <p>For characteristic positions(2,3,4,5,6,7,8) numerical values can be defined for a point and therefore user should be able to do default settings using numerical value for characteristic positions(2,3,4,5,6,7,8), but when numerical values(0-9) are used as default values in alarm configuration, alarm window does not open using defined numerical default values.</p><p>Snapshot is attached for your reference.</p><p><br></p><p>Similar behavior &nbsp;is observed with <strong>predefined characteristics filter</strong> when numerical values(0-9) are used for characteristic positions(2,3,4,5,6,7,8).&nbsp;</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2 U0 |  | <p>OV3.6.0</p><p>Drop153 W7 64b</p> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open the alarm configuration window in developer studio.</p><p>2. configure alarm to filter by characteristics and in normal mode filtering tab define numerical value(0-9) for characteristic positions(2,3,4,5,6,7,8).</p><p>3. Download the drop and then open the alarm window.</p><p>4. Go to the filter tab and&nbsp;click the characteristic filter popup.</p><p>5. check the default configuration of alarm window, the characteristic position where numerical default values were used will not contain the default configuration.</p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 109482
38230 | FINDING | Alarm printer does not print Characteristics column | Augustine, Lisa EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:13 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-09 11:31 |  | Alarm printer does not print Characteristics column, while the Alarm list shows that column on OPCON.<br>Characeristics can be used to filter alarms in line by line alarm printer, hence this coulmn must be available in Alarm printer. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ov3.6.0 EWS Drop157 (Windows 10) updated with&nbsp; OVA360FP1_U0. |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38239 | FINDING | DEC - On some systems (not all), the "no Controller" timeout behavior does not behave as expected | Wimer, Walter L EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-11 10:22 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-11 10:22 |  |  |  | 2017-01-11 10:22 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-12 16:25 |  | <p>This behavior appears on some Ovation systems, but not on others. &nbsp;It is not yet known why this is true.</p><p><br></p><p>Redundant modules are configured for timeout action of 'relinquish control'.&nbsp;After powering off both redundant controllers and timeout period expires, the in control module gives up control to the partner module, stating '<span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">EPR state INCTRL, Non Critical Fail==&gt;Giving Control to OK Partner Going to FAIL state’, even though the partner is not ‘OK’ as he can’t communicate to the controllers either.&nbsp;</span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">This was expected to work as described in resolution section of F#36947 :</span></p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 8pt;"><span style="color:black;line-height:105%;font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">When the controlling DEC module detects a loss of R-Line communication, the controlling module now waits approximately 50 milliseconds to see if the partner DEC module remains &quot;ok&quot; or not. &nbsp;If the partner module has lost communication as well, then the partner will immediately go to the &quot;not ok&quot; state. &nbsp;The controlling module will base its behavior on the partner's state. &nbsp;If the partner goes &quot;not ok&quot;, then the controlling module will retain control and will carry out the configured action (e.g. trip the generator). &nbsp;If the partner remains &quot;ok&quot; for 50 milliseconds, then the controlling module will release control to the partner module and thus let the partner module take charge of the situation.</span></p><p><font face="Times New Roman" size=3> <br></font></p></span><p><br></p> |  |  |  |  | 0 |  |  |  | IC 1/11/17&gt; created SDR #38443 to track the issue, closed Finding. | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OVA360FP1 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Follow steps listed in description. </p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 107588
38244 | FINDING | AY field shows different values on different Ovation Applications | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 08:28 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 08:28 |  |  |  | 2017-01-03 08:28 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-13 20:20 |  | <p>For points using Sensor Alarm Characteristics, when the point is in Sensor Alarm, Sensor Alarm Characteristics are used for filtering the alarms.</p> <p>When a point is put into Sensor Alarms, Ovation applications which use filtering based on Characteristics (destination) shows Sensor characteristics in AY field (for example Alarm Application)&nbsp;where as the Ovation applications which do not use filtering&nbsp;shows current characteristics in AY field (for example Point Info).</p> <p>&nbsp;</p> <p>So there is a mismatch between values of AY field in different applications and <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:107%;"><font color="#000000" size=2>it could create confusion to the operator viewing both the applications at a time.</font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ov3.6.0 EWS Drop157 (Windows 10) updated with&nbsp;OVA360FP1_U1 |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 107292
38252 | FINDING | In SIS Diagnostics tool, The SNR showing error message on Firmware Revision option. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:19 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-12-14 05:09 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">In SIS Diagnostics, The SNR showing error message &quot; Please upgraded the device with the supported firmware”&nbsp;on Firmware Revision option .</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">( Please find attached snapshot of “Error_SNR.jpg”)</span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">However Firmware of SNR has been already upgraded &amp; it is also showing in SIS Diagnostics as Rev 2.1.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">&nbsp;</span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | Joshi, Parmesh EMR SYSS PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | [6 empty] | Implementation |  |  | Ov360+OVA360FP1_U1,Ws12R2,SNR,SIS Controller OCR1100,SDS,LS (1508) |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">1. Firmware has been&nbsp;upgraded of SNR successfully in OVA360FP1_U1</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">2. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Opened the SIS Diagnostics Tool</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">3. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Click on Primary SNR/Secondary SNR</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">4. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Go to Firmware Revision<span style="">&nbsp; </span></span></p><font face="Times New Roman" size=3> </font> |  | OVA360FP1_U1 |  |  | FINDING | [6 empty] | 112961
38253 | FINDING | Firmware Revision of SDS in SIS Diagnostics tool shows wrong version. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 10:44 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-01-03 10:44 |  |  |  | 2017-01-03 10:44 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-12-14 05:11 |  | <font face="Times New Roman" size=3> </font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Firmware Revision of SDS in SIS Diagnostics tool shows wrong version as 3.6.0.81h instead of 3.6.0.134h .</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">&nbsp;Please find attached snapshot of &quot;Error_SDS_Firmware.jpg&quot;.</span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [6 empty] | Implementation |  |  | Ov360+OVA360FP1_U1,Ws12R2,SNR,SIS Controller OCR1100,SDS,LS (1508) |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | IC 1/3/17&gt; added note to 3.6.0 FP1 DIR and closed Findings since this issue will now be tracked as&nbsp;SDR #38392. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">1. Firmware of SDS&nbsp;has been&nbsp;upgraded&nbsp;successfully in Ov360+OVA360FP1_U1</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">2. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Opened the SIS Diagnostics Tool</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">3. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Click on SDS01/SDS01_B</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">4. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Go to Firmware Revision<span style="">&nbsp; </span></span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="">5. </span></span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">It is showing 3.6.0.81h instead of 3.6.0.134h&nbsp;</span></p><font face="Times New Roman" size=3> </font> |  | OVA360FP1_U1 |  |  | FINDING | [6 empty] | 107301
38254 | FINDING | In SIS Diagnostics tool, The SDS showing error message on Firmware Revision option. | Raciborski, Mikolaj AUTOSOL PSS WRSW | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2019-05-27 07:40 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2019-05-27 07:40 |  |  |  | 2016-12-16 15:20 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2016-12-14 05:22 |  | <font face="Times New Roman" size=3><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">In SIS Diagnostics tool, The SDS showing error message &quot;Failed to retrieve SDS firmware name from registry. OvSis key does not exit&nbsp;”&nbsp;</span></p><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">on Firmware Revision option . </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">( Please find attached snapshot of “Error_SDS_Firmware.jpg”)</span></p><font face="Times New Roman" size=3></font><p style="margin:0cm 0cm 0pt;line-height:18pt;"><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">However Firmware of SDS has been already upgraded.</span></p></font><p style="margin:0cm 0cm 0pt;line-height:18pt;">PP: 05/27/2019- The same issue (The SDS showing error message on Firmware Revision option) is also observed in Ov3.7.0+OVA370011.<br></p> |  |  |  |  | 0 |  |  |  | <p><br></p> | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Bridger, Matthew J EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Thakre, Dushyant AUTOSOL PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA |  |  |  | Implementation |  |  | Ov360+OVA360FP1_U1,Ws12R2,SNR,SIS Controller OCR1100,SDS,LS (1508) |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">1. Firmware has been&nbsp;upgraded of SDS successfully in Ov3.6.0+OVA360FP1_U1</span><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">2. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Opened the SIS Diagnostics Tool</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">3. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Click on SDS01/SDS01_B</span></p><p><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">4. </span><span style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Go to Firmware Revision<span>&nbsp; </span></span></p> |  | OVA360FP1_U1 |  |  | FINDING | [6 empty] | 142200
38268 | FINDING | In OVA360FP1_U1 on 1Gb Suzi Network, the 1800 Graphics only shows the left NIC for each Workstaion | Spillane, Donal AUTOSOL PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:25 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2016-12-15 17:14 |  | <p>In OVA360FP1_U1 on 1Gb Suzi Network, the 1800 Graphics only shows&nbsp;the left&nbsp;connection for each Workstaion.</p> <p>&nbsp;</p> <p>175&nbsp; -&nbsp; DBS&nbsp; -&nbsp;&nbsp; Ws12R2 -&nbsp; NIC Teaming - 2 NICs -&nbsp;&nbsp; PI: KM = Generic, VE = Unkown, K0&nbsp;= Active, K1 = Unknown,&nbsp; -&nbsp; Graphics 1800:&nbsp; Left: Green, Right: None&nbsp; -&nbsp; PI wrong, 1800 wrong.</p> <p>172&nbsp; -&nbsp;&nbsp;OpSt&nbsp; -&nbsp;&nbsp;&nbsp;W10 -&nbsp; OHI - 2 NICs -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; PI: KM = 1 Gb, VE = OHI, K0&nbsp;= Active, K1 = Available,&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;1800:&nbsp; Left: Green, Right: None&nbsp; -&nbsp; PI - OK, 1800 wrong.</p> <p>174&nbsp; -&nbsp;&nbsp;OpSt&nbsp; -&nbsp;&nbsp;&nbsp;W7&nbsp; &nbsp;-&nbsp; OHI - 2 NICs -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; PI: KM = 1 Gb, VE = OHI, K0&nbsp;= Active, K1 = Available,&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;1800:&nbsp; Left: Green, Right: None&nbsp; -&nbsp; PI - OK, 1800 wrong.</p> <p>&nbsp;</p> <p>Before U1 was installed &amp; when U1 is removed, Graphics 1800 shows both NICs&nbsp;active as Green &amp; Yellow to match PI.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38280 | FINDING | Historical Review is unable to filter alarms based on Sensor Alarm Characteristics | Augustine, Lisa EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 4 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:24 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2016-12-16 03:33 |  | <p>Historical Review is unable to filter alarms based on Sensor Alarm Characteristics. As observed in Point tab and Common tab of Historical Review application, filtering based on Characteristics is not working for Sensor Alarm Characteristics. If filter is applied for current characteristics or Sensor characteristics, all the instaces including both type of characteristics - 'current and sensor' are displayed.</p> <p>&nbsp;</p> <p>For example, please refer to attached screenshots and text logs from Historical Review.</p> <p>For point <a href="mailto:'ASG_SRF2241_LA1.UNIT0@NET36'">'ASG_SRF2241_LA1.UNIT0@NET36'</a>, current characteristics are set to NORMALPR and sensor alarm characteristics are set to SENSORPR. In Point tab setting the characteristics filter to NORMALPR, the instances of sensor alarms are also displayed (in the even of sensor alarm, sensor alarm characteristics are appliable) alongwith normal alarm and return events. Similarly in Common tab, setting the characteristics filter to SENSORPR, the instances of&nbsp;normal alarms and return events are also displayed.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ov3.6.0 EWS Drop157 (Windows 10) updated with&nbsp;OVA360FP1_U1s |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Validation | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38282 | FINDING | Algorithm Help for RunTime algorithm needs to be updated. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Casteel, Linda EMR SYSS PWS PITT | 2017-01-17 15:09 | [11 empty] | Casteel, Linda EMR SYSS PWS PITT | 2017-01-17 15:09 |  |  |  | 2017-01-17 15:09 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-12-16 03:52 |  | <p>Runtime&nbsp;algorithm description needs to be updated as new Option &quot;INITP&quot; is added to Runtime&nbsp;&nbsp;algorithm as per SDR-37007.</p><p>&nbsp;This option initializes the algorithm from the output points which may be selected to be saved periodically via the &quot;periodic save&quot; feature.&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OW360_R1100</p><p>Algorithm Online Help</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | LC 01/17/2017: Problem is fixed in OW360_R1100 Version 2 January 2017. The manual has been posted to Crossroads. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 107812
38283 | FINDING | DEC - Not all tasks monitored by the watchdog force a module failover when the task fails | Wimer, Walter L EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2016-12-16 15:22 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2016-12-16 13:57 |  | <p>Tasks monitored by the watchdog should create&nbsp;a dead task log and cause a module failover to the backup.&nbsp; </p><p>The failure of task tEPRedund is creating a dead task log and reporting a task failure in the module record, but is not causing a module failover.&nbsp;&nbsp; </p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38302 | FINDING | EIO: Both RNCs indicate Backup Mode when powered on simultaneously | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2017-06-07 07:51 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-06-07 07:51 |  |  |  | 2017-06-07 07:51 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-12-19 12:24 |  | OCR1100 Controller 22/72 (TIMOTHY)<br>EIO:&nbsp; Redundancy Mode = Standard, Network Connectivity = Ovation Network, Remote Node Type = Ovation<br><br>When a node's power supply is turned on both RNCs will indicate Backup Mode after booting (based on the LED pattern).&nbsp; At this point there is no communication with the Ovation I/O.&nbsp; Once the OCR in Control is power cycled and its partner takes Control, the RNC on the same &quot;side&quot; will enter Control Mode and communicate with the I/O.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360010-10312016114645 |  |  | FINDING | [6 empty] | 113895
38303 | FINDING | EIO: Communication occurs only with one OCR/RNC pair | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2017-06-07 07:51 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-06-07 07:51 |  |  |  | 2017-06-07 07:51 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-12-19 12:47 |  | OCR1100 Controller 22/72 (TIMOTHY)<br>EIO:&nbsp; Redundancy Mode = Standard, Network Connectivity = Ovation Network, Remote Node Type = Ovation<br><br>Once an OCR/RNC pair communicates with I/O (Finding 38302), the partner OCR and RNC will not.&nbsp; For example, assume the left OCR and left RNC are in Control.&nbsp; If the left OCR is rebooted and the right OCR takes control, the right RNC stays in Backup.&nbsp; The left RNC LEDs show Control but no Communication.&nbsp; Once the left OCR is placed in Control again, I/O communication will resume.&nbsp; The only known way to force an RNC to take control is to re-seat its partner.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Durbin, Michael EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360010-10312016114645 |  |  | FINDING | [6 empty] | 113896
38316 | FINDING | EIO: RNC node point bits don't appear to match those in the EPS | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Brown, Sean EMR SYSS PWS PITT | 2017-01-05 11:09 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-01-05 11:09 |  |  |  | 2017-01-05 11:09 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-12-20 11:23 |  | OCR1100 Controller 22/72 (TIMOTHY)<br>EIO:&nbsp; Redundancy Mode = Standard, Network Connectivity = Ovation Network, Remote Node Type = Ovation<br><br>The A2 bits of an EIO RNC's RN point do not appear to be correct, based on the EPS.&nbsp; A screen copy of the RN point for an RNC in Control and communicating with I/O as well as the EPS are attached.<br> |  |  |  |  | 0 |  |  |  | Refer to the attached file <span style="font-style:italic;">Correct_RN_Status_Bits.xlsx</span> in Finding <a href="https://uspit-tfs-v.emrsn.org/tfs/web/wi.aspx?pcguid=2605fe0b-34ed-4a68-b4af-085b61e75426&amp;id=38369" target=_blank>38369</a>. | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Durbin, Michael EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [6 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360010-10312016114645 |  |  | FINDING | [6 empty] | 107434
38319 | FINDING | EIO: Addresses are writing over other addresses | Durbin, Michael EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2017-01-30 13:25 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-01-30 13:25 |  |  |  | 2017-01-30 13:25 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-12-20 14:19 |  | OCR1100 Controller 22/72 (TIMOTHY)<br>EIO:&nbsp; Redundancy Mode = Standard, Network Connectivity = Ovation Network, Remote Node Type = Ovation<br><br>Most slots in Node 1 are configured for a Digital Output module.&nbsp; Control writes 16-bit values to eight packed points such that the channel being set matches the branch for Branch X Slot 1 (where X=1-8).&nbsp; There is an output module in Slot 1 of every branch.<br><br>For example:&nbsp; Branch 1 Slot 1 has only Channel 1 (Bit 0) set, Branch 2 Slot 1 has only Channel 2 (Bit 1) set, and so on.&nbsp; The A2 fields of the packed points verify that this is being done.&nbsp; However, each output module in each Slot 1 (Branches 1-8) actually shows Channel 8 (Bit 7) being set.&nbsp; It appears that the 16-bit value for Branch 8 Slot 1 overwrites the values for Branches 1-7 Slot 1.&nbsp; The module in Branch 1 Slot 1 does occasionally toggle between Channel 8 and Channel 7 being set (it should be Channel 1).<br><br>Update:&nbsp; OCR1100 Controller 21/71 (TIMOTHY) has DO modules at 5.3.1.1 and 5.3.1.3.&nbsp; There is also an AO module at 5.3.2.7.&nbsp; The value of the analog point assigned to Channel 1 of the AO module at 5.3.2.7 is causing the DO LEDs at 5.3.1.1 and 5.3.1.3 to change (rather than the values of the packed points assigned to the DO modules).<br> |  |  |  |  | 0 |  |  |  | Resolved with FPGA Revision bB.<br> | 0 |  | Ovation for Windows/Controller/Third Party Communications/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [8 empty] | Implementation | FPGA rev bB |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | IC per 1/26/17 Val+Dev Mtg&gt; fixed by Tim piper in rev bB of FPGA. Val should retest. | 11 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OVA360010-10312016114645 |  |  | FINDING | [6 empty] | 108189
38323 | FINDING | Installation order for Ovation3.6.0 Patches are not correct and requires un-installation of critical patch | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2016-12-22 00:40 | [11 empty] | USPITTFSService | 2016-12-22 00:40 |  |  |  | 2016-12-20 21:51 |  |  |  | Mittal, Utkarsh AUTOSOL PWS NOIDA | 2016-12-20 21:39 |  | <p><font size=3>Installation order for Ovation3.6.0 Patches are not correct and requires un-installation of critical patch.</font></p> <p><font size=3>Please see the attached file for reference-<font color="#000000"><em>10_InstallationOrderofPatches.PNG</em></font><span style="FONT-SIZE:13pt;FONT-FAMILY:&quot;Cambria&quot;,serif;COLOR:#4f81bd;LINE-HEIGHT:115%;"></span></p></font> <p><font size=3></font>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:115%;"><font color="#000000"> <p class=MsoNormal style="MARGIN:0in 0in 10pt;"><font size=3>Ovation3.6.0 updated with OVA360006 -09272016132658.</font><span class=Heading2Char><span style="FONT-SIZE:13pt;LINE-HEIGHT:115%;"></span></span></p></font></span> |  | Ovation for Windows | Ovation | General | Software | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Mittal, Utkarsh AUTOSOL PWS NOIDA | Software Quality |  | <p><font size=3>Resolved With SCADA 3.0 U1 build dated 24-10-16</font></p> <p><font size=3></font>&nbsp;</p> <p><font size=3>UM(22/12/2016): </font></p> <p><font size=3>Resolved with released OVA360005 patch. Also corrected the product category and other relevent fields for the finding.</font></p> | 5 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p class=MsoNormal style="MARGIN:0in 0in 12pt;LINE-HEIGHT:normal;"><span style=""><font color="#000000" size=3>Ovation patch OVA36006 was for adding SCADA3 functionalities but that patch installation order&nbsp;was not correct. For installing patch6, patch5&nbsp;was mandatory but for installing patch5, patch1 and patch4 were required to be uninstalled.<br></font><font color="#000000" size=3>Hence&nbsp; needed to uninstall patch 1 and patch 4 before installing patch 5 and 6.<br>&nbsp;After this, needed to install patch 1 and 4 again</font></span><span class=Heading2Char><span style="FONT-SIZE:13pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;FONT-WEIGHT:normal;"></span></span></p> | EPM Product Development | OVA360005 |  |  | FINDING | [6 empty] | 107068
38352 | FINDING | SDR37769: "GBNT GUI has some problems when displayed on a 4K monitor (or even when windows font scale set to LARGE on normal monitor" failed | Johnson, Kathy EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-09-28 08:43 |  |  |  | 2017-01-03 11:04 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2016-12-26 04:10 |  | <p>while testing the SDR37769 following items were found not working:</p><p><br></p><p>a) GBNT: grid options is not working properly. (please refer attached snapshot)</p><p>b) GBNT: Button dialog is going out of screen.</p><p>c) Some Draw Toolbar Options goes out of screen with monitor <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:12pt;">resolution (1280*1024) .</span></p><p><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><span style="color:black;font-size:12pt;"><font face=Calibri><br></font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>OV3.6.0 </p><p>drop153, OS-W7 64b</p><p><font face=Calibri>Monitor-Dell P2213</font></p><p><br></p><p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p style="margin:0in 0in 0pt;"><span style="font-size:12pt;"><font face=Calibri>1.Monitor Used-Dell P2213</font></span></p><p><font face="Times New Roman" size=3></font><span style="font-size:12pt;"><font face=Calibri>2.Resolution-1680*1050(maximum resolution)</font></span></p><p><font face="Times New Roman" size=3></font><span style="color:black;font-size:12pt;"><font face=Calibri>3.Font scale display property to LARGE [150%]</font></span></p><p><span style="color:black;font-size:12pt;"><font face=Calibri>4. Open Graphic builder.</font></span></p><p><span style="color:black;font-size:12pt;"><font face=Calibri>5. Click on the grid options. Grid will not be properly aligned along the screen.</font></span></p><p><span style="color:black;font-size:12pt;"><font face=Calibri>6. Now Open the GBNT: Button dialog box. Some part of dialog box will not be accessible.</font></span></p><p><span style="color:black;font-size:12pt;"><font face=Calibri>7. Now Change the monitor resolution to (1280*1024). Now observe the Draw Toolbar Options in Graphic Builder. Some of the options will be out of screen and hence not accessible.</font></span></p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 118595
38369 | FINDING | EIO: RNC node alarm states don't match those in the EPS | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2017-01-05 11:09 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-01-05 11:09 |  |  |  | 2017-01-05 11:07 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2016-12-29 08:59 |  | EIO RNC alarm states don't correspond to the descriptions in the latest EPS.&nbsp; Please refer to Finding <a href="https://uspit-tfs-v.emrsn.org/tfs/web/wi.aspx?pcguid=2605fe0b-34ed-4a68-b4af-085b61e75426&amp;id=38316">38316</a> and its attachments.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | Ovation 3.6.0 Feature Pack 1-12092016091132 |  |  | FINDING | [6 empty] | 107435
38384 | FINDING | Point Information application got hang when Ovation Point Browser popup of PI application tried to browse all 500K points of 52 Drops. | Augustine, Lisa EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:25 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2017-01-02 22:51 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>When 500K points of 52 Drops are browsed through Ovation Point browser popup of Point information application, Ovation Point Browser displayed a message for unhandled exception of Microsoft .Net framework. </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font size=3><font face=Calibri>Wait for some time and after that Point Information application got hang<span style="color:black;">.</span></font></font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  |  | Implementation |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>DC+DB Server Drop200 (Windows2012 R2) With Ovation 3.6.0 FP01 having 500K points</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>3 VCH - Drop251, Drop252 and Drop253(Windows 7 SP1)</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>OPS- Drop201 (Windows2012 R2)</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Physical Controller OCR1100 – Drop1/Drop51</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Vxsim Drops – Drop2 to Drop50</font></p><font face="Times New Roman" size=3> </font> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Software Quality |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3><ol><li>Open Point Information application.</li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">In Select Point Frame, click on Browse for Points Symbol.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Ovation Point Browser popup gets open.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Drops from ribbon section.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Verify all Drops are selected, if not click on set all button.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Start Button.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Points Search started and searched around 150K points very soon after that taking a lot time to search remaining points.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">After some time Ovation Point Browser displayed a message for unhandled exception of Microsoft .Net Framework. </p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Please find the attached <b>“Microsoft.NetFrameWork.png” </b>screenshot and <b>“Microsoft .net Framework messages.txt”</b> file for reference.</p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Wait for some time and after that Ovation Point Browser (Not Responding) popup appeared and PI got hang. </p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Please find the attached “<b>Point_Information_Hang.PNG</b>” screenshot.</p></li></ol><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><font face="Times New Roman" size=3> <br></font></p><p style="margin:0in 0in 0pt;"><b>Observation:</b> Microsoft .Net frame work is unable to handle the Ovation Point Browser application if more than 500K points are used in the Ovation 3.6.0.</p><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><font face="Times New Roman" size=3> <br></font></p><ol><p style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><font face="Times New Roman" size=3> <br></font></p></ol><p> <br></p></font><p><br></p><p><font face="Times New Roman" size=3> <br></font></p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38388 | FINDING | “Performing Ovation database analysis...” is taking more than 40 minutes during import of file containing 10 points when database has 500k points and 22606 Control Sheets. | Swartz, Mark EMR SYSS PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Swartz, Mark EMR SYSS PWS PITT | 2017-02-09 09:36 | [11 empty] | Swartz, Mark EMR SYSS PWS PITT | 2017-02-09 09:36 | 72907 |  |  | 2017-01-11 10:26 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2017-01-03 07:10 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>“Performing Ovation database analysis...” is taking more than 40 minutes during import of file containing 10 points, If database having 500K points and 22606 Control Sheets.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>It’s not depending on numbers of points being imported &nbsp;it could be import of 10 points or 10000 Points.</font></p><font face="Times New Roman" size=3> </font> |  |  |  | <p>The affected area is the database script (Analyze.sql) which is executed during an OvPtImport operation.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  | Implementation | OVA360FP2 |  | <p><font face=Calibri><span style="color:black;"><font size=3>DC+DB Server Drop200 (Windows2012 R2)</font></span><font size=3> </font><span style="color:black;"><font size=3>With Ovation 3.6.0 FP01 having 500K points</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>3 <span style="color:black;">VCH - Drop251, Drop252 and Drop253(Windows 7 S</span></font><font size=3>P</font><span style="color:black;"><font size=3>1)</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><span style="color:black;"><font face=Calibri size=3>OPS- Drop201 (Windows2012 R2)</font></span></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Physical Controller OCR1100 – Drop1/Drop51</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Vxsim Drops – Drop2 to Drop50</font></p><font face="Times New Roman" size=3></font> |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Software Quality |  | The&nbsp;oracle script used to analyze the database tables (executed during an OvPtImport operation) has been changed.&nbsp; Specifically, the script has been changed to direct Oracle to utilize additional processor cores (6) to complete the operation.&nbsp;Note that there is no adverse behavior if the database server has less than 6 processor cores. | 16 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><ol><li><div style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Create 10 points using DBID tool.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">To import those points, Use the following command <i>“OvPtImport -u ptadmin/ptadmin@ptdb -s ovation -n </i>path of IMP file”&nbsp; </div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Note down the time for <i>“[OvPtImport]: Performing Ovation database analysis...”.</i> Total how much time it took for analysis.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">It is taking more than 40 minutes and It does not depends on no of points are imported.<font face=Calibri size=3>&nbsp;</font></div></li></ol><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><font size=3>Observation:</font></b><font size=3> Point import is taking more than 40 minutes for Ovation database analysis if user is adding few points in Ovation 3.6.0</font></font></p><font face="Times New Roman" size=3> </font> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 108629
38389 | FINDING | Trend application is taking more than 15 minutes to browse 500K points of 52 Drops. | Bargaje, Prashant C EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:27 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2017-01-03 07:15 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>When 500K points of 52 Drops are browsed through Point browser popup of Trend application, Point Browser is taking more than 15 minutes to browse all 500K points </font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  | Implementation |  |  | <p><font face=Calibri><span style="color:black;"><font size=3>DC+DB Server Drop200 (Windows2012 R2)</font></span><font size=3> </font><span style="color:black;"><font size=3>With Ovation 3.6.0 FP01 having 500K points</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>3 <span style="color:black;">VCH - Drop251, Drop252 and Drop253(Windows 7 S</span></font><font size=3>P</font><span style="color:black;"><font size=3>1)</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><span style="color:black;"><font face=Calibri size=3>OPS- Drop201 (Windows2012 R2)</font></span></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Physical Controller OCR1100 – Drop1/Drop51</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Vxsim Drops – Drop2 to Drop50</font></p><font face="Times New Roman" size=3></font> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Software Quality |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face="Times New Roman" size=3> </font><ol><li><div style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Open Trend application.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">In Trend tab click on Browse Points.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Point Browse popup gets open.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Drops from ribbon section.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Verify all Drops are selected, if not click on Set All button.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Start Button.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Points Search started and searched around 150K points very soon after that taking more than 15 minutes to search remaining points.</div></li></ol><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>&nbsp;</font><font face=Calibri><b><font size=3>Observation:</font></b><font size=3> In Trend application Point Browse is taking more than 15 minutes to brows all points.</font></font></p><font face="Times New Roman" size=3> </font> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38390 | FINDING | Sometime Point Review application hang is observed when browsing the points and some time it is taking more than 15 minutes to browse all the points. | Augustine, Lisa EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:27 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2017-01-03 07:21 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Sometime Point Review application hang is observed when browsing the points and some time is taking more than 15 minutes to browse the points.</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Review/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  | Implementation |  |  | <p><font face="Times New Roman" size=3><br></font></p><p style="margin:0in 0in 0pt;"><font face=Calibri><span style="color:black;"><font size=3>DC+DB Server Drop200 (Windows2012 R2)</font></span><font size=3> </font><span style="color:black;"><font size=3>With Ovation 3.6.0 FP01 having 500K points</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri><font size=3>3 <span style="color:black;">VCH - Drop251, Drop252 and Drop253(Windows 7 S</span></font><font size=3>P</font><span style="color:black;"><font size=3>1)</font></span></font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><span style="color:black;"><font face=Calibri size=3>OPS- Drop201 (Windows2012 R2)</font></span></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Physical Controller OCR1100 – Drop1/Drop51</font></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>Vxsim Drops – Drop2 to Drop50</font></p><font face="Times New Roman" size=3></font> |  | Ovation for Windows | Ovation | Operator Station/Point Review | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Software Quality |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><ol><li><div style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Open point Review application.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Go to Filter tab. </div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on the Drops from ribbon section.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Verify all Drops are selected, if not click on Set All button.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Do the changes in Point properties and Live data filter accordingly.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Click on Start Button.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Points Search started and searched around 50K points very soon after that taking a lot time to search remaining points.</div></li><font face="Times New Roman" size=3></font><li><div style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">After some time Ovation Point Review displayed a message for unhandled exception of Microsoft .Net Framework. </div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Please find the attached <b>“Microsoft .Net Frame Work.png” </b>screenshot and <b>“Microsoft .net Framework_messages.txt”</b> file for reference.</div></li><font face="Times New Roman" size=3></font><li><div style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">When clicked on Continue button it appears again and again.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">If clicked Quit button, Point Review application gets closed.</div></li><li><div style="color:rgb(0, 0, 0);font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">If application hang is not observed than its taking more than 15 minutes to browse all the points<font face=Calibri size=3>&nbsp;</font></div></li></ol><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri><b><font size=3>Observation:</font></b><font size=3> Microsoft .Net frame work is unable to handle the Ovation Point review application if more than 500K points are used in the Ovation 3.6.0.</font></font></p><font face="Times New Roman" size=3> </font> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38391 | FINDING | cbOperation crash is observed during the Export of Control Sheet in Ovation 3.6.0 FP01. | Hutchison, Steven EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:28 |  |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | 2017-01-03 07:46 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Calibri size=3>cbOperation crash is observed during the Export of Control Sheet in Ovation 3.6.0 FP01.</font></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Control Options/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Kant, Krishna EMR SYSS PWS NOIDA | Saini, Shiva AUTOSOL PWS NOIDA | Arora, Priyanka AUTOSOL PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA |  |  | Implementation |  |  | <p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>DC+DB Server Drop200 (Windows2012 R2) With Ovation 3.6.0 FP01 having 500K points</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>3 VCH - Drop251, Drop252 and Drop253(Windows 7 SP1)</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>OPS- Drop201 (Windows2012 R2)</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Physical Controller OCR1100 – Drop1/Drop51</font></p><p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Vxsim Drops – Drop2 to Drop50</font></p><p><font face="Times New Roman" size=3> <br></font></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Control Options | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saklani, Rajnish EMR SYSS PWS NOIDA | Software Quality |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><font face="Times New Roman" size=3> </font><font face=Calibri size=3>Different scenarios are tested to verify the crash of cbOperation during the export of Control Sheets in Ovation 3.6.0 Fp01. Detail of the tested scenarios are as below</font></p><ol><li><font face="Times New Roman" size=3> </font>When All 50 Drops Control Sheets are exported: <b>(Total Control Sheets are 22604)</b></li></ol><ul style="margin-right:0px;" dir=ltr><ul><ul dir=ltr><li><div><font face="Times New Roman" size=3> </font>cbOperation gets crashed when Drop10 Control Sheets export was in progress.</div></li><li><div>WindowsEventLog.png” and “cbOperation Crash.png” are attached for reference.</div></li></ul></ul></ul><ol><li>When Drop1 and Drop10 Sheets are exported: <b>(Total Control Sheets are 1797)</b></li></ol><ul style="margin-right:0px;" dir=ltr><ul style="margin-right:0px;" dir=ltr><ul><li>Drop1 and Drop10 Control Sheets are exported successfully </li></ul></ul></ul><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">When Drop8 to Drop12 Sheets are exported: <b>(Total Control Sheets are 2580)</b></p></li></ol><ul><ul><ul><li><font face="Times New Roman" size=3> </font>All 2580 Control Sheets exported successfully.</li></ul></ul></ul><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">Export of 3500 Control Sheets: <b>(3500 Control Sheets)</b></p></li></ol><ul><ul><ul><li><font face="Times New Roman" size=3> </font>We have selected Drop6 to Drop14 is such a way so we can perform export operation for 3500 Control Sheets.</li><li>All 3500 Control Sheets exported successfully.</li></ul></ul></ul><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;">When Drop7 to Drop15 Sheets are exported: <b>(Total Control Sheets are 4257)</b></p></li></ol><ul><ul><ul><li><font face="Times New Roman" size=3> </font>Drop7 to Drop14 Control Sheets exported successfully but cbOperation crashed during the export of Drop15 Control Sheets.&nbsp;</li></ul></ul></ul><p><b>Observation:</b> It seems if More than 4000 Control sheet are selected for Export operation, it will crash the cbOperation.</p><p><font face="Times New Roman" size=3> <br></font></p> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38396 | FINDING | MHM: Differential Expansion- Changing Sensor Model does not update the Start and End values correctly for Cone1/ Cone2/Double Cone 1/Double Cone2 measurements | Patel, Sunil EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:36 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-01-04 02:37 |  | <p>In&nbsp;Differential Expansion&gt;Processing types Cone1/ Cone2/Double Cone 1/Double Cone2, changing &nbsp;Sensor Model change the Start and End values to -1.#J and 1.#J instead of changing it to the correct values for the selected Sensor.</p> <p>&nbsp;</p> <p><img src="http://tfs.emersonprocess.com/tfs/Quality/WorkItemTracking/v1.0/AttachFileHandler.ashx?FileNameGUID=25d4bec3-d3b4-487b-9161-9791bd71e537&amp;FileName=tmpDF80.png" width=771><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Steele, Kevin D AUTOSOL KNOX | Brown, Sean EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | Patel, Sunil EMR SYSS PWS PITT | Sachan, Pallavi EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | Ov3.6.0FP1, MHM Module in OCR1100 Drop27/77, Branch2, Slot3. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Configure MHM Differential Expansion companion&nbsp;measurement in the Module. </li> <li>Select Cone 1 Processing type</li> <li>Value of Start and End are according to theconfigured sensor</li> <li>Change the Sensor Model</li> <li>Start and End values&nbsp;change as displayed above.</li></ol> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38397 | FINDING | MHM: In Differential Expansion Tandem Processing type, Sensor and Range settings are not identical for X abnd Y channels. | Patel, Sunil EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 | [11 empty] | Maxwell, Jeffrey C EMR SYSS PWS PITT | 2017-05-17 10:12 |  |  |  | 2017-01-11 10:37 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-01-04 03:09 |  | <p>In Differential Expansion Paired measurement, Tandem measurement require identical Sensor and Range settings in both the X and Y channels. </p> <p>However right now Ovation MHM UI let us change the Sensor of any one channel and that change is not reflected in another channel.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Sean EMR SYSS PWS PITT | Steele, Kevin D AUTOSOL KNOX | Patel, Sunil EMR SYSS PWS PITT | Kumar, Sudheer EMR SYSS PWS NOIDA | Sachan, Pallavi EMR SYSS PWS NOIDA | [5 empty] | Implementation |  |  | Ov3.6.0FP1, MHM Module in OCR1100 Drop27/77, Branch2, Slot3. |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Configure MHM Differential Expansion companion&nbsp;measurement in the Module. </li> <li>Select Tandem Processing type.</li> <li>Sensor model and&nbsp;Range&nbsp;is&nbsp;PR6423 in both the channels.</li> <li>Change the Sensor Model to PR6422&nbsp;in Y channel.</li> <li>In X channel it is observed that Sensor model is still PR6423. It is not identical to the one configured in channel Y.</li></ol> |  | OVA360FP1 |  |  | FINDING | [6 empty] | 112961
38422 | FINDING | OVA360FP1-MHM: Few test cases need to be modified in 3.6.0FP1_MHM_Detailed_SVTP_rev1.5 SVTP. | Saxena, Pratishtha EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2018-02-23 23:44 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2018-02-23 23:44 |  |  |  | 2018-02-23 23:44 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-01-09 03:56 |  | <p>Below Test Cases need to be modified in 3.6.0FP1_MHM_Detailed_SVTP_rev1.5 SVTP:</p> <p>&nbsp;</p> <p>Test Case 5.3&gt; 51 &amp; 52-Peak/Phase RPM Field should be added</p> <p>Test Case 5.7&gt;19- Over range for any channel will set the bit of C reg but not cause alarm</p> <p>Test Case 5.8&gt; 5- Sensitivity can not be set manually for position measurement. Configuring Start and End working range will calculate the Sensitivity.</p> <p>Test Case 5.8&gt;19- Over range for any channel will set the bit of C reg but not cause alarm</p> <p>Test Case 5.8&gt; 23- Sensor Range can be different for both sensors of paired case expansion channels.</p> <p>Test Case 5.8&gt;33- Difference parameter should be added in SVTP.</p> <p>Test Case 5.10&gt;7-&nbsp; Sensitivity can not be set manually for position measurement. Configuring Start and End working range will calculate the Sensitivity.</p> <p>Test Case 5.10&gt;19- Over range for any channel will set the bit of C reg but not cause alarm</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | MHM_Detailed_SVTP_rev1.8.doc |  | OVA360FP1&nbsp;MHM SVTP |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | LC 01/09/2017: Reassigning to Nooch. Validation handles the Test Procedures. | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 124480
38435 | FINDING | Ovation membrane Keyboard is not working properly for Iconic alarming. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-17 10:50 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-17 10:50 |  |  |  | 2017-03-17 10:50 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-01-10 15:30 |  | Ovation membrane Keyboard is not working as expected. &nbsp;Keys configured corresponding to alarm groups are not properly turning on and off. &nbsp;<div>If keys lit for corresponding alarm group; its not turning off until points in alarm are acknowledged, reset and removed from alarm check.</div><div>&nbsp;</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Goyal, Ashish EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA360FP2 U0 |  | Ovation 360+FP1<div>OS- Win 7 64bit</div><div>Drop- Drop126 (EWS)</div><div>Network- EMILY</div><div><br></div> |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue tested on Ov360+Fp2 and found to be fixed. hence SDR passed validation. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Configured Iconic alarm on Drop126 with two group:<div>Group1:<span style="text-indent:-0.25in;font-family:Calibri, sans-serif;"><span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp; &nbsp;</span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">ASG_ICONIC_DROP126_GRP1</span></div> <p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp; </span>i.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="font-family:&quot;Calibri&quot;,sans-serif;">Plant Area Grouping Criteria</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">1.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Position1&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; S</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">2.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Position2&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; E</span></p> <p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">ii.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="font-family:&quot;Calibri&quot;,sans-serif;">Priority Grouping Criteria</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">1.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Priority 1</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">2.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Priority 8</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;"><span style="font-stretch:normal;line-height:normal;"><font face="Calibri, sans-serif">Group2-&nbsp;</font></span><span style="font-family:&quot;Times New Roman&quot;;font-stretch:normal;font-size:7pt;line-height:normal;">&nbsp;</span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">ASG_ICONIC_DROP126_GRP2</span></p> <p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;</span>i.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="font-family:&quot;Calibri&quot;,sans-serif;">Plant Area Grouping Criteria</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">1.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Position1&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">2.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Position2&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; -</span></p> <p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">ii.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="font-family:&quot;Calibri&quot;,sans-serif;">Priority Grouping Criteria</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">1.<span style="font-stretch:normal;font-size:7pt;line-height:normal;font-family:&quot;Times New Roman&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </span></span><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;">Priority 7</span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;font-family:Calibri, sans-serif;"><br></span></p><p class=MsoListParagraph style="margin-top:0in;margin-right:0in;margin-bottom:0in;margin-left:1.5in;margin-bottom:.0001pt;text-indent:-1.5in;"><span style="text-indent:-0.25in;"><font face="Calibri, sans-serif">Iconic alarms&nbsp;are working properly as per the grouping criteria (Characteristics &amp; Priority) but membrane keyboard is not working properly with groups.</font></span></p> |  | FP1 |  |  | FINDING | [6 empty] | 110091
38558 | FINDING | Error saving shortcut while installiing FP2 on Ovation Security Server (OSS) | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-09 08:53 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-09 08:53 |  |  |  | 2017-03-09 08:53 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2017-01-25 14:20 |  | <p>Error popup while installiing FP2 on Ovation Security Server (OSS):</p> <p>&nbsp;</p> <p>Script: ..\Scripts\postinstall.vbs</p> <p>Error:&nbsp; Unable to save shortcut: &quot;C:\Users\Public\Desktop\Ovation Applications\Ovation Machine Works.lnk&quot;</p> <p>&nbsp;</p> <p>See: Attached <a href="mailto:FP@_on_OSS.jpg">FP2_on_OSS.jpg</a></p> <p>&nbsp;</p> <p>--</p> <p>msb - 3/09/2016 - Ok in FP2_U1</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2 U1 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | smatreja: Fixed in FP2 U1 | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 109853
38635 | FINDING | SVTP "3.6.0_ WIN10_OPTIONAL_SW_SVTP_rev1.S.doc" & "3.6.0_WIN10_SystemTests_SVTP_rev2.G" needs enhancement | Gupta, Chandresh EMR SYSS PWS NOIDA | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2019-04-26 06:20 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2019-04-26 06:20 | [7 empty] | Tripathi, Sandeep AUTOSOL PWS NOIDA | 2017-02-07 02:57 |  | <ol><li><strong>Test case 5.21: Economic Optimizer</strong> of SVTP &quot;3.6.0_ WIN10_OPTIONAL_SW_SVTP_rev1.S.doc&quot; needs addition of one more test case 5.21.3&nbsp;as part of enhancement. Enhanced SVTP is attached for more details.</li><li>Test case 5.7.5.1-4 has been added in SVTP &quot;3.6.0_WIN10_SystemTests_SVTP_rev2.G&quot;&nbsp;for&nbsp; OHI testing of a windows 10 EWS machine. Enhanced SVTP is attached for more details.</li></ol><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | SVTP &quot;3.6.0_ WIN10_OPTIONAL_SW_SVTP_rev1.S.doc&quot; &amp; &quot;3.6.0_WIN10_SystemTests_SVTP_rev2.G&quot; |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Released to Library | 0 |  |  | Tripathi, Sandeep AUTOSOL PWS NOIDA | Validation |  | CG 4/26/19&gt; Details updated in section 5.7.5.x of SVTP rev 2.H. | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Please refer test case 5.21.3 of attached SVTP &quot;3.6.0_ WIN10_OPTIONAL_SW_SVTP_rev1.S.doc&quot; and test case 5.7.5.1-4 of SVTP &quot;3.6.0_WIN10_SystemTests_SVTP_rev2.G&quot;. |  | Win 10 |  |  | FINDING | [6 empty] | 141101
38636 | FINDING | STABLE97: Steam Table (STABLE97) algorithm can't be loaded into controller. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-03-08 03:28 | [11 empty] | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-03-08 03:28 |  |  |  | 2017-03-08 03:28 |  |  |  | Lal, Ramesh External | 2017-02-07 03:11 |  | APC 3.6.0_Update1_U0&nbsp; software and&nbsp; its appropriate licences were installed on Ovation 3.6.0 (installed with FP2).&nbsp;A control sheet consisting of STABLE97 algorithm was prepared and saved. An attempt was made to load this sheet into&nbsp;the &nbsp;Advanced Controller. But it resulted into error &quot;Unable to resolve Function Id (STABLE97). Therefore. the controller doesn't have support for STABLE97 algorithm. Please refer the attached snapshot of the error. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | [8 empty] | Implementation |  |  | <p>Ovation 3.6.0 FP2, DBS (OS Win Server 2012 R2), Controller OCR1100/400</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Lal, Ramesh External | Validation |  |  | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>-Prepare control sheet containing STABLE97 algorithm.</p><p>- Save the sheet.</p><p>- Load the controller and observe the error.</p> |  | OVA360FP2-U0 |  |  | FINDING | [6 empty] | 109744
38658 | FINDING | Logics containing the Operater Mapper Algoes like Keyboard, Setpoint & Mastation mappers fails to get loaded. Missing Functiond ID KBDMap error appears in the end of loading operation. | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-02-12 23:51 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-02-12 23:51 |  |  |  | 2017-02-12 23:49 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-02-08 05:56 |  | <p>APC 3.6.0_Update1_U0&nbsp; software and&nbsp; its appropriate licenses were installed on Ovation 3.6.0 (installed with FP2).</p><p>Created control sheets containing the Operator Mapper Algorithms like Keyboard, Set point &amp; MA station mappers. Saved the &amp; compiled the sheets.</p><p>No error occur while compiling.</p><p>Load the controller-&gt; Failed to finish the load operation with the message &quot;Function ID KBDMap error&quot;.</p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Bush, Kirt T EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [6 empty] | Implementation |  |  | Drop100-DBS -Ov3.6.0-Win2012R2 |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>This issue is fixed after running the OVPT bridge as a workaround along with the steam table algorithms.</p><p>So I have closed the finding with the state reason Confirmed to be fixed.</p><p>However I don't have any information regarding this.&nbsp; These issues &amp; workaround solutions are to be documented for the reference of the testers.</p> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>APC 3.6.0_Update1_U0&nbsp; software and&nbsp; its appropriate licenses were installed on Ovation 3.6.0 (installed with FP2).</p><p>Created control sheets containing the Operator Mapper Algorithms like Keyboard, Set point &amp; MA station mappers. Saved the &amp; compiled the sheets.</p><p>No error occur while compiling.</p><p>Load the controller-&gt; Failed to finish the load operation with the message &quot;Function ID KBDMap error&quot;.</p><p><br></p> |  | OVA360FP2-U1 |  |  | FINDING | [6 empty] | 108811
38668 | FINDING | OV360FP02: VC's for VCH(drop171) network connection was showing as Magenta in status diagram. | Burgoon, Frank AUTOSOL PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-07-21 13:40 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-07-21 13:40 | [7 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-09 05:19 |  | <p>VC's for VCH(drop171) network connection&nbsp;status changes to&nbsp;<strong>Magenta</strong> in status diagram after&nbsp;installing OV360FP02. Although the network connection status for the VCH (171) is green.</p><p>K0 and K1 field of VCH drop shows as 'unknown' in PI.</p> |  |  |  | Virtual controllers should reflect network connection as generic ethernet with primary interface reflecting actual status with valid tx/rx and error counts | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | <p>Ovation 360 FP02 - VCH Drop</p><p>Windows 10- 2016 LSTB</p> |  | Ovation for Windows | Ovation | Operator Station/General | Software | Standard Release | 3.6.0 |  |  | Released to Library | 1 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | Corrected for 3.6.0 FP2 | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>4Check the status of network connection in status diagram and Point Information.</li><li>Install Ovation360 FP02 on the VCH Drop (Operating Station = Windows 10)</li><li>Check the status of network connection in status diagram and Point Information.</li></ol> |  | FP2 |  |  | FINDING | [6 empty] | 116392
38670 | FINDING | Install wizard window is not visible during uninstallation of Ovation 360 FP02 package | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2017-02-13 10:41 | [11 empty] | McMaster, James External Artech | 2017-02-13 10:41 |  |  |  | 2017-02-13 10:41 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-09 05:19 |  | <p>Install wizard window is not visible during uninstallation of Ovation 360 FP02 package.</p><p>During uninstallation of the FP02 package from the DBS/EWS on Ovation3.6.0 network, install wizard in not visible, although the icon can be seen in the taskbar.</p><p><br></p><p>Note: Uninstallation gets completed successfully</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | <p>DBS/EWS</p><p>WS12 R2/ Win7 64 bit/ Win 10</p> |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Uninstall the package from Control panel.</p><p>Initially install shield is visible, but after making required selection for uninstallation, it becomes invisible.</p> |  | FP2 |  |  | FINDING | [6 empty] | 108840
38680 | FINDING | Control sheets are showing errors with the message "Missing required attributes" for the optional inputs like enable, etc when not connected for the SetPoint & MAStation Mapper Algorithms. | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-19 23:15 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-19 23:15 |  |  |  | 2017-04-19 23:15 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-02-12 23:38 |  | Control sheets are showing errors with the message &quot;Missing required attributes&quot; for the optional inputs like enable, etc. when not connected for the Set Point &amp; MA Station Mapper Algorithms as per the document SRF2234_HLD_120516. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software | The input pins referred to in this finding (related to the Setpoint Mapper&nbsp;and Mastation Mapper algorithms) were mistakenly set as 'required'. They have been corrected in the templates&nbsp;and&nbsp;set as &nbsp;'optional'. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | Ovation 3.6.0-FP02+APC 3.6.0 Update_U1. DBS drop#100, OS 2012R2 Server. |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>The input pins referred to in this finding (related to the Setpoint Mapper&nbsp;and Mastation Mapper algorithms) were set as &nbsp;'optional' to fix this finding.</p><p><br></p><p>TN:04/20:</p><p>With APC3.6.0 Update_U1 verified this issue is fixed. The sheets are saved when optional pins are not connected.</p><p>Thus closing the finding.</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Created the sheet . Added the Set Point &amp; MA Station Mapper Algorithms , &amp; Mapped algorithms.</p><p>Connected the Mapper algo LC points. Saved the sheet. Have not connected other inputs like Enable, etc which are referred as optional inputs in the document.</p><p>Saved the sheet. sheets are showing errors with the message &quot;Missing required attributes&quot;.</p><p>Please refer the attached snapshots.</p><p><br></p> |  | OVA360FP2-U1 |  |  | FINDING | [6 empty] | 111404
38717 | FINDING | Error saving shortcut while installing FP2 on Win 10 EWS | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-04-03 23:10 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-04-03 23:10 |  |  |  | 2017-04-03 23:10 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-17 05:24 |  | <p>Error saving shortcut while installing FP2 on Win 10 EWS</p><p>&nbsp;</p><p>Script: ..\Scripts\postinstall.vbs</p><p>Error:&nbsp; Unable to save shortcut: &quot;C:\Users\Public\Desktop\Ovation Applications\Ovation Machine Works.lnk&quot;</p><p>&nbsp;</p><p>See: Attached FP2 on Win10.png</p> |  |  |  |  | 0 |  |  |  | <p>This issue is seen particularly on one Win10 EWS consistently, Else everything is fine.</p><p>Issue is resolved in FP2_U2</p> | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | <p>Looks like someone deleted Ovation Application folder from the Desktop. That is the reason FP2 script failed.</p><p><br></p><p>AR - 02/22 - FP2 is installed on the new drop, and brought up from scratch.</p><p>Steps Followed :</p><p>1. Drop loaded with OS and patches.</p><p>2. Added to domain.</p><p>3. OHI installed.</p><p>4. Ovation Installed.</p><p>5. FP2 installed.</p><p><br></p><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 110612
38718 | FINDING | Ovation 3.6.0 Feature Pack 2 Readme.txt is having incorrect 'Patch Name' & 'description' | McMaster, James External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-19 21:52 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-19 21:52 |  |  |  | 2017-02-17 13:05 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-02-17 05:26 |  | <p>Ovation 3.6.0 Feature Pack 2 Readme.txt is having incorrect 'Patch Name' &amp; 'description' </p><p>in the Readme.txt file under the Patch name, OVA360FP1 is written instead of OVA360FP2 and in the description, Feature Pack 1 is written instead of Feature Pack 2.</p><p>Readme.txt file is attached.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | The README file gets generated by Validation (Mati) at the end of the validation cycle once all features are included. | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open the Readme.txt file in the folder of Ovation 360 FP2 software and look at the Patch name and description. |  | FP2 |  |  | FINDING | [6 empty] | 109049
38729 | FINDING | EIO: RNC EID Index information is displaying an incorrect format. | Souders, Sarah EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2017-10-25 08:48 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-10-25 08:48 | 79246 |  |  | 2017-10-25 08:48 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2017-02-21 09:19 |  | <p>The EIO RNC should be using Format-A to display the EID Index; it is currently displaying partial Format-B information.&nbsp; The EID document is attached.<br></p> |  |  |  | <p>1. Open Controller Diagnostics.</p><p>2. Click the I/O tab.</p><p>3. Open the EIO device tree.</p><p>4. Click one of the Nodes listed.</p><p>5. Note the number of values listed in the EID Index. There should be 4 values, each separated by a dot.</p><p>6. Install the patch.</p><p>7. Re-open Controller Diagnostics.</p><p>8. Open the I/O tab and navigate to the same Node.</p><p>9. The EID Index should now have 8 values, each separated by a dot. If the EIO Node has a label on it, the EID Index on the label should match the EID Index in Controller Diagnostics.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Software | <p>Some fields for node partner data were added to the I/O hardware info struct, which scan_io_server fills. These fields also needed to be explicitly transmitted in dpustat_xdr and received in ctrldxdr. Finally, the EIO Node's device type is special-cased for the purposes of EID parsing. It is entry type 1 like other node types, but we use its device type to indicate a different EID parsing method.<br><br></p><p>Also fixed cases where:</p><p>1. EID info is shown for only 1 EIO node when 1 node of a redundant pair&nbsp;is offline&nbsp;in Standard redundancy mode</p><p>2. EID info is&nbsp;shown twice (duplicated)&nbsp;for EIO nodes in Legacy redundancy mode. Now, only the EID info of the node in control is shown.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Souders, Sarah EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [7 empty] | Implementation | OVA360035-10122017123218 |  |  |  | Ovation for Windows | Ovation | Controller/Diagnostics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | The EIO Node EID Index&nbsp;is&nbsp;now parsed as EID Format-A and displayed accordingly. | 18 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360010-01302017144845 |  |  | FINDING | [6 empty] | 119597
38732 | FINDING | STABLE97: Configuration paarmeters for Entholpy in STABLE97 algorithm need correction. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2017-05-16 22:52 | [11 empty] | Lal, Ramesh External | 2017-05-16 22:52 |  |  |  | 2017-05-16 22:52 |  |  |  | Lal, Ramesh External | 2017-02-21 21:49 |  | <p>Following discrepancies should be corrected for configuration parameters for STABLE97 algorithm:</p><p>1. HIUNT:&nbsp; psia/lbm/ft3 should be changed to psi/lbm/ft3 to comply with SDD document.</p><p>2. HOUNT: psia/lbm/ft3 should be changed to psi/lbm/ft3 to comply with SDD document.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OVATION 3.6.0, DBS Drop100 (Win Server 2012R2), Controller Drop25/Drop75 (OCR1100) |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>The unit psia/lbm/ft3 is correct. The problem is in Table 9 and 10 in SDD.<br>SDD will be updated</p><p>Units for HIUMT and HOUNT have been corrected in the algorithm symbol, hence finding is closed.<br></p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Prepare a control sheet containing STABLE97 algorithm. Click on STABLE97 algoriths.</p><p>Verify HIUNT and HOUNT parameters.</p> |  | OVA360FP2-U0 |  |  | FINDING | [6 empty] | 112939
38791 | FINDING | Detail of NA test in SVTP- "SRF1625_SVTP_rev1.1_YJ" | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-02 17:13 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-02 17:13 | [7 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-02 17:12 |  | <a name=_GoBack></a><span style="font-size:11.0pt;line-height:107%;font-family:&quot;Arial&quot;,sans-serif;">(i) 5.1.4 Test: a) to i)- NA because historian is on base station and could not perform test item&nbsp;<span style="font-size:14.6667px;">a) to i)</span>.&nbsp;</span><div><span style="line-height:107%;"><span style="font-family:Arial, sans-serif;font-size:14.6667px;">(ii) 5.1.4 Test: o)&nbsp;</span><span style="font-family:Arial, sans-serif;font-size:14.6667px;">NA because no other </span><font face="Arial, sans-serif"><span style="font-size:11pt;">1GB network </span><span style="font-size:14.6667px;">available</span><span style="font-size:11pt;">.</span></font></span></div><div><span style="line-height:107%;"><font face="Arial, sans-serif"><span style="font-size:11pt;">(iii)&nbsp;</span></font><span style="font-family:Arial, sans-serif;font-size:11pt;">5.1.6 Test: NA because no controller is connected using </span><font face="Times, serif"><span style="font-size:12pt;">Multi-mode </span><span style="font-size:16px;">fiber</span><span style="font-size:12pt;">&nbsp;</span></font><span style="font-family:Times, serif;font-size:12pt;">media type.</span><br></span></div><div><span style="line-height:107%;"><font face="Arial, sans-serif"><span style="font-size:11pt;">(iv)&nbsp;</span></font><span style="font-family:Arial, sans-serif;font-size:11pt;">5.1.7 Test: NA because no controller is connected using&nbsp;Single-</span><font face="Times, serif"><span style="font-size:12pt;">mode&nbsp;</span><span style="font-size:16px;">fiber</span><span style="font-size:12pt;">&nbsp;</span></font><span style="font-family:Times, serif;font-size:12pt;">media type.</span><span style="font-family:Times, serif;font-size:12pt;"><br></span></span></div><div><span style="line-height:107%;"><span style="font-size:11.0pt;line-height:107%;font-family:&quot;Arial&quot;,sans-serif;">(v) 5.1.11 Test (ii)&nbsp;</span></span><span style="font-family:Arial, sans-serif;font-size:14.6667px;">NA because</span><span style="font-family:Arial, sans-serif;font-size:14.6667px;">&nbsp;</span><span style="font-family:Arial, sans-serif;font-size:11pt;">GLC-LX-SMD is not available.</span></div><span style="font-size:11.0pt;line-height:107%;font-family:&quot;Arial&quot;,sans-serif;"><span class=msoIns><ins cite="mailto:Jain,%20Yukta%20[AUTOSOL/PWS/NOIDA%5d" datetime="2017-01-11T16:29"></ins></span></span><div><span style="line-height:107%;"><span style="font-family:Arial, sans-serif;font-size:14.6667px;">(vi) 5.1.11 Test (iii)&nbsp;</span><span style="font-family:Arial, sans-serif;font-size:14.6667px;">NA because</span><span style="font-family:Arial, sans-serif;font-size:14.6667px;">&nbsp;</span><span style="font-size:11.0pt;line-height:107%;font-family:&quot;Arial&quot;,sans-serif;"><span class=msoIns><ins cite="mailto:Jain,%20Yukta%20[AUTOSOL/PWS/NOIDA%5d" datetime="2017-01-11T16:18">GLC-ZX-SMD</ins></span><span class=msoIns><ins cite="mailto:Jain,%20Yukta%20[AUTOSOL/PWS/NOIDA%5d" datetime="2017-01-11T16:30">&nbsp;</ins></span></span><span style="font-family:Arial, sans-serif;font-size:11pt;">&nbsp;is not available.</span><span style="font-family:Times, serif;font-size:12pt;"><br></span></span></div><div><span style="line-height:107%;"><span style="font-family:Arial, sans-serif;font-size:11pt;">(vii) 5.2 TestCase: NA because no Configuration Tool was available for validation.</span></span></div><div><span style="line-height:107%;"><span style="font-family:Arial, sans-serif;font-size:11pt;"><br></span></span></div><div><span style="line-height:107%;"><span style="font-family:Arial, sans-serif;font-size:11pt;">Note: New testcases added in Rev1.1 were performed with 500k system and additional test result is attached with in SVTP document.</span></span></div><div><span style="line-height:107%;"><br></span></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Benzvi, Mati EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP1 |  |  | FINDING | [6 empty] | 109575
38811 | FINDING | EIO: Redundancy Mode needs to be present in the CONFIG.EIO file. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2017-05-08 12:26 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-05-08 12:26 |  |  |  | 2017-05-08 12:26 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2017-03-06 08:21 |  | According to Mike Durbin, <span style="font-weight:bold;">RedundancyMode: Standard</span> must be present in the <span style="font-weight:bold;">CONFIG.EIO</span> file for Standard Redundancy Mode to function.&nbsp; If the Redundancy Mode is not <span style="font-weight:bold;">Standard</span> or is missing the RNC will default to <span style="font-weight:bold;">Legacy</span>. |  |  |  | <p>The affected area is the software responsible for generating controller configuration files.&nbsp; Specifically, the list of attributes applicable to the CONFIG.EIO file has been augmented to include the drop-level specified ethernet remote node redundancy mode.&nbsp; The format of this redundancy specification is defined in the Resolution field of this Finding.</p><p>Tests should verify that the file format has been changed accordingly.&nbsp; The user will need to modify one or more attributes of a drop's ethernet remote nodes or the drop's ethernet remote node redundancy mode via the Ovation Developer Studio.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Durbin, Michael EMR SYSS PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [7 empty] | Implementation | OVA360FP2_U2 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>A RedundancyMode entry will be added to CONFIG.EIO.</p><p>The actual format of the redundancy mode specification will include the specification of the Device number -- Device.X.RedundancyMode.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | Ovation 3.6.0 Feature Pack 1-12092016091132, Ovation 3.6.0 Feature Pack 2-01242017131344 |  |  | FINDING | [6 empty] | 112420
38817 | FINDING | PWTTS - RM 8732E Rev 4. Smart Meter Verification (SMV) method show as "Not Run" on AMS Device Manager user interface. | Shaw, Scott External Artech | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-04-03 13:10 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-04-03 13:10 |  |  |  | 2017-04-03 13:10 |  |  |  | Phan, Quang EMR ENT TECH AUS | 2017-03-06 15:35 |  | <p>When running SMV method on Rosemount 8732E Rev 4 device, result show status as &quot;Not Run&quot;.&nbsp; Same information shows on SMV report.&nbsp; </p><p>Even though Device Manager shows method is not running, it does actually run and completed locally at device.&nbsp; </p><p><br></p><p>Customer (Florida Power &amp; Light Power Generation) is reporting the same behavior on RM 8732E Rev 2.</p><p><br></p><p>Issue was observed on Ovation 3.6.0 and 3.5.1 with the same AMS 13.1.001.273 installed.</p><p><br></p><p>WORK AROUND:</p><p>In order for SMV report on AMS Device Manager&nbsp;to show correct information from device, a scan device method needs to perform right after SMV method is completed.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Brown, Rick P EMR SYSS PWS PITT | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | System Deviation Report created | 0 |  |  | Phan, Quang EMR ENT TECH AUS | Validation |  | IC 4/3/17&gt; Closed Finding since issue is now racked as SDR #38920. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | See attached for details steps to reproduce.&nbsp; Also attached is command trace when SMV method was running with some flow condition. |  | U9 Release |  |  | FINDING | [6 empty] | 110592
38831 | FINDING | Unable to launch Graphics.exe while working remotely. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-29 17:20 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-29 17:20 | 74475 |  |  | 2017-03-29 17:20 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-03-07 15:58 |  | Unable to launch Graphics.exe while working remotely after FP2 loading on Emily System.<div>Issue has been oberved on Win7 machines and found to be okay on WS2012 DBS machine.</div><div>Snapshot is attached.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0-FP2_U2 |  |  |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Retested on Ov360Fp2_U2 and found to be fixed. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 110460
38832 | FINDING | Ov-3.6.0-FP2_U1 on OpSt - repeating WesIconic.dll error displayed in the OvationError.log | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-03 07:41 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-03 07:41 | 74126 |  |  | 2017-04-03 07:41 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-07 16:26 |  | <p>After loading Ov-3.6.0-FP2_U1 on OpSt - we get repeating WesIconic.dll error displayed in the OvationError.log:</p> <p>&nbsp;</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; WesIconic.dll GraphicAlarmIconClient&nbsp;&nbsp;&nbsp;&nbsp; CANNOT Attach to the Shared Memory between the Arbitrator and the Alarm Graphic Groups Server&nbsp;</p> <p>&nbsp;</p> <p>---</p> <p>msb 4/03/2017 - Fp2_U2</p> <p>&nbsp; Reboot on Emily network:&nbsp; DBS(125), Opst(122,126, 127)</p> <p>&nbsp;&nbsp;&nbsp; WesIconic.dll&nbsp;error - Not in Error.log</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Alarms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2_U2 |  |  |  | Ovation for Windows | Ovation | Operator Station/Alarms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U1 |  |  | FINDING | [6 empty] | 110564
38834 | FINDING | 3.6.0 - SVTPs updated by GEC after 3.6.0 and G04 1100 testing | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-03-07 17:02 | [11 empty] | USPITTFSService | 2017-03-07 17:02 | [7 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-03-07 17:02 |  | <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">As part of our validation process, GEC team members have enhanced SVTP documents while <br>executing test cases and post completion of recent projects Ov3.6.0 and G04 OCR1100<br><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">I extracted the files and put then on Val\Tests\3.6.0\SVTP-Future\Updated By GEC\.<br>This findings serves as a reminder to formally update the SVTPs on SharePoint. </span></span> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | Ux |  |  | FINDING | [6 empty] | 109740
38860 | FINDING | Dropload of Redundant OpSt fails with PEDIT error | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-10 13:04 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-10 13:04 |  |  |  | 2017-03-10 13:04 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-10 10:58 |  | <p>New Redundant Operator Stations drop120/119 created after upgrade to Ov-3.6.0 - FP2_U1.</p> <p>On&nbsp;the Rdn-Opst - &nbsp;2 DU records &amp; a couple of points.</p> <p>Upon Drop Load to&nbsp;either OpSt, the Load fails,&nbsp;PEDIT errors are displayed in both&nbsp;Studio &amp;&nbsp;OvationErrLog of the client:&nbsp;</p> <p>&nbsp;</p> <p>Studio Error:</p> <p>&nbsp;&nbsp; &nbsp;[Error 6] from PEDIT LoadBegin attempt with &quot;DROP119&quot;, operatorStatus = [0], errorNumber = [0]</p> <p>Client Error:</p> <p>&nbsp;&nbsp;&nbsp; OP119&nbsp;&nbsp;&nbsp;&nbsp; Point Editor&nbsp;&nbsp;&nbsp; Unknown message type to process : 10</p> <p>&nbsp;</p> <p>Clear &amp; New dropload, gives the same errors.</p> <p>See Attached.</p> <p>---</p> <p>msb 3/10 - Closed as 'distracted old User Error' - (FP2 was not loaded)</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | User Error | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U1 |  |  | FINDING | [6 empty] | 109923
38875 | FINDING | OV360FP2: Sum Algo help needs to be modified to mention correct Record Field | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-27 00:33 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-27 00:33 | 75399 |  |  | 2017-04-27 00:33 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-03-15 06:21 |  | <p>Calculate track out option (TBLK) is linked to X2 byte in LC Record Field. The help needs to modified to mention X2 instead of X3.</p> <p>Please see the screenshot attached for reference.</p> |  |  |  |  | 0 |  |  |  | TK 25-April-2017: The help is updated to mention X2 in place of X3. Hence finding is closed. | 0 |  | Ovation for Windows/General/Documentation | <p>AA (04-26-2017): The required changes to the&nbsp;SUM algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OV360FP2U4 |  | OV360FP2 |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | <p>AA (04-26-2017): The required changes to the&nbsp;SUM algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1) Add Sum Algo in a control sheet.</p> <p>2) Right click open Help.</p> <p>Observation : TBLK refers to X3 byte.</p> |  | OV360FP2 |  |  | FINDING | [6 empty] | 111760
38877 | FINDING | STABLE97: SteamTable algorithm (STABLE97) default configuration parameters for atmospheric pressure need changes. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-03 01:56 | [11 empty] | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-03 01:56 |  |  |  | 2017-04-03 01:56 |  |  |  | Lal, Ramesh External | 2017-03-15 06:23 |  | <p>1. Default configuration parameter for Atmospheric Pressure as per Design Documents is MPA. But in Control Builder as well as Signal Diagram it shows PSI. It should be corrected.</p><p>2. Nomenclature of&nbsp; Atmospheric Pressure configuration parameter shown in the Signal Diagram is ATMUNT. It should be changed to PATMUNT to make it consistent with FAPATM, FBPATM.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | Ovation 3.6.0 FP2, DBS DROP100 (Win Server 2012R2), Controller DROP25/DROP75 (OCR1100). |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | Due to the last SDD version (2.1) the default unit for ATM is PSI.<br>The name PATMUNT is to long, the limit is for 6 signs. <br> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1.&nbsp; Prepare Control Sheet using STABLE97 algorithm.</p><p>2. Verify Configuration parameters for Atmospheric Pressure.</p> |  | OVA360FP2-U1 |  |  | FINDING | [6 empty] | 110547
38890 | FINDING | OV360FP2: Multiswitch Algo symbol 11 is not working as per specification | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-17 04:58 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-17 04:58 | Changeset 74787, 74979 |  |  | 2017-04-17 04:58 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-03-17 05:03 |  | <p>Multiswitch Algorithm Symbol 11 is not generating the desired output upon selection of selector switch S4. </p> <p>The algorithm generates an output 0 irrespective of the input provided on Input pin IN4. </p> <p>&nbsp;</p> <p>Please see the screenshot attached for reference.</p> <p>&nbsp;</p> <p>PS: Randomly checked the algorithm symbols 1, 01 , 02 , 04 and 11. Out of these 5 , only symbol 11 is behaving inappropriately. </p> <p>Checking&nbsp;other symbols as well.&nbsp;</p> |  |  |  |  | 0 |  |  |  | TK 17-April-2017: The symbol 11 is giving the desired output. Hence issue is fixed , so closing this finding. | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>OVA360FP2_U1</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>Create a control sheet using Multiswitch Algo symbol-11.</li> <li>Connect all the inputs and selector switches.</li> <li>Assign values to all the inputs.</li> <li>change the value of selector switch S4 from 0 to 1.</li></ol> <p>Observation: Output value changes to 0 irrestpective of value at IN4.</p> |  | OV360FP2_U1 |  |  | FINDING | [6 empty] | 111190
38891 | FINDING | OV360FP2: Multiswitch help not available in Control Builder help. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-27 00:28 | [11 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-27 00:28 | 75399 |  |  | 2017-04-27 00:28 |  |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-03-17 05:07 |  | <p>Control Builder Help - Algorithm Online help needs to be updated to mention Multiswitch Algo.</p><p><br></p><p>LC 03/17/2017: This affects the Algorithm book and online help.</p> |  |  |  |  | 0 |  |  |  | TK 27-April-2017: The online help as well as the user manual is updated to mention Multiswitch Algorithm help. Hence Closing this finding. | 0 |  | Ovation for Windows/General/Documentation | <p>AA (04-26-2017): The required changes to the&nbsp;MULTISWITCH algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OV360FP2U4 |  | OV360FP2_U1 |  | Ovation for Windows | Ovation | General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  | <p>AA (04-19-17): Reassigning this finding to the concerned developer responsible for merging the generated Qt online help with the Ovation software. For reference purpose, the details regarding the&nbsp;MULTISWITCH algo can be seen in the updated OW360_R1100V3&nbsp;user guide kept at:</p><p><a href="file://\\uspit-fp04\VAL\Tests\3.6.0\FP2\User_Manuals">\\uspit-fp04\VAL\Tests\3.6.0\FP2\User_Manuals</a></p><p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;MULTISWITCH algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol> <li>Open Control Builder Algorithm help from Control Builder</li></ol> <p>Observation: No details available for Multiswitch Algo.</p> |  | OV360FP2_U1 |  |  | FINDING | [6 empty] | 111759
38893 | FINDING | Historical Point Review : Network/Unit filter box causing crash | Augustine, Lisa EMR SYSS PWS PITT | Monitoring | [10 empty] | 35 | FINDING |  |  |  |  | 0 | McMaster, James External Artech | 2017-03-29 09:56 | [11 empty] | McMaster, James External Artech | 2017-03-29 09:56 |  |  |  | 2017-03-29 09:56 |  |  |  | Bargaje, Prashant C EMR SYSS PWS PITT | 2017-03-17 08:39 |  | On machine 172.16.209.150, If you click on&nbsp;+ sign for&nbsp;node SUZSYS, the application crashes. Applicable to all All MMI application |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Contento, James AUTOSOL PWS PITT | McMaster, James External Artech | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | Software | Standard Release | 3.6.0 |  |  | Monitoring to see if issue re-occurs | 0 |  |  | Bargaje, Prashant C EMR SYSS PWS PITT | Development |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | 3.6.0-FP2 |  |  | FINDING | [6 empty] | 110435
38900 | FINDING | STABLE97: Steam Table algorithm (STABLE97) dosn't display output pin mnemonics in the Signal Diagram if that pin is not connected. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-03 02:18 | [11 empty] | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-03 02:18 |  |  |  | 2017-04-03 02:18 |  |  |  | Lal, Ramesh External | 2017-03-20 05:33 |  | <p>In the STABLE97 algorithm if&nbsp;an output pin is not connected its pin name (mnemonics) will not be shown in the Signal Diagram whereas it is displayed in the older version of Ovation steam table algorithms. e.g. STM-TBL TSL. However, input pins are shown even if they are not connected. </p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ovation 3.6.0, DBS DROP100 (Win Server 2012 R2), Controller DROP25/DROP75 (OCR1100)</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | In STABLE97 outputs pins are optional, when output is not connected then output point is not created.<br>This is a reason why mnemonic are not visible.<br>In older version outputs are required and output points are created automatically, even if they are not connected.<br><br><br> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>1. Prepare a control sheet&nbsp; using STABLE97 algorithm. Do not connect any output pin.</p><p>2. Save the sheet.</p><p>3. Load the controller.</p><p>4. View the sheet in the&nbsp;signal diagram.</p> |  | OV360FP2-U1 |  |  | FINDING | [6 empty] | 110548
38904 | FINDING | The SIS Diagnostics tool shows the SDS firmware revision 3.6.0.9999.build9 instead of 3.6.0.134h (as per SDR#34320) | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Prasad, Parmatma EMR SYSS PWS NOIDA | 2017-04-04 23:08 | [11 empty] | Prasad, Parmatma EMR SYSS PWS NOIDA | 2017-04-04 23:08 | 74468 |  |  | 2017-04-04 23:08 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2017-03-21 07:04 |  | <p><font color="#000000" size=3>The&nbsp;SIS Diagnostics tool shows the SDS firmware revision&nbsp;3.6.0.9999.build9 instead of 3.6.0.134h (as per SDR#38392) in OVA360FP2.</font></p> <p><font color="#000000" size=3>It is also verfied in SDS via telnet. </font><font color="#000000" size=3>Observation:&nbsp;The SIS Diagnostics tool also shows message while selecting Firmware Revision options as &quot;Failed to Retrieve Firmware name from registry Ovsis key does not exit&quot;.&nbsp; </font></p> <p><font color="#000000" size=3>Please find attched snapshot of &quot;SDS01_System_info.jpg&quot; for reference.</font></p> <p><font color="#000000" size=3></font>&nbsp;</p> <p><font color="#000000" size=3>Hence RR#38784 of SDR#38392 is failed.</font></p> <p><font color="#000000" size=3></font>&nbsp;</p> <p><font color="#000000" size=3>PP:04/05/2017-W<font face=Calibri>e have upgraded SDS firmware in OVA360FP2_U2 build.</font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>&nbsp;</font><font face=Calibri>Steps followed:</font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>1. Installed OVA360FP2_U2</font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>2. Upgraded the SDS Firmware </font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>3. Open SIS Diagnostic Tool</font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>4. Verify the SDS Firmware Revision</font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font face=Calibri>5. Found the SDS Firmware is showing <b><span style="COLOR:#00b050;">3.6.0.149h. </span></b></font></p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" face=Calibri><span style="COLOR:#00b050;"></span></font>&nbsp;</p> <p class=MsoNormal style="MARGIN:0cm 0cm 0pt;"><font color="#000000" face=Calibri><span style="COLOR:#00b050;"><font color="#000000">Hence, Finding closed validation.</font></span></font></p> <p></font>&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Raciborski, Mikolaj AUTOSOL PSS WRSW | [6 empty] | Implementation | OVA360FP2_U2 |  | OV360+OVA360FP2, DBS drop100 (Ws12R2) |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | the issue was fixed on SDS, now the expected revision is 3.6.0.149h Please note that there is no functional change introduced.<br> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Installed OVA360FP2</p> <p>2. Upgraded the SDS Firmware </p> <p>3. Open SIS Diagnostic Tool</p> <p>4. Verify the SDS Firmware Revision</p> <p>5. Found the SDS Firmware is showing 3.6.9999build9</p> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 110671
38906 | FINDING | Ov360FP2_U1 manual and help should be updated for ALGFIELD algorithm | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Sharma, Satish AUTOSOL PWS NOIDA | 2017-05-02 04:03 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2017-05-02 04:03 | 75399 |  |  | 2017-05-02 04:03 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2017-03-22 05:09 |  | Ov360FP2_U1 manual and help should be updated for ALGFIELD algorithm. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Documentation | <p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;ALGFIELD algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p>SS (05-02-2017): Online help updated but the hyperlink is still not working in U4 build.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OV360FP2_U4 |  | <p>Windows7, Windows10, Windows Server 2012 R2</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  | <p>AA (04-19-17): Reassigning this finding to the concerned developer responsible for merging the generated Qt online help with the Ovation software. For reference purpose, the details regarding the ALGFIELD algo can be seen in the updated OW360_R1100V3&nbsp;user guide kept at:</p><p><a href="file://\\uspit-fp04\VAL\Tests\3.6.0\FP2\User_Manuals">\\uspit-fp04\VAL\Tests\3.6.0\FP2\User_Manuals</a></p><p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;ALGFIELD algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | FP2_U1 |  |  | FINDING | [6 empty] | 112043
38914 | FINDING | DB_XMIT_SERVER failed on DBS due to wrong startup sequence of Ovation Startup processes | Morris, Gilbert L AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-22 13:06 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-22 13:06 | 74483 |  |  | 2017-04-22 13:06 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-22 11:18 |  | <p>DBS on Emily Network, with Ov-3.6.0_FP2_U1, fails to start DB_XMIT_SERVER upon reboot.</p> <p>&nbsp;</p> <p>Messages in OvationErrorlog:</p> <p>&nbsp;&nbsp; DB_XMIT_SERVER&nbsp; 2329 SHC_Open_Memory error (16)</p> <p>&nbsp;&nbsp; DB_XMIT_SERVER&nbsp;&nbsp;1132 Setup process failed&nbsp;&nbsp;&nbsp;</p> <p>&nbsp;</p> <p>As seen in the attached DBS_Startup.jpg, &nbsp;the Ovation_DB_Startup &amp; Ovation_Startup processes are starting in the wrong order.</p> <p>---</p> <p>Local Workaround:</p> <p>&nbsp; We put the 'Ovation Database Startup Service' in Automatic (Delayed Start) mode</p> <p>&nbsp; and restart the DBS,</p> <p>--</p> <p>msb 4/22 - Closed - Passed: No failure reported since U2.</p> |  |  |  | <p>Please modify the 'Ovation Database Sturtup Service' mode by placing back to Automatic - not Delayed Start.</p><p>Apply the feature pack and reboot the machine.</p><p>Check to ensure that the <span class=info-text>DB_XMIT_SERVER started without issue.</span></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | OVA360FP2_U2 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  | <p>msb 3/29/2017 - </p> <p>&nbsp; With OVA360-FP2_U2 loaded on all Emily Stations &amp; Controllers<br>&nbsp; a. Reboot DBS at 8:45 while 'Ovation Database Startup Service' in Automatic (Delayed Start) mode.</p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Ovation Ops came up correctly. No DB_XMIT errors in OvationError.log</p> <p>&nbsp; b.&nbsp;Reboot DBS at 9:00 while 'Ovation Database Startup Service' in Automatic mode&nbsp;</p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Ovation Ops came up correctly. No DB_XMIT errors in OvationError.log</p> <p>&nbsp; c. Will monitor for a week for normal DBS operation with random reboot.</p> <p>---</p> | 8 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OVA360FP2_U1 |  |  | FINDING | [6 empty] | 111537
38915 | FINDING | Ovation Base drop should not include the 'Ovation Machine Works' shortcut | Matreja, Shyam EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-03 07:56 | [11 empty] | Benzvi, Mati EMR SYSS PWS PITT | 2017-04-03 07:56 |  |  |  | 2017-04-03 07:56 |  |  |  | Benzvi, Mati EMR SYSS PWS PITT | 2017-03-22 15:59 |  | <p>Ovation Base drop should not include the 'Ovation Machine Works' shortcut </p> <p>in the Ovation Applications folder</p> <p>or in the 'Ovation - Ovation Applications' menu.</p> <p>&nbsp;</p> <p>1. There are no MHM tools loaded on Base drop.</p> <p>2. When selected, popup error displays: </p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 'Windows is searching for OvMHMPlotting.exe. </p> <p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; To locate yourself, click Browse.'</p> <p>---</p> <p>msb - 4/03/2017 - FP2_U2 -</p> <p>&nbsp; BaseSt(128) on Emily network:</p> <p>&nbsp;&nbsp;&nbsp; No 'Ovation Machine Works'&nbsp;shortcut</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; in the Ovation Applications folder</p> <p>&nbsp;&nbsp;&nbsp;&nbsp; or in the 'Ovation - Ovation Applications' menu.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Ovation Machine Works/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2_U2 |  |  |  | Ovation for Windows | Ovation | Operator Station/Ovation Machine Works | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Benzvi, Mati EMR SYSS PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U1 |  |  | FINDING | [6 empty] | 110570
38927 | FINDING | Virtual Controllers are reporting an error on a load operation | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-26 08:21 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-26 08:21 | 75040 |  |  | 2017-04-26 08:21 |  |  |  | Perdeus, Matthew AUTOSOL PWS PITT | 2017-03-27 13:24 |  | <p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">The virtual controllers are reporting the following error to the Ovation Error Log and to its own error buffer.&nbsp; &quot;Point Editor : Error in creating load protection: S_errno_ENOENT; initiate Clear again&quot;</span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">No fault condition is created and the virtual controllers are properly loaded. </span></p> |  |  |  | Complete the testing done for SDR 35834 on virtual and hardware controllers. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Ovation Virtual Controller/General/Software | The load protection feature was made independent of virtual or hardware controllers by checking the root directory. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Matthew Cimino | Silvaggio, Gregory W EMR SYSS PWS PITT | [8 empty] | Implementation | OVA360FP2U4 |  | Ovation 3.6.0 FP2 |  | Ovation for Windows | Ovation | Ovation Virtual Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | The load protection feature was made independent of virtual or hardware controllers by checking the root directory. | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Perform&nbsp;a load operation on&nbsp;a virtual controller. |  | OVA360FP2 |  |  | FINDING | [6 empty] | 111697
38934 | FINDING | Alarm Graphic Group toolbar is showing as Iconic alarming instead of Alarm Graphic Group. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2017-03-29 12:38 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2017-03-29 12:38 |  |  |  | 2017-03-29 07:35 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2017-03-28 23:55 |  | <p>Alarm Group Graphic toolbar&nbsp;&nbsp;is showing Iconic alarming instead of Alarm Group Graphic. See the attached snapshot for your reference.&nbsp;</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>Ov3.6.0-FP1</p><p>Drop 100 (DBS)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Validation |  | Way It works.&nbsp; The configuration of the grouping criteria&nbsp;for&nbsp;alarm graphic groups and&nbsp;iconic alarming groups are the same.&nbsp; The same grouping criteria configuration parameters are used. Thus, the tab names will be the same. | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | FP2 |  |  | FINDING | [6 empty] | 110442
38935 | FINDING | Alarm Graphic Group online help is not open and showing some error. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Kumar, Sudheer EMR SYSS PWS NOIDA | 2017-04-25 22:57 | [11 empty] | Kumar, Sudheer EMR SYSS PWS NOIDA | 2017-04-25 22:57 |  |  |  | 2017-04-25 22:57 |  |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | 2017-03-29 00:29 |  | <p>Alarm Graphic Group online help is not open and showing some error. Error details as mentioned below:</p><p>Can't load help file= 'c:\\Ovation\help\EN\OvPtstudio.chm', HelpID=1909.</p><p>See the attached snapshot for your reference.</p> | SJ April 3, 2017: Alarm graphic group added to online help with the respective help ids. |  |  | SJ April 3, 2017: Alarm graphic group added to online help with the respective help ids. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Documentation | SJ April 3, 2017: Alarm graphic group added to online help with the respective help ids. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | Ov3.6.0-FP2_U3 |  | <p>Ov3.6.0-FP2_U2</p><p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Kumar, Sudheer EMR SYSS PWS NOIDA | Documentation |  | <p>AA (03-29-17): Currently, I am not working on the Control Builder User Manual. For online help issues, please contact Steven Hutchison.</p><p>The help ids have been assigned as follows:&nbsp; Alarms Graphic Groups&nbsp;=&nbsp;1910 , Group Names under Alarm Graphic Groups = 1911.&nbsp;</p><p>LC 03/29/2017: This is alarm configuration information for the Studio. I believe it belongs in the Operator Station Configuration Guide.</p><font face=Consolas size=2><p>SJ April 3, 2017: Check Ov3.6.0-FP2_U3<br></p></font><p><br></p> | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP2 |  |  | FINDING | [6 empty] | 111669
38936 | FINDING | STABLE97: In STABLE97 (Steam Table algorithm) for this specific range (PI <=0.000611212 MPa and TI <= 273.15K ) algorithm recognize incorrect Region (4 instead 2). | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jha, Rahul AUTOSOL PWS NOIDA | 2017-04-25 23:16 | [11 empty] | Jha, Rahul AUTOSOL PWS NOIDA | 2017-04-25 23:16 | 74615 |  |  | 2017-04-25 23:16 |  |  |  | Jha, Rahul AUTOSOL PWS NOIDA | 2017-03-29 06:43 |  | <p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">For this specific range (PI &lt;=0.000611212 MPa and TI &lt;= 273.15K ), STABLE97&nbsp;algorithm recognizes incorrect Region. It calculates Region as&nbsp;<strong>4 </strong>instead of <strong>2</strong>. </span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><br></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Below test cases failed while testing&nbsp;test section&nbsp;5.5.1.3 of&nbsp;&nbsp;SVTP </span><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">'3.6.0FP2_SRF2229_STABLE97_SVTP_ rev1.1' :</span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">1. <span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;4 of Test Scenario: H_TP_REG1 (where RREG=5).&nbsp;(<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (e).i from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">2. <span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;4 of Test Scenario: </span>S_TP_REG1&nbsp;(where RREG=5).&nbsp; (<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (e).ii from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">3. <span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;4 of Test Scenario: </span>V_TP_REG1 (where RREG=5).&nbsp; (<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (e).iii from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">4. <span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">1, 3, 7 &amp;&nbsp;9</span> of Test Scenario:</span><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">&nbsp;H_TP_REG2 (where RREG=5).&nbsp; (<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (f).i from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)&nbsp;</span></span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">5.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">1, 3, 7 &amp;&nbsp;9</span> of Test Scenario: </span>S_TP_REG2&nbsp;(where RREG=5).&nbsp;&nbsp; (<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (f).ii from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)</span></span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">6. <span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">TEST ID&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">1, 3, 7 &amp;&nbsp;9</span> of Test Scenario: </span>V_TP_REG2 (where RREG=5).&nbsp;&nbsp; (<span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">Used test (f).iii from Excel sheet “STABLE97 Validation Data” </span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">[5]</span>)</span></span></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | <p>Ovation 3.6.0</p><p>APC 3.6.0 + Update1_U0</p><p>Drop100 (WS12_R2)</p><p><br></p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jha, Rahul AUTOSOL PWS NOIDA | Validation |  | RJ 04/26/2017: Verified the issue in OVA360FP2-U3 + APC360_Update1_U1. Observed that issue is fixed. Hence, Closed the finding. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Run following test scenarios&nbsp;and verify the logs:</p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">1.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test Scenario: H_TP_REG1 where RREG=5.&nbsp;</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">2.<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"> Test Scenario: </span>S_TP_REG1&nbsp;where RREG=5.&nbsp;</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">3.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test Scenario: </span>V_TP_REG1 where RREG=5.</span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">4.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test Scenario:</span><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">&nbsp;H_TP_REG2 where RREG=5.&nbsp;</span></span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">5.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test Scenario: </span>S_TP_REG2&nbsp;where RREG=5.&nbsp;</span></span></span></p><p><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">6.&nbsp;<span lang=EN-IN style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Test Scenario: </span>V_TP_REG2 where RREG=5.</span></span></span></p> |  | OVA360FP2-U2 |  |  | FINDING | [6 empty] | 111670
38959 | FINDING | OVA360FP2 SRF 2236: Mini alarm summary is not handling zoom-in properly. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-20 01:54 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-20 01:54 | 74825 |  |  | 2017-04-20 01:54 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-03 05:10 |  | <p>OVA360FP2_U2 SRF2236: For&nbsp;alarm group icon, Mini alarm summary is not working properly when the diagram is zoomed:</p> <p>&nbsp;</p> <p>1&gt; Open mini alarm summary for any alam group icon and zoom-in the diagram, the Alarm summary stay as it is. But if we click on another alarm group icon, mini alarm summary disappears. It can be displayed again on full view of the diagram.</p> <p>2&gt; Open the diagram, zoom-in. Double clicking on any alarm group icon do not display mini alarm summary when the diagram is zoomed in. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_FP2_U3 |  | OVA360FP2_U2: Issue oserved on diagrams in DBS and EWS |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | prs 20 Apr 2017: Validated in U3. Found Fixed. Zoom is working properly now. Thanks | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Steps to reproduce are:</p> <p>Case 1:</p> <ol> <li>Create a diagram with more than one alarm group icon in GBNT. Download to the workstation drop.</li> <li>In online graphics, open the diagram.</li> <li>Open mini alarm summary for any alam group icon and zoom-in the diagram, the Alarm summary stay as it is. </li> <li>Click on another alarm group icon, mini alarm summary disappears. </li> <li>Zoom out to&nbsp;full view&nbsp;the diagram. Double clicking the alarm group&nbsp;icon again opens the mini alarm summary.</li></ol> <p>Case 2:</p> <ol> <li>Open the diagram, zoom-in. </li> <li>Double clicking on any alarm group icon do not display mini alarm summary when the diagram is zoomed in.&nbsp;&nbsp;</li> <li></li></ol> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 111414
38960 | FINDING | OV360FP2 : Unable to perform test case 5.5.5 of "BASIC_FUNCTIONS_SVTP_rev1.R.doc" due to unavailability of hardware | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-04-03 08:53 | [11 empty] | USPITTFSService | 2017-04-03 08:53 | [7 empty] | Kakroo, Tanisha EMR SYSS PWS NOIDA | 2017-04-03 05:54 |  | OV360FP2 : Unable to perform test case 5.5.5 of &quot;BASIC_FUNCTIONS_SVTP_rev1.R.doc&quot; due to unavailability of hardware. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OV360FP2 |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Kakroo, Tanisha EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OV360FP2 |  |  | FINDING | [6 empty] | 110580
38961 | FINDING | SDR37031 RR38937 Failed: Developer Studio allows setting LS proof test reminder alert greater or equal interval. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Hutchison, Steven EMR SYSS PWS PITT | 2017-04-03 08:55 | [11 empty] | Hutchison, Steven EMR SYSS PWS PITT | 2017-04-03 08:55 |  |  |  | 2017-04-03 08:55 |  |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | 2017-04-03 07:52 |  | <p>Installing the OVA360FP2 in Ov3.6.0,.</p><p>Developer Studio should not allow setting LS proof test reminder alert greater or equal&nbsp;proof test interval in logic solver's properties window. Proof Test reminder alert must be less than interval.</p><p><br></p><p>ALERT &lt; INTERVAL</p><p>In&nbsp;Dev Studio, there is no alert box popup appeared for message indicating that the ( Proof test remind alert due (days) value must be less than the Proof test interval (days)).</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | Joshi, Parmesh EMR SYSS PWS NOIDA | Morris, Gilbert L AUTOSOL PWS PITT | [6 empty] | Implementation |  |  | <p>Ws12R2,OV3.6.0+OVA360FP2</p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | No Action Required | 0 |  |  | Prasad, Parmatma EMR SYSS PWS NOIDA | Validation |  | NOT RELEASED YET - RR marked as in U3. | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1.&nbsp; open a CSLS and on the Proof Testing tab.</p><p>2.&nbsp; set the remind alert due (days) field to be greater than the interval (days) field. Please find attached snapshot for your review.</p><p>3.&nbsp; click either OK or Apply.</p><p><br></p><p>In&nbsp;Dev Studio, there is no alert box popup appeared for message indicating that the ( Proof test remind alert due (days) value must be less than the Proof test interval (days)).</p> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 110583
38969 | FINDING | Runtime Algorithm help is not complete. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-06-07 22:02 | [11 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-06-07 22:02 | 76415 |  |  | 2017-06-07 22:02 |  |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-04-03 23:07 |  | <p>Runtime Algorithm help is not complete.</p><p><font face="Times New Roman" size=3> As per SRF#2252</font></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">The new fields in LC record are required for RUNTIME algorithm. The list of the fields is presented below:</span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">R4 – STIM: Tuning value for Time;</span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Y0 – CMSTIM: Command for time tuning value.</span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">G6 – SNST: Tuning value for number of starts;</span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Y1 – CMSNST: Command for number of starts tuning value</span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Y2 – QTIM: Set good quality for time;</span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Y3 – QNST: Set good quality for number of starts</span></p><font face="Times New Roman" size=3><p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Set BAD quality for RTIME and NUMST when high limit reached and counting is stopped.</span></p><p> <br></p></font><p><br></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">&nbsp;</span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation | <p>AA (04-26-2017): The required changes to the&nbsp; RUNTIME algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p><br></p><p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;RUNTIME algorithm have been added to the updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p><br></p><p>The changes in the online help will be visible in the Future Release. So changing the status of the Finding to <strong>Will fix in Future Update</strong>.</p><p><br></p><p>AA (06-07-2017): The issue has been fixed in the Ovation Algorithm manual and online help.</p><p>The updated manual (OW360_R1100V4) is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP3/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Aditya, Abhinav AUTOSOL PWS NOIDA | [9 empty] | Implementation | OV360FP3U1 |  | OVA360FP2_U2 |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  | <p>AA (04-26-2017): The required changes to the&nbsp;RUNTIME algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;RUNTIME algorithm have been added to the updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p><br></p><p>The changes in the online help will be visible in the Future Release. So changing the status of the Finding to <strong>Will fix in Future Update</strong>.</p><p><br></p><p><strong><br></strong></p><p>AA (06-07-2017): The issue has been fixed in the Ovation Algorithm manual and online help.</p><p>The updated manual (OW360_R1100V4) is kept at:</p><p><a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p><p><br></p><p>AR- (06-08-2017) &gt; Updated manual and online help is verified and is OK.</p> | 10 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | OVA360_FP2 U2 |  |  | FINDING | [6 empty] | 113952
38970 | FINDING | LONGACC STAT pin Bit 6 not getting reset automatically when gain parameters returns to some valid value from NaN | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-05 06:00 | [11 empty] | Plamowski, Sebastian EMR SYSS PWS WRSW | 2017-04-05 06:00 |  |  |  | 2017-04-05 06:00 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-04 01:53 |  | <p>LONGACC STAT pin Bit 6 (Gain paramater value is NAN or Inf) not getting reset automatically after gain parameters returns to some valid value&nbsp;from NaN.</p> <ol> <li>This behavior is observed&nbsp;with IN pin connected with any value i.e. zero or no-zero value.</li> <li>This behavior is not observed when Set command pin&nbsp;is in enabled state i.e. with this pin enabled, bit 6 of STAT pin resets as soon as Gain parameter has some valid value.</li> <li>This behavior is not observed when Increment command pin&nbsp;is in enabled state i.e. with this pin enabled, bit 6 of STAT pin resets as soon as Gain parameter has some valid value.</li></ol> <p>Other bits of STAT pins gets reset automatically when the error condition is removed. Example Bit 0 (ACC value on top limit), Bit 1 (ACC value on top limit), Bit 3 (IN value is NAN or Inf), etc.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Plamowski, Sebastian EMR SYSS PWS WRSW | [8 empty] | Implementation |  |  | <p>GEC Ovation 3.6.0 setup (Net#36) updated with OVA360FP2-U2.</p> <p>Controller - OCR1100 Drop45/95</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | Tjis is correct algorithm behaviour. The idea is to inform the user about the cause of the problem by the STAT bit.<br>STAT bit is active until user reset it.<br><br> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol> <li>In Signal Diagram select the LONGACC algorithm and tune the value of GAIN parameter to NaN. This will set the STAT pin bit 6.</li> <li>Now set the value of GAIN parameter to some valid value. This does not reset the STAT pin bit 6.</li> <li>Try enabling IC or SC pin, this immediately resets STAT pin bit 6.</li></ol> | EPM Validation | OVA360FP2-U2 |  |  | FINDING | [6 empty] | 110699
38973 | FINDING | STABLE97: Engineering units needs correction | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-07-12 09:37 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-07-12 09:37 | 74752 |  |  | 2017-07-12 09:25 |  |  |  | Czerwinski, Kamil EMR SYSS RS WRSW | 2017-04-04 06:15 |  | <p>The following incompatibilities in&nbsp;units&nbsp;was detected:</p><p>1.&nbsp;Specific enthalpy: unit name 'psia/lbm/ft3' should&nbsp;be replaced to 'psia*ft3/lbm'. (TO UPDATE: Algorithm template, algorithm source, Tables 3, 9, 10 in SDD and User Manual).</p><p>2. Specific enthalpy: Value of Factor A&nbsp;in&nbsp;'hp*hr/lbm' unit should&nbsp;be modified to 5918.3525 in conversion 'Pin to Internal'.&nbsp; In opposite conversion&nbsp;Factor A equals to 1/5918.3525.&nbsp;(TO UPDATE: Algorithm source, Tables&nbsp; 9, 10 in SDD and User Manual).</p><p>3. Specific entropy: Value of Factor A&nbsp;in&nbsp;'bar*cm3/g/K' unit&nbsp;should be modified to 0.1 in conversion 'Pin to Internal'.&nbsp;In opposite conversion&nbsp;Factor A equals to 10.0.&nbsp;(TO UPDATE: Algorithm source, Tables&nbsp; 9, 10 in SDD and User Manual).</p><p>4. Specific entropy: Value of Factor A&nbsp;in&nbsp;'J/kg/K' unit should be modified to 0.001 in conversion 'Pin to Internal'.&nbsp;In opposite conversion&nbsp;Factor A equals to 1000. &nbsp;(TO UPDATE: Algorithm source, Tables&nbsp; 9, 10 in SDD and User Manual).</p><p>5. Specific entropy: Value of Factor A&nbsp;in&nbsp;'ft*lbf/lbm/R' unit&nbsp;should be modified to 5.38032e-03 in conversion 'Pin to Internal'. In opposite conversion&nbsp;Factor A equals to 1/5.38032e-03.&nbsp;(TO UPDATE: Algorithm source, Tables&nbsp; 9, 10 in SDD and User Manual).</p><p>6. Specific entropy: Value of Factor A&nbsp;in 'kcal/g/K' unit&nbsp;should be updated in algorithm sources.</p><p>7.&nbsp;Modified units should be updated in validation test cases.</p><p><br></p><p><br></p><p>SP: All item are done!<br></p><p><br></p> |  |  |  |  | 0 |  |  |  | IC 7/12/17&gt; per RL 7/12 email: <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">I checked the manual today. <br>Software (algorithm functions) were checked during </span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">First pass and Regression testing.</span></p><font face="Times New Roman" size=3> </font> | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 U3 |  | OVATION 3.6.0, DBS Drop200 (Win Server 2012R2), Controller Drop61/Drop161 (OCR1100) |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Czerwinski, Kamil EMR SYSS RS WRSW | Development |  | <p>AA (04-21-17): Since, the User Manual also needs to be verified, I have kept the latest version of the APC Toolkit 3.6.0&nbsp;Update 1 User Guide at the following locations:</p><p><br></p><ul><li><a href="file://\\Uspit-fp04\val\Tests\APC\3.6.0">\\Uspit-fp04\val\Tests\APC\3.6.0</a> Update 1\Docs</li><li>Q:\Communication\TechComm\Share\Feature Pack 2\APC Toolkit\APC360_002</li></ul><p><br></p><p>AA (05-18-17): The updated APC360_002V3 pdf is kept at:<br></p><ul><li>Q:\Communication\TechComm\Share\APC Toolkit 3.6.0 Update 1</li><li><a href="file://uspit-fp04/val/Tests/APC/3.6.0">\\Uspit-fp04\val\Tests\APC\3.6.0</a> Update 1\Docs</li></ul><p>IC 6/12/17&gt; changed state to Closed/Confirmed since this was checked by RL and since old state (Closed/DIR) was not correct.</p> | 11 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2-U2 |  |  | FINDING | [6 empty] | 115692
38979 | FINDING | Safety Shell-During resynchronization, an invalid sequence numbers are not counted. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 08:58 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 08:58 | 75111 |  |  | 2017-05-03 05:39 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-05 03:14 |  | <p><font face="Times New Roman" size=3> </font><span style="line-height:107%;font-size:10pt;"><font face=Arial>During resynchronization, an invalid sequence numbers are not counted.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="line-height:107%;font-size:10pt;"><font face=Arial> </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial><u><br></u></font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial><u>Out of sequence/less than</u>, <u>Out of sequence/greater than</u> and <u>Repeated</u> sequence faults received during synchronization should be counted.</font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial><br></font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial>Current behavior of system as following:&nbsp; <br></font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>e.g. Injected 5 consecutive repeated sequence via Error injection tool.</font></span></p><p><font face="Times New Roman" size=3> </font><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in ddbStatusAll (on receiving controller drop 31/81):&nbsp; repeated seq error counter incremented by 1; unsync count<i> </i>error counter incremented by<strong> </strong>1.<br><span style="line-height:107%;font-size:10pt;"><font face=Arial>Repeated sequence numbers are not counted.</font></span></font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial>S</font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>imilar behavior observed for multiple out of sequence/less than and&nbsp;multiple&nbsp;out of sequence/greater than. </font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial><br></font></span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  | Perform tests as before and observe the change in behavior | 0 |  |  |  | <p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">VP 08/09/17 &gt; Retested&nbsp;in regression testing cycle. System loaded with <strong>OVA360FP3_U4</strong>:</span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Following are verified&nbsp;scenario with results:</span></p><p style="margin:0in 0in 0pt;"><u><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Scenario #1</span></u><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">: Out of Sequence/ +1 error generated.</span></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Noted Current sequence number DDB via ddbTool i.e. #less than 120</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Using Error Injection Tool on EWS drop102, injected Out of sequence +1 error in selected ddb.<br></span><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Inserted set of sequence numbers <b style="">#231 #233 #235 #237 #239 #241 #243 #245 #247 #249</b></span><span style="font-family:&quot;Times New Roman&quot;,serif;"><font size=3> </font></span></li></ul><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">&nbsp;Verified results: </span></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via ddbStatusAll in controller Console: Out of sequence error counter increment by 10.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via SS_Status algorithm, OSCT output value increment by 10. </span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> </font><u><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Scenario #2</span></u><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">: Out of Sequence/ less error generated.</span></p><ul style="margin-top:0in;"><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Noted Current sequence number DDB via ddbTool i.e. #75000 above</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Using Error Injection Tool on EWS drop102, injected Out of sequence/less error in selected ddb.</span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"> Inserted set of sequence numbers <b style="">#99 #97 #95 #92 #88 #84 #81 #76 #72</b>.</span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Verified results: </span></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via ddbStatusAll in controller Console: Out of seq error counter increment by 9; Unsync error counter increment by 1. </span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via SS_Status algorithm, OSCT output of value increment by 9. </span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">&nbsp;<u>Scenario #3</u>: Consecutive repeated sequence error. </span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Using Error Injection Tool on EWS drop102, injected 9 consecutive errors in selected ddb</span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Verified results: </span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via ddbStatusAll in controller Console: repeated seq error counter increment by 9, </span><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Unsync error counter incremented by1&nbsp;</span><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;"><span style="">&nbsp;</span></span></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:black;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:10pt;">Via SS_Status algorithm, RSCT output value increment by 9. </span></li><font face="Times New Roman" size=3> </font></ul><p><font face="Times New Roman" size=3> <br></font></p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Long, Michelle J External Artech | Capani, Innocenzo AUTOSOL PWS PITT | Gupta, Chandresh EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA |  |  |  | Implementation | Ovation 3.6 FP2 U4 |  | <p>Ov 3.6.0+ FP2_U2; Net#52</p><p>Drop102: EWS running with custom driver for using Error Injection Tool.&nbsp;</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Out of sequence faults counted during resynchronization. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face=Arial size=2>Injected 5 consecutive repeated sequence via Error Injection Tool&nbsp; on workstation drop102 running with custom driver.</font><p><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in ddbStatusAll( on receiving controller drop 31/81): </font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial><b>repeated seq</b> error counter incremented by <b>1</b>; <b>unsync count</b><i> </i>error counter incremented by <b>1.</b></font></span></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial>Repeated sequence numbers are not counted.</font></span></p> |  | FP2 |  |  | FINDING | [6 empty] | 117152
38984 | FINDING | Safety Shell- SS_Status algorithm, DDBs received with both out of sequence errors and invalid source IDs generate faults associated with the wrong drop number. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 00:57 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 00:57 | 75111 |  |  | 2017-04-27 23:22 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-05 05:33 |  | <font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> <span style="line-height:107%;font-size:10pt;"><font face=Arial><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>SS_Status algorithm, DDBs received with both out of sequence errors and invalid source IDs generate faults associated with the wrong drop number.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><br>Scenario: Injected 5 consecutive Invalid Source using Error Injection Tool.<br>Discrepancy observed between SS_Status algorithm’s (<span style="">Controller Level High Integrity DDB Fault Counters)<b> </b>output OSCT value </span>&nbsp;and controller’s ddbStatusAll (<span style="">DDB Level High Integrity Fault Counters</span>) out of sequence error counter value.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in ddbStatusAll (on receiving controller drop31/81) as expected: </font></span><font face=Arial><b><span style="line-height:107%;font-size:10pt;">bad source</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>5</b>; <b>out of seq</b> error counter incremented by <b>5</b>; </span></font><font face=Arial><b><span style="line-height:107%;font-size:10pt;">delayed ddb</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>1</b></span></font></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in signal diagram-safety Shell Algorithm: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>Value of<b> BSCT</b><span style="">: “<b>5</b>”;<b> </b></span>Value of<b> OSCT</b><span style="">: “<b>1</b>”;<b>&nbsp;</b></span>Value of<b> DDCT</b><span style="">: “<b>1</b>”<b> </b></span></font></span></p></font><p style="margin:0in 0in 0pt;"><br></p></span><p style="margin:0in 0in 0pt;"><br></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style=""><strong><br></strong></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style=""><strong><br></strong></span></font></span></p> <br></font> |  |  |  | Perform test as described and observe that safety shell faults are reported in connection with appropriate drop ID. | 0 |  |  |  | <p>VP 08/09/2017&gt; Retested for regression testing. System loaded with final build FP3_U4. </p><p>Observation: No discrepancy observed between bad source error counter (in Controller-ddbStatusAll) result and Value of <strong>OSCT </strong>output pin<strong>&nbsp;</strong>in<strong> SS_Status</strong>&nbsp;algorithm.&nbsp;&nbsp;</p><p>Performed steps:</p><p><br></p><p><span style="line-height:107%;font-size:10pt;"><font face=Arial><span><strong>Scenario#1:</strong></span></font></span></p><p>Injected&nbsp;<strong>12</strong> consecutive Invalid Source <font face=Arial size=2>via Error Injection Tool&nbsp; on workstation drop102 running with custom driver</font>.<br></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><strong>Observation in ddbStatusAll (on receiving controller drop31/81):</strong> </font></span><font face=Arial><b><span style="line-height:107%;font-size:10pt;">bad source</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <strong>12</strong>; <b>out of seq</b> error counter incremented by <strong>12</strong>; </span></font><font face=Arial><b><span style="line-height:107%;font-size:10pt;">delayed ddb</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>1</b></span></font></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><strong>Observation in signal diagram-safety Shell Algorithm</strong>: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>Value of<b> BSCT</b><span>: “<strong>12</strong>”;<b> </b></span>Value of<b> OSCT</b><span>: “<strong>12</strong>”;<b>&nbsp;</b></span>Value of<b> DDCT</b><span>: “<b>1</b>”</span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span><strong><br></strong></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span><strong>Scenario#2:</strong></span></font></span></p><span style="line-height:107%;font-size:10pt;"><font face=Arial><p>Injected&nbsp;<strong>20</strong> consecutive Invalid Source <font face=Arial size=2>via Error Injection Tool&nbsp; on workstation drop102 running with custom driver</font>.<br></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><strong>Observation in ddbStatusAll</strong> <strong>(on receiving controller drop31/81)</strong>: </font></span><font face=Arial><b><span style="line-height:107%;font-size:10pt;">bad source</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <strong>20</strong>; <b>out of seq</b> error counter incremented by <strong>20</strong>; </span></font><font face=Arial><b><span style="line-height:107%;font-size:10pt;">delayed ddb</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>1</b></span></font></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><strong>Observation in signal diagram-safety Shell Algorithm</strong>: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>Value of<b> BSCT</b><span>: “2<b>0</b>”;<b> </b></span>Value of<b> OSCT</b><span>: “2<strong>0</strong>”;<b>&nbsp;</b></span>Value of<b> DDCT</b><span>: “<b>1</b>”</span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span><br></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span>Both scenarios verified for slow and Fast ddb.</span></font></span></p></font></span> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Gupta, Chandresh EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  | Implementation | Ovation 3.6 FP2 U4 |  | <p>Ov 3.6.0+ FP2_U2; Net#52</p><p>Drop102: EWS running with custom driver for using Error Injection Tool.&nbsp;</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>Controller DDB driver modified to assign safety shell faults to drop ID listed as originator of the DDB generating the fault rather than the drop ID received in the DDB.</p><p><br></p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Injected 5 consecutive Invalid Source <font face=Arial size=2>via Error Injection Tool&nbsp; on workstation drop102 running with custom driver</font>.<br><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in ddbStatusAll (on receiving controller drop31/81) as expected: </font></span><font face=Arial><b><span style="line-height:107%;font-size:10pt;">bad source</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>5</b>; <b>out of seq</b> error counter incremented by <b>5</b>; </span></font><font face=Arial><b><span style="line-height:107%;font-size:10pt;">delayed ddb</span></b><span style="line-height:107%;font-size:10pt;"> error counter incremented by <b>1</b></span></font></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Observation in signal diagram-safety Shell Algorithm: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>Value of<b> BSCT</b><span style="">: “<b>5</b>”;<b> </b></span>Value of<b> OSCT</b><span style="">: “<b>1</b>”;<b>&nbsp;</b></span>Value of<b> DDCT</b><span style="">: “<b>1</b>”<b> </b></span></font></span></p> |  | FP2 |  |  | FINDING | [6 empty] | 117124
38986 | FINDING | OV360FP2: MHM configuration gives error "Error from GenerateXML" | Patel, Sunil EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sachan, Pallavi EMR SYSS PWS NOIDA | 2017-04-26 07:00 | [11 empty] | Sachan, Pallavi EMR SYSS PWS NOIDA | 2017-04-26 07:00 | OV360FP2 U4 |  |  | 2017-04-26 07:00 |  |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | 2017-04-05 06:28 |  | MHM configuration changes or new configurations gives error &quot;Error from GenerateXML&quot;. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Saxena, Pratishtha EMR SYSS PWS NOIDA | Kumar, Sudheer EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [6 empty] | Implementation | OV360FP2 U4 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sachan, Pallavi EMR SYSS PWS NOIDA | Validation |  | <p>(4/19/2017)&nbsp; Fixed in source code. -ssp&nbsp;</p><p>26Apr17 PS: Verified in OV360_FP2_U4 the issue no more exists. Hence finding is Closed as FIXED.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p><span style="FONT-SIZE:10pt;"><font color="#000000" face="Segoe UI Symbol">Step1&gt;&nbsp;Configure MHM module in OCR1100&nbsp;Controller Drop 27/77&gt;Branch2&gt;Slot2. </font></span></p> <p><span style="FONT-SIZE:10pt;"><font color="#000000" face="Segoe UI Symbol">Step2&gt; Right click on MHM Module in hierarchy and select Engineer to open Ovation MHM UI for configurations</font></span></p> <p><span style="FONT-SIZE:10pt;"><font color="#000000" face="Segoe UI Symbol">Step3&gt;&nbsp;After performing Configurations, Click Apply.</font></span></p> <p><span style="FONT-SIZE:10pt;"><font color="#000000" face="Segoe UI Symbol">Step4&gt; Ovation Developer Studio Error &nbsp;appears as seen in attached mhm-config-error.jpg</font></span></p> <p><span style="FONT-SIZE:10pt;"><font color="#000000" face="Segoe UI Symbol">Step5&gt; Click Apply, this window appears 4 times and then the configuration is saved successfully.</font></span></p> <p><font size=3 face="Times New Roman"><br></font></p> |  | OV360FP2 |  |  | FINDING | [6 empty] | 111693
38991 | FINDING | Safety Shell-One extra missed DDBs due to even number of sequence error injection. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 04:30 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 04:30 | 75111 |  |  | 2017-05-08 00:23 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-05 09:37 |  | <p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>One extra missed DDBs due to even number of&nbsp; sequence error injection.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Scenario: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>For Slow High Integrity DDB, following behavior observed when consecutive repeated sequence error injected via Error Injection Tool.</font></span></p><ul><li><div style="margin:0in 0in 0pt;"><font face="Times New Roman"></font><span style="line-height:107%;font-size:10pt;"><font face=Arial>One number of repeated sequence give result of one missed frame.</font></span></div></li><li><div style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Two&nbsp;numbers of repeated sequence give result of three missed frames.</font></span></div></li><li><div style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Three&nbsp;numbers of repeated sequence give result of three missed frame.<br></font></span></div></li><li><div style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Four&nbsp;numbers of repeated sequence give result of&nbsp;Five missed frame, which causes timeout.</font></span></div></li></ul><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>For Fast High Integrity DDB, Forty-eight numbers of repeated sequence give result of&nbsp;forty-nine missed frames (verified in SOE events at receiving drops), which causes timeout.</font></span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"></font><span style="line-height:107%;font-size:10pt;"><font face=Arial><br>Note: Missed samples verified in SOE events at receiving controller drop31/81.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><br></font></span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"></font><span style="line-height:107%;font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Similar behavior observed (as above mentioned)&nbsp;with multiple Out of sequence/greater than and Out of sequence/less than error. Where,&nbsp;sequence error&nbsp;Injected&nbsp;&nbsp;via Error injection Tool- “Insert Sequence Numbers” option.</span></p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><p><br></p><p><br></p><p style="margin:0in 0in 0pt;"><br></p><font size=3><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> <br></font></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><br></span></p></font><p style="margin:0in 0in 0pt;"><br></p></span><p style="margin:0in 0in 0pt;"><br></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  | Perform tests described above and observe the expected number of missed frames. | 0 |  |  |  | <p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>VP-08/10- Retested the issue with regression test cycle. system is loaded with &nbsp;OVA360FP3_U4. </font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>No extra missed DDB observed upon injecting sequence error.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><br></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Scenario: </font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>For Slow High Integrity DDB, following behavior observed when consecutive repeated sequence error injected&nbsp;via Error Injection Tool in Originating EWS drop102.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>Below observation done for receiving controller drop drop 31/81. <span style="line-height:107%;font-size:10pt;"><font face=Arial>Note: Missed samples verified in SOE events at receiving controller drop31/81.</font></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial>For slow DDB, verified for one , two, five, six, eleven, twelve consecutive repeated sequence injection.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"><font face=Arial>For Fast DDB, verified for one , two, five, six, forty-eight, forty-nine consecutive repeated sequence injection.</font></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"><br></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"></span></font></span><span style="line-height:107%;font-size:10pt;"><font face=Arial>For Fast High Integrity DDB, Forty-nine numbers of repeated sequence give result of&nbsp;forty-nine missed frames (verified in SOE events at receiving drops), which causes timeout.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"><font face=Arial>For&nbsp;Slow High Integrity DDB, Five numbers of repeated sequence give result of&nbsp;five missed frames (verified in SOE events at receiving drops), which causes timeout.</font></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"><span style="line-height:107%;font-size:10pt;"><font face=Arial><span style="line-height:107%;font-size:10pt;"><font face=Arial><br></font></span></font></span></span></font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;">Also verified the result&nbsp;for multiple Out of sequence/greater than and Out of sequence/less than error. Where,&nbsp;sequence error&nbsp;Injected&nbsp;&nbsp;via Error injection Tool- “Insert Sequence Numbers” option.</span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:10pt;">Detail Test results are updated in attached document &quot;Finding38991_result_in regression.docx&quot;</span></p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Long, Michelle J External Artech | Capani, Innocenzo AUTOSOL PWS PITT | Zochowski, Piotr EMR SYSS RS WRSW | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Gupta, Chandresh EMR SYSS PWS NOIDA |  |  |  | Implementation | Ovation 3.6 FP2 U4 |  | <p>Ov 3.6.0+ FP2_U2; Net#52</p><p>DDB origination EWS Drop102: EWS running with custom driver for using Error Injection Tool.&nbsp;</p><p>Receiving drop31/81: OCR1100</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 1 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Controller DDB driver's Safety Shell resynchronization logic was flawed. Software was corrected to perform as described in Safety Shell software design. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP2 |  |  | FINDING | [6 empty] | 117169
39009 | FINDING | Ov3.6.0 FP2_U2 ScStep, ScStepNA algorithm new added STEP pin is not working. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Sharma, Satish AUTOSOL PWS NOIDA | 2017-05-08 23:46 | [11 empty] | Sharma, Satish AUTOSOL PWS NOIDA | 2017-05-08 23:46 |  |  |  | 2017-05-08 23:46 |  |  |  | Sharma, Satish AUTOSOL PWS NOIDA | 2017-04-10 05:13 |  | Newly added STEP pins to ScStep, ScStepNA does not function. The added pins calculate step numbers in a sequential logic. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Plamowski, Sebastian EMR SYSS PWS WRSW | [8 empty] | Implementation |  |  | <p>Ov360_FP2_U2 + Windows Server 2012 R2</p><p>Ov360_FP2_U2 + Windows 10</p><p>Ov360_FP2_U2 + Windows 7</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Sharma, Satish AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>1. Open Developer Studio.</p><p>2. Select a <strong>controller</strong>,&nbsp;Navigate to&nbsp;<strong>Control Tasks</strong>, select a<strong> Control Task</strong> , Navigate to <strong>Control Sheets</strong>, right click, Select <strong>Insert new .</strong></p><p>3. Create a control logic as attached above.</p><p>4. Verify that <strong>ALGFIELD</strong> gives the <strong>STEP</strong> number.</p> |  | OVA360FP2_U2 |  |  | FINDING | [6 empty] | 112425
39019 | FINDING | Few test cases are NA for RUNTIME algorithm in SRF#2252 Ansaldo | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-04-11 00:19 | [11 empty] | USPITTFSService | 2017-04-11 00:19 | [7 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-04-11 00:19 |  | <p>3.6.0FP2_RUNTIME_SVTP_rev1.2_XX is having some test cases as NA</p><p>Section 5.5 Tracking is NA for RUNTIME algorithm, As tracking is not available for the same.</p><p>Section 5.11.3 &amp; 5.11.4 are NA as&nbsp; inputs are LD type and rest of the calculations are internal.</p><p>These Sections can be marked as NA.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360 FP2 |  |  | FINDING | [6 empty] | 111008
39020 | FINDING | Few test cases are NA for DIVIDE & MULTIPLY algorithm in SRF#2252 Ansaldo | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-04-11 04:21 | [11 empty] | USPITTFSService | 2017-04-11 04:21 | [7 empty] | Rathi, Ankur AUTOSOL PWS NOIDA | 2017-04-11 04:21 |  | 3.6.0FP2_DIVIDE_SVTP_rev1.1_XX &amp; 3.6.0FP2_MULTIPLY_SVTP_rev1.1_XX&nbsp; having some test cases as NA<p><strong>Section 5.9</strong> - Bit positions of inputs &amp; Outputs, is invalid for both the algorithms and must be marked as NA.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Rathi, Ankur AUTOSOL PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360 FP2 |  |  | FINDING | [6 empty] | 111027
39062 | FINDING | OV360FP2: LONGACC algorithm help does not have detailed description for INITP and RECOP. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-06-15 04:26 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-06-15 04:26 | OV360FP3U2 |  |  | 2017-06-15 04:26 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-17 00:50 |  | <p>LONGACC algorithm help does not have detailed description for INITP and RECOP. Following&nbsp;points could be added in details accordingly:</p> <ol> <li>For INITP&nbsp;user need to create analog point (Frequency A) with option periodic save and use this point as an LONGACC output. Refer to attached screenshots Frequency-A.png and Periodic Save.png</li> <li>For RECOP option user need to make reconcile before rebooting both controllers.</li> <li>If both options are ON, algorithm executes as a first RECOP and after INITP – it means that If user&nbsp;want to use&nbsp;RECOP option then&nbsp;user need to turn off INITP option.</li></ol> <p>( Refered following revision of help document since FP2 help is not yet available: <a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals\OW360_R1100V3.pdf">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals\OW360_R1100V3.pdf</a>&nbsp;)</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation | <p>AA (04-26-2017): The required changes to the LONGACC algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p><p><br></p><p><br></p><p>AA (04-26-2017): The required changes to the&nbsp;LONGACC algorithm have been added to the updated user guide is kept at:</p><p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3.</p><p><br></p><p>The changes in the online help will be visible in the Future Release. So changing the status of the Finding to <strong>Will fix in Future Update</strong>.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Aditya, Abhinav AUTOSOL PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | OV360FP3U2 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>AA (04-26-2017): The required changes to the LONGACC algorithm have been added. Please,&nbsp;refer to&nbsp;the latest online help. The updated user guide is kept at:</p> <p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3</p> <p>&nbsp;</p> <p>ASG (04-27-2017): Changes mentioned were available in the user guide kept at <a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>, but these changes are missing in Control Builder help for LONGACC algorithm, hence the finding is being marked as Failed Retest.</p> <p><br></p> <p><br></p> <p>AA (04-26-2017): The required changes to the&nbsp;LONGACC algorithm have been added to the updated user guide is kept at:</p> <p><a href="file://uspit-fp04/val/Tests/3.6.0/FP2/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP2\User_Manuals</a>. Name of the&nbsp; user guide is OW360_R1100V3.</p> <p><br></p> <p>The changes in the online help will be visible in the Future Release. So changing the status of the Finding to <strong>Will fix in Future Update</strong>.</p> <p><br></p> <p>AA (06-07-2017): The issue has been fixed in the Ovation Algorithm manual and online help.</p> <p>The updated manual (OW360_R1100V4) is kept at:</p> <p><a href="file://uspit-fp04/val/Tests/3.6.0/FP3/User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> <p><br></p> <p><br></p> <p>AA (06-15-2017): The issue has been fixed in the Ovation Algorithm manual and online help.</p> <p><br></p> <p>The updated manual (OW360_R1100V4) is kept at:</p> <p><a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p> <p>&nbsp;</p> <p>ASG 06/15/2017&gt;</p> <p>Verified in OW360_R1100V4 manual (kept at <a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a>) and in Control Builder help that the information has been added. Hnece closing the finding.</p> | 13 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OV360FP2_U3 |  |  | FINDING | [6 empty] | 114324
39075 | FINDING | OCR1100 G01: Backup controllers are not communicating when they come up after reboot, generating EXCMON error. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 10:28 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 10:28 | 75292, 75300 |  |  | 2017-04-27 10:28 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-17 14:01 |  | <span style="font-size:11.0pt;line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;">Backup controllers are not communicating when they come up after reboot, generating EXCMON error.&nbsp;</span><div><span style="font-size:11.0pt;line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;">EXCMON error showed up for Backup Controller 54 when&nbsp;</span><span style="font-family:Calibri, sans-serif;font-size:11pt;">it came up after&nbsp;</span><span style="font-family:Calibri, sans-serif;font-size:11pt;">clear reboot operation and for Backup Controller 60 &nbsp;when it came up after Download reboot.</span></div><div><span style="font-family:Calibri, sans-serif;font-size:11pt;">Other Notes:</span></div><div><span style="font-family:Calibri, sans-serif;">1. The error was observed on Backup Controller only.</span></div><p class=MsoNormal style="margin-bottom:0in;margin-bottom:.0001pt;line-height:normal;"></p> <p class=MsoNormal style="margin-bottom:0in;margin-bottom:.0001pt;line-height:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">2. The error was observed when controller come up after reboot operation.</span></p> <p class=MsoNormal style="margin-bottom:0in;margin-bottom:.0001pt;line-height:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">3. It was observed on OCR 1100 G01.</span></p> <p class=MsoNormal style="margin-bottom:0in;margin-bottom:.0001pt;line-height:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">4. Need to Reboot the controller again to bring it to healthy state.</span></p> <p class=MsoNormal style="margin-bottom:0in;margin-bottom:.0001pt;line-height:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">5. Observed on System with Ov360+FP2_U2 &amp; U3. &nbsp;</span></p> |  |  |  | Recreate the scenario using the above &quot;steps to reproduce&quot;. &nbsp;Verify that with the FP2_U4 in place, the issue is resolved. &nbsp;Note that we expect to see the following message in controller diagnostics when double clicking the drop pair after the &quot;Init SHC message in the Error Log.&quot; &nbsp;The error will be &quot;Error refreshing DROPX: clnt_create() to 'ipaddress' failed: Program not registered. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | The init_drop process that starts up the controller processes will wait for COORD to initialize the &quot;dpuInfo&quot; pointer. &nbsp;After the dpuInfo pointer is initialized, it will resume starting other processes, such as toolsrvr. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP2_U4 |  | <span style="font-family:Calibri, sans-serif;">&nbsp;Ov360+FP2_U2 &amp; U3</span><div><span style="font-family:Calibri, sans-serif;">OCR1100 G01</span></div><div><span style="font-family:Calibri, sans-serif;">Controller 54 &amp; Controller 60</span></div> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Changed the start up process so that toolsrvr cannot crash. &nbsp;<div><br></div><div>YJ: Retest on&nbsp;OVA360FP2_U4 System. Tried to recreate issue 3-4 time but didnt see any error.</div><div>Hence closing the finding. &nbsp;</div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Perform&nbsp;<span style="font-family:Calibri, sans-serif;font-size:11pt;">&nbsp;</span><span style="font-family:Calibri, sans-serif;font-size:11pt;">clear reboot or&nbsp;</span><span style="font-family:Calibri, sans-serif;font-size:14.6667px;">Download reboot.</span><div><span style="font-family:Calibri, sans-serif;font-size:14.6667px;"><br></span></div><div><font face="Calibri, sans-serif"><span style="font-size:14.6667px;">GWS&gt; Monitor the OvationErrorLog After the message &quot;Init_SHC : Initializing SHC 0&quot; appears, repeatedly double click on the DropX/DropY pair in controller diagnostics. &nbsp;During this time (while the controller is clear) there is an approximate 30 second window where the toolsrvr program can crash a create the EXCMON message. &nbsp;</span></font></div> |  | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 111823
39080 | FINDING | OvPtImport operation get terminated due to CJC attribute error for default Analog and default Deluxe Analog point. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-28 00:29 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-28 00:29 | 75197 |  |  | 2017-04-28 00:29 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-18 00:22 |  | <p>Import operation get terminated due to CJC attribute error for default Analog and default Deluxe Analog point.</p><p><br></p><p>Example of Import operation that got terminated due to error &nbsp;&quot;Unable to map attribute CJC_TEMPERATURE_UNITS&quot;.</p><p>Perform Import using command <em>C:\Ovation\OvationBase&gt;ovptimport -u </em><a href="mailto:ptadmin/ptadmin@ptdb"><em>ptadmin/ptadmin@ptdb</em></a><em> path of Import file.</em></p><p>Following error appeared during import operation:<br><em>[OvPtImport]: &lt;V2Parse.cpp:411&gt; Unable to map attribute CJC_TEMPERATURE_UNITS at line 236<br>[OvPtImport]: &lt;OvPtImport.cpp:644&gt; Unrecoverable error encountered, terminating.</em></p><p><em></em><br></p><p>Note: Import operation successfully done if attribute &quot;CJC_TEMPERATURE_UNITS&quot; removed from Import file for default Analog points and default Deluxe Analog points. </p> |  |  |  | <p>The affected area is in the file (attribute) parsing portion of the OvPtImport.exe application.&nbsp; The CJC-related attributes:&nbsp; CJC_NAME, CJC_TEMPERATURE_UNITS, CJC_CONVERSION_COEFF_1, and CJC_CONVERSION_COEFF_2 (in the context of default analog points and default deluxe analog points) have been added to an already existing list of ignored attributes.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  | <p>Retested with FP2_U4,&nbsp;</p><p>Observed&nbsp; that CJC-related attributes for&nbsp; default Analog&nbsp;points and Default&nbsp;Deluxe Analog point.</p><p>Performed Import operation&nbsp;using Import file with&nbsp;CJC related attributes&nbsp;for Default Analog Point default Deluxe Analog Point.</p><p>Import operation successfully done without any error.</p><p>Hence finding is closed.</p><p><br></p> | 0 |  | Ovation for Windows/Engineering Tools/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA360FP2_U4 |  | Ovation 3.6.0+ FP2_U3 |  | Ovation for Windows | Ovation | Engineering Tools/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p>OvPtImport.exe will be changed to ignore CJC-related attributes if found in an import file for default analog and default deluxe analog points.</p> | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 111886
39088 | FINDING | By clicking B3 field in value tab of PI application goes to A2 record field of online help wrongly instead B3. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-09 03:36 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-09 03:36 | 75303 |  |  | 2017-05-09 03:36 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-19 03:00 |  | <p>By clicking B3 field in value tab of PI application goes to A2 record field of online help wrongly instead B3.same is observed on Ov3.6.0 with FP1</p> |  |  |  | SJ April 19, 2017: In OvationApplications.chm, for record types book, help id is used as follows: For 'Packed Dynamic data fields'- help id of A2 record field: 20553, help id of B3 record field: 20255. Reassigning it to the developer. | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Documentation | <p>SJ April 19, 2017: In OvationApplications.chm, for record types book, help id is used as follows: For 'Packed Dynamic data fields'- help id of A2 record field: 20553, help id of B3 record field: 20255. Reassigning it to the developer.</p><p>TN:05/09: Verified in U4 that issue has been fixed. Hence closing this finding.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Benzvi, Mati EMR SYSS PWS PITT | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA360FP2_U4 |  | OV3.6.0 all EWS stations with FP2-U3 &amp; FP1. |  | Ovation for Windows | Ovation | Operator Station/Point Information | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>SJ April 19, 2017:&nbsp;Reassigning it to the developer.<br></p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | FP2-U3 |  |  | FINDING | [6 empty] | 112431
39093 | FINDING | For Operator Mapper algorithms, from the control builder->right click help goes to the general Algorithm Online help intsead of the particular algo of APC toolkit. | Bush, Kirt T EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-16 01:53 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-16 01:53 |  |  |  | 2017-05-16 01:53 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-19 06:08 |  | For Operator Mapper algorithms, (Keyoard/Setpoint/Mastation Mappers,) &nbsp;from the control builder-&gt;right click help goes to the general Algorithm Online help instead of the particular algo of APC toolkit. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Drop-100-DBS 2012R2, OV360FP2+APC 3.6.0_update_U1 |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>AA (04-20-17): Reassigning this Finding to the concerned developer responsible for merging the generated APC Toolkit online help with the latest release Builds. For reference purpose, you can see the latest APC Toolkit 3.6.0 Update 1 User Guide kept at:</p><p><br></p><p><a href="file://\\Uspit-fp04\val\Tests\APC\3.6.0">\\Uspit-fp04\val\Tests\APC\3.6.0</a> Update 1\Docs'</p><p><br></p><p>TN:05-16-2017: Verified the issue in U2 &amp; found help is opening correctly. now. Thus closing the finding.<br></p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>add the algorithm&nbsp;in the control sheet. right click-help.</p> |  | OVA360FP2-U3 |  |  | FINDING | [6 empty] | 112889
39099 | FINDING | Event trend: Some Cosmetic Problems in Filter tab. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:27 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:27 |  |  |  | 2017-06-15 13:27 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-19 17:28 |  | Filter tab in event trend has some cosmetic issues-<div>(1) Network/unit section is not displayed in Ribbon Bar. (It is not working at all.&nbsp;<a href="https://uspit-tfs-v.emrsn.org/tfs/Quality/FINDING/_workitems/edit/39195" class=caption style="box-sizing:border-box;color:rgb(0, 122, 204);cursor:pointer;font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:18px;white-space:nowrap;">FINDING 39195:</a>&nbsp;has been entered)</div><div>(2) Under Historian tab, there is nothing in brackets along with historian name. It should be either removed or has text ('OPH') inside.</div><div>See the attached snapshots</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | Ovation-OVA360FP2_U3<div>Drop Name- Drop127 (EMILY)</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03</div> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 114359
39100 | FINDING | Online help of APC360_002 ->Using Operator mapper Algorithms->some lines are missing for both KBDMapper & Setpoint Mapper sections. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-16 02:54 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-05-16 02:54 | APC3.6.0_Update_U2/75722 |  |  | 2017-05-16 02:54 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-19 23:37 |  | <p>Online help of APC360_002 -&gt;Using Operator mapper Algorithms-&gt;some lines are missing for both Keyboard Mapper &amp; Set Point Mapper sections.</p><p>Attached are the snapshots.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Documentation | <p>AA (05-16-17): The issue has been resolved in the U2 Build of 3.6.0 Update 1.</p><p><br></p><p>The online help is updated, The updated pdf is kept at: <a href="file://uspit-fp04/val/Tests/APC/3.6.0">\\Uspit-fp04\val\Tests\APC\3.6.0</a> Update 1\Docs</p><p>TN:05-16-17:&nbsp; Verified the issue is fixed in U2. Thus closing the finding.</p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | APC3.6.0_Update_U2 |  | Drop-100 (2012R2-OS)-OV3.6.0+APC3.6.0_Update_U1 |  | Ovation for Windows | Ovation | Controller/Algorithms | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>AA (05-16-17): The issue has been resolved in the U2 Build of 3.6.0 Update 1.</p><p><br></p><p>The online help is updated, The updated pdf is kept at: <a href="file://\\Uspit-fp04\val\Tests\APC\3.6.0">\\Uspit-fp04\val\Tests\APC\3.6.0</a> Update 1\Docs</p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Add the advanced algo in the control sheet. Right click-&gt; help. Online help of APC360_002 opens.</p><p>Under the sections of Using Operator mapper Algorithms.</p> |  | OVA360FP2-U3 +APC3.6.0_Update_U1 |  |  | FINDING | [6 empty] | 112892
39101 | FINDING | GBNT Crashes occasionally while dragging & dropping anything multiple times into condition box | Johnson, Kathy EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-28 03:35 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-28 03:35 | 75302 |  |  | 2017-04-28 03:35 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-20 02:09 |  | <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000">While using variables in conditional boxes, GBNT crashes sometimes..</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000">As per communication with cdeveloper, it&nbsp;is found that GBNT crashes repeatedly if&nbsp;3 or 4 variables are dragged-n-dropped&nbsp;onto consecutive lines of the GBNT:ProcessPt dialog conditional field. The crash would happen after dropping the 3rd or the 4th variable.&nbsp;&nbsp;</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000" size=3>&nbsp;</font></span></p> |  |  |  | Test dragging-n-dropping variables from GBNT_Variables dialog into multi-line edit fields on dialogs (e.g. PROCESS_PT dialog conditional field, DYNAMIC_LINE/DYNAMIC_POLYGON dialog x,y coords field, BLINK dialog conditional fields, etc. ..) | 0 |  |  |  | prs 28Apr 2017: Issue fixed. closing this finding. | 0 |  | Ovation for Windows/Engineering Tools/Graphics Builder/Software | was setting a NULL character beyond the memory allocated in a temporary buffer ... |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_FP2_U4 |  | 3.6.0_FP2_U3, DBS Drop100. |  | Ovation for Windows | Ovation | Engineering Tools/Graphics Builder | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | Fixed in U4 | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Observed occasionally. Steps mailed to developer. |  | 3.6.0_FP2_U3 |  |  | FINDING | [6 empty] | 111896
39102 | FINDING | Runtime Graphics application crashes occasionally after working on mini alarm summary | Spillane, Donal AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-24 05:42 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-24 05:42 | [7 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-20 03:03 |  | <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000">Online Graphics application crashed when we directly close the diagram after working on mini Alarm Summary (for&nbsp;Alrm Group Icon),&nbsp;without closing mini alarm summary. Attached are the jpegs from Event Viewer for GraphicsAlarm-Crash.</font></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Graphics/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0_FP2_U3. DBS drop100 |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>Is it possible for me to log into your system to look at your environment and try to recreate the problem as I can not reproduce it here on my test system.</p><p>prs 24Apr: E-mailed developer required inputs on 20Apr.</p> | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ul> <li><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000">While working on Alarm_Group_Icon, opened Mini Alarm Summary for the Alarm Icon.</font></span></li> <li><span style="FONT-FAMILY:&quot;Calibri&quot;,sans-serif;"><font color="#000000">Online Graphics application crashed occasionally when we directly close the diagram after working on mini Alarm Summary (for&nbsp;Alrm Group Icon),&nbsp;without closing mini alarm summary.</font></span></li></ul> |  | 3.6.0_FP2_U3 |  |  | FINDING | [6 empty] | 111545
39103 | FINDING | High Performance Alarm Icon in Graphics: Some of the Variable Fields of Alarm_Group_Data type are not working properly | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-07-19 05:12 | [11 empty] | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-07-19 05:12 | 76784 |  |  | 2017-07-19 05:12 |  |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | 2017-04-20 03:23 |  | <p>Some of the Variable Fields of Alarm_Group_Data type are not working properly. These fields are displaying incorrect information as displayed in attached &quot;Incorrect Alarm_Group_Data fields&quot; jpeg.</p> <p>&nbsp;</p> <p>Group_Priority:&nbsp;&nbsp; &nbsp;It should be&nbsp;<strong>6</strong> instead of <strong>3</strong></p> <p>Group_Status:&nbsp;&nbsp;&nbsp; &nbsp;It should be&nbsp;<strong>3</strong> instead of <strong>1</strong></p> <p>Pri_Ack[6]:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; It should be&nbsp;<strong>1</strong> instead of <strong>2</strong></p> <p>Pri_alarms[7]:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;It should be <strong>3</strong> instead of <strong>0</strong></p> <p>Pri_Supp[7]:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;It should be <strong>0</strong> instead of <strong>1</strong></p> <p>&nbsp;</p> <p>Another field Pri_Unack is displaying corrupt data as &quot;++++&quot;</p> <p>&nbsp;</p> <p>Please note that all the graphics and macros have been compiled after installing U3 and Downloaded to the drops. Graphics application has been restarted. </p> |  |  |  | Use attached test graphic. | 0 |  |  |  | PRS 19July2017: Retested Finding in 3.6.0_FP3_U2. All the reported fields are displaying correct data. Finding Fixed. | 0 |  | Ovation for Windows/Operator Station/Graphics/Software | Code changes for NUM_EVENTS field of ALARM_GROUP_DATA variables in runtime graphics did not make it into U3; U4 will contain the required support. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0_FP3_U2 |  | 3.6.0_FP2_U3 |  | Ovation for Windows | Ovation | Operator Station/Graphics | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Saxena, Pratishtha EMR SYSS PWS NOIDA | Validation |  | <p>Need the U4 version of runtime graphics. Changes for NUM_EVENTS field went out in GB in U3(4/9/17), but not put into graphics.exe until 4/11/17 (so not in U3 as that build was made 4/10/17).</p> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ul> <li>Used Variable Fields of Alarm_Group_Data type as Process point command in foreground.</li> <li>Save and compiled the diagram. </li> <li>Downloaded to the drop</li> <li>Started Runtime graphics application and open the diagram.</li> <li>Data displayed is as shown in the attached jpeg. Mini alarm Summary is also shown to know the group data.</li></ul> |  | 3.6.0_FP2_U3 |  |  | FINDING | [6 empty] | 116156
39106 | FINDING | Controller oscillography doesn't work when event trigger point is placed off scan | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-26 11:46 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-26 11:46 | 75337 |  |  | 2017-04-26 11:46 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-20 08:08 |  | Controller oscillography doesn't work when event trigger point is placed off scan.<div><br></div><div>Fails with OSC Error : 0x4 : 0xFFFFFFFF6 : 0 : 0</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | OVA360FP2U4 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Validation |  | There was diagnostic code in place to log instances the oscillography &quot;put dynamic&quot; library function to see what tasks are calling this function. &nbsp;When taking a point off scan, the value changes from a task (ADM) that is not a control task, this causes the log message. &nbsp;The log was intended to be a &quot;notice&quot; but was accidentally set to &quot;error&quot;. &nbsp;The issue as been corrected by changing it to an debug print message. | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Take an oscillography or trigger point off-scan. |  | FP2U4 |  |  | FINDING | [6 empty] | 111727
39107 | FINDING | DEC Oscillography does not work when the backup controller takes control | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-26 11:47 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-26 11:47 | 75337 |  |  | 2017-04-26 11:47 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-04-20 08:56 |  | DEC Oscillography does not work when the backup controller takes control. &nbsp;The controller must boot up in primary mode in order for DEC oscillography to work. &nbsp;The OSC tasks are pending on a semaphore from coord, waiting for the controller to come in control. The problem is that COORD or whoever is not giving the semaphore. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wimer, Walter L EMR SYSS PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | 360FP2U4 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  | Added the semaphore gives to:&nbsp;__COORDMON_tasks_resume. | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | 360FP2U3 |  |  | FINDING | [6 empty] | 111728
39112 | FINDING | Controller Triggered Event is not working. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 09:20 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 09:20 | 75058 |  |  | 2017-04-27 09:20 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-20 16:36 |  | Controller triggered event is not working. Not able to see any event or data in OPH after trigger. |  |  |  | Perform a controller triggered event and verify the information is sent to the scanner\oph | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | 360FP2U4 |  | OVA360FP2_U3 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | The string case of the &quot;metaData&quot; xml node in the metadata file was not correct. &nbsp;Has been changed to &quot;Metadata&quot;.<div><br></div><div>YJ: Retested in U4. Able to generate Events but for some typical scenarios controller is failing on loading events. (F#39132-<span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">&nbsp;failure occurs when&nbsp;new points and the configuration are loaded in one step).</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">&nbsp;</span></div><div><br></div> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 111811
39113 | FINDING | Developer Studio: Not able to add 2nd Trigger Event under Controller. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:50 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:50 | 75746 |  |  | 2017-06-01 13:50 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-20 16:45 |  | Not able to add 2nd Trigger Event under Controller.<div>Snapshot is attached.<br><div><br></div></div> |  |  |  | The affected area is limited to the operation menu for the phantom folder [Triggered Events] in Ovation Development Studio.<div><br></div><div>YJ: Retested in FP03. Issue fixed.</div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  | OVA360FP2_U3 Developer Studio<div><br></div> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>The Insert operation was inadvertently left out of the operations menu for the parent&nbsp;phantom folder [Triggered Events].&nbsp; This will be corrected.</p><p>This was missed during development (in part) because the testing&nbsp;of controller triggered event creation focused primarily on import.</p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Controller --&gt; Configuration --&gt; Controller --&gt; Triggered Events --&gt; Currently only one event can be define.&nbsp; |  | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 113644
39114 | FINDING | Controller Triggered Event: Able to add blank "Trigger Event Point" in Developer Studio, No error message even if point name is missing. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:50 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:50 | 75746 |  |  | 2017-06-01 13:50 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-20 16:59 |  | Developer studio is allowing to add blank &quot;Trigger Event Point&quot;.<div>No error popup If user does not enter any point name in &quot;Trigger Event Point&quot; window. &nbsp;</div> |  |  |  | <p>The affected area is the definition of this particular attribute.&nbsp; Note that the specification of the event trigger point will also be changed to be required.</p><p>No specific test recommendation other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software | <div><br></div><div>YJ: Retested in FP03. Issue fixed.<br></div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  | Ovation-OVA360FP2_U3 Developer Studio |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | The definition trigger event point attribute will be altered to make it a required field (i.e., the field cannot be left blank/empty).&nbsp; In addition, the event trigger point (on the event object) will also be made to be a required field. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Controller --&gt; Configuration --&gt; Controller --&gt; Triggered Events --&gt;</span>Trigger Event Point --&gt;<span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">&nbsp;&nbsp;</span>Insert new or open &quot;Trigger Event Point&quot; --&gt; do not enter ovation point --&gt; Apply --&gt; Developer studio is not generating error and adding blank point.<div>Snapshot is attached.</div> |  | OVA360FP2_U3 |  |  | FINDING | [6 empty] | 113645
39121 | FINDING | STABLE97: Selecting Help from STABLE97 symbol dosn't open correct page. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Lal, Ramesh External | 2017-05-16 22:35 | [11 empty] | Lal, Ramesh External | 2017-05-16 22:35 |  |  |  | 2017-05-16 22:35 |  |  |  | Lal, Ramesh External | 2017-04-21 06:33 |  | <p>If we open on-line Help for STABLE97 algorithm it doesn't open the page for STABLE97,&nbsp;the previously opened page will be displayed instead. </p><p>The behaviour is the same if Help is selected through right click on STABLE97 symbol either in Control Builder or Signal Diagram.</p><p>Please refer the attached snapshots.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p>DBS Drop100 (Win Server 2012R2), Advanced Controller Drop25/Drop75</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>5/17/17: RL - Tested after installation of APC 3.6.0 Update 1_U2 build. Help is working fine now. Hence, finding is closed.</p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>- Right click on STABLE97 algorithm symbol either in Control Builder or Signal Diagram and select 'Help'.</p><p>- Verify the page displayed.</p><p><br></p> |  | OVA360FP2-U3 |  |  | FINDING | [6 empty] | 112937
39127 | FINDING | OV360FP2: SRF2257- Control Logic of Virtual SIS CHARAMs goes into bad quality after Full snapshot load if snapshot has SIS Force values | Raciborski, Mikolaj AUTOSOL PSS WRSW | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-24 02:46 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-24 02:46 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-21 21:50 |  | <p>Control Logic of Virtual SIS CHARAMs Control Sheet goes into bad quality after Full snapshot load if snapshot has SIS Force values.</p> <ol> <li>The output of all Virtual SIS CHARMs algorithms goes into bad quality.</li> <li>The ouput pins of Control Logic have he status as if the SIS force is in place, but on selecting the SIS algorithm in Signal Diagram, it does not show SIS force on it's input.</li> <li>The output of algorithms does not change with change in input values.</li> <li>It it not possible to put Control Module into Debug Mode (for SIS Force).</li></ol> <p>Please refer to attached <em>OvationError.log</em> and <em>Warning_VCSLS_Mainport.txt</em> for Ovation Error Log messages and Warning message recorded through VCSLS mainPort. No error messages were found in VCSLS mainPort.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Sudheer EMR SYSS PWS NOIDA | Pandey, Vijay EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  | <p>Ov3.6.0 Updated with OVA360FP2_U3.<br></p> <p><u>Controller:</u> Virtual Controller configured as OCR1100, OS Version 6.9.4.8, Kernel Version 2.13</p> <p>&nbsp;</p> <p><u>VCSLS:</u> Details from mainPort are as below</p> <p>Common Subsystem Info</p> <p><br>[3;1H Build Date : Mar 17 2017, 14:04:35, 1.0.0.0.ovr</p> <p>&nbsp;Sw Revision: 1.0</p> <p>&nbsp;Hw Revision: 41.1</p> <p>&nbsp;</p> <p>&nbsp;Subsystem ID = Diag&nbsp;&nbsp;&nbsp;&nbsp; State = CONFIGURED&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> <p><br>&nbsp;Current OS Time = Mon Apr 24 07:38:53 2017</p> <p><br>&nbsp;DV System Time&nbsp; = Mon Apr 24 07:38:53 2017</p> <p><br>&nbsp;Since reset&nbsp; = 0 yrs 0 days 0 hrs 55 mins 53 secs </p> <p>&nbsp;</p> <p>&nbsp;SLS Name&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; D1_VCSLS1&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </p> <p>&nbsp;Our ID&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1 </p> <p><br>&nbsp;Simplex&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Y</p> <p>&nbsp;Left SLS&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Y</p> <p>&nbsp;Commissioned&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Y</p> <p>&nbsp;Locked&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; N</p> <p>&nbsp;Active&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Y</p> <p>&nbsp;Was Configured&nbsp;&nbsp;&nbsp; Y</p> <p>&nbsp;</p> <p>&nbsp;Local Task Status:&nbsp;0000 Good</p> <p>&nbsp;Subsystem Integrity:&nbsp;00000001</p> <p>&nbsp;Last CRC test time:&nbsp;248 sec</p> <p><br>&nbsp;Virtual CSLS Factor:&nbsp;5</p> <p><br>&nbsp;Firmware CRC: 2828863428</p> <p>&nbsp;PlatformID: </p> <p>&nbsp;Serial Num: </p> <p>&nbsp;Part Num&nbsp; : </p> <p>&nbsp;MFT Rev&nbsp;&nbsp; : 0x0</p> <p><br>&nbsp;Mfg Mac Addr (PRI)&nbsp;&nbsp;&nbsp;&nbsp; : 000000000000</p> <p>&nbsp;Mfg Mac Addr (SEC)&nbsp;&nbsp;&nbsp;&nbsp; : 000000000000</p> <p>&nbsp;Assigned Mac Addr (PRI): 02230A101401</p> <p>&nbsp;Assigned Mac Addr (SEC): 02230A101801</p> <p><br>&nbsp;Unlock Inhibit: Disabled </p> <p>&nbsp;Key Position&nbsp; : Unlock Allowed&nbsp;&nbsp; </p> <p>&nbsp;Min Pulse Period&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; : 4.0</p> <p>&nbsp;Dropped Pulse Counter : 0</p> |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>In a healthy running VCSLS:</p> <ol> <li>SIS force the input pin of a SIS CHARMs algorithm.</li> <li>Through Simcontrol.exe, create (save) a Full snapshot of the Virtual Controller hosting the test VCSLS.</li> <li>Now remove the SIS Force and take the Conttrol Module out of Debug mode.</li> <li>Through Simcontrol.exe, Load the Full snapshot of Virtual Controller hosting the test VCSLS.</li> <li>Observe the Control Logic behavior in Signal Diagram.</li></ol> |  | OV360FP2_U3 |  |  | FINDING | [6 empty] | 111541
39131 | FINDING | DEC - DEC triggered event will not get to OPH if the triggered event logger it is sent to is in backup mode (redundant scanner) | Hatok, Alan M AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Contento, James AUTOSOL PWS PITT | 2018-05-07 09:15 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2018-05-07 09:15 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-24 14:00 |  | <p>The controller is only sending to one triggered event logger.&nbsp; If this logger is a redundant scanner and it is in backup mode, it will not be recieved.</p><p><br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | Contento, James AUTOSOL PWS PITT | Bergey, Steve EMR SYSS PWS PITT | [6 empty] | Implementation |  |  | 3.6.0 + FP2 U3 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Configure the controller to use redundant scanners for the triggered event loggers.&nbsp; Configure so that the backup scanner is first in the list.&nbsp; </p><p>Trigger an event and see that it does not get to OPH.</p> |  | OVA360FP2-U3 |  |  | FINDING | [6 empty] | 127784
39132 | FINDING | Controller Triggered Events: Controllers are going into Fail mode after loading Triggered event configuration. | Hatok, Alan M AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 5 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 13:49 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 13:49 | 76844 | [6 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-24 14:57 |  | <p>Controllers are going into fail mode after loading Controller Triggered event configuration.</p><p>Not able to bring the controller back to healthy condition even after clear load operation.</p><p><br></p><p>Controller Error : Subsystem Group 1 Error : OSC Error : 0x1 : 0x3 : 0x1 : 0x0&lt;/Err&gt;</p> |  |  |  |  | 0 |  |  |  | <span style="color:rgb(34, 34, 34);">YJ: Failure still occurs when&nbsp;new points and the configuration are loaded in one step.&nbsp;</span><div>Controller Error : Subsystem Group 1 Error : OSC Error : 0x2 : 0x1e : 0x1 : 0x0<span style="color:rgb(34, 34, 34);"><br></span></div> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | Perdeus, Matthew AUTOSOL PWS PITT | [8 empty] | Implementation | 3.6.0 FP3 |  | OVA360FP2_U3 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Define Triggered Event --&gt; Load the controller. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116110
39133 | FINDING | OCR Event Configuration Initializtion | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2017-07-21 14:20 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-07-21 14:20 | 76858 |  |  | 2017-07-21 14:20 |  |  |  | Hatok, Alan M AUTOSOL PWS PITT | 2017-04-24 15:51 |  | During the loading of a controller drop, the triggered event software may attempt to acquire a LID prior to the LID being created. If this is the case the controller will go into failure mode. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Perdeus, Matthew AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0 FP3 |  |  |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Hatok, Alan M AUTOSOL PWS PITT | Development |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | cg (7/18/17) - Finding assigned to Matt for retesting. |  | SP2 |  |  | FINDING | [6 empty] | 116394
39139 | FINDING | Safety Shell SVTP-Editorial changes need to be done in SVTP section 5.2 and section 5.3. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:34 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:34 |  |  |  | 2018-01-10 04:29 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-04-25 12:16 |  | <font face=Arial size=3><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:107%;font-size:9pt;">Following Editorial changes need to be done in SVTP section 5.2 “Safety Shell Configuration” and section 5.3 &quot;Database Export/Import support for High Integrity Attributes&quot;.</span></p></font><p style="margin:0in 0in 0pt;"><font face=Arial><b><span style="line-height:107%;font-size:9pt;">1. Statement modification needed in Test case 5.2.4.d</span></b><span style="line-height:107%;font-size:9pt;">,</span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In Test case, statement </font><i><font face=Arial>“Each High Integrity point originated by OCR1100 and received by OCR400 shall be forced to some other value at least once during execution of the test.” </font><u><br><font face=Arial> </font></u></i></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>Statement in test case needs to be modified as</strong>: </font><i><font face=Arial>“Each High Integrity point originated by OCR1100 and received by <b>Virtual Controller OCR1100</b> shall be forced to some other value at least once during execution of the test.”</font><u><br><font face=Arial> <br> </font></u></i></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><span style="line-height:107%;font-size:9pt;"><font face=Arial>2. Statement modification needed in Test case 5.2.5 and 5.2.6</font></span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In description of Test case 5.2.5 and 5.2.6, there are steps (step1 to step16) mentioned for changing High Integrity configuration for points in system. In Validation testing it is observed that minor modification needed in statement mentioned in steps-4, 12 and 16. Details are mentioned in 2.a, 2.b, 2.c. Modification in test cases as per verified software functionality.<br><br></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial> <b>2.a</b>. <b>Statement in Step-4</b><i>: “Switch off the High Integrity for the point and save the configuration. </i></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 4.5pt;line-height:normal;text-indent:9pt;"><font face=Arial><i><span style="font-size:9pt;"><span>&nbsp;</span><span>&nbsp;</span></span></i><span style="font-size:9pt;">Verify that a pop-up<i> “<u>are you sure</u>” </i>message appeared for confirmation of the modification.”</span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial> <b>As per software functionality, statement in step-4 needs to be modified as</b>: <i>Switch off the High Integrity for the point and save the configuration. Verify that a pop-up <u>“High Integrity” is being changed from “1” to “0”. </u></i></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 36.9pt 0pt 0.25in;"><i><u><span style="color:windowtext;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">This will place the originating drop and all drops which explicitly receive this point into a reload-required state.</span></u></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 36.9pt 0pt 0.25in;"><i><u><span style="color:windowtext;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">Do you wish to proceed?</span></u></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0in;line-height:normal;"><b><u><span style="font-size:9pt;"><br><font face=Arial> </font></span></u></b><font face=Arial><b><span style="font-size:9pt;">2.b.</span></b><i><span style="font-size:9pt;"> <b>Statement in Step-12</b>: Switch on the High Integrity for the point and save the configuration.</span></i></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in -9pt 0pt 0.25in;line-height:normal;"><span style="font-size:9pt;"><font face=Arial><strong> </strong><strong>As</strong> <b>per verified software functionality, s</b><strong>tatement in step-12 needs to be modified as</strong>: <br> <i>Switch on the High Integrity for the point and save the configuration.</i></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><i><span style="line-height:107%;font-size:9pt;"><font face=Arial>Verify that a pop-up<u> “High Integrity” is being changed from “0” to “1”. </u></font></span></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 36.9pt 0pt 0.25in;"><i><u><span style="color:windowtext;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">This will place the originating drop and all drops which explicitly receive this point into a reload-required state.</span></u></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 36.9pt 0pt 0.25in;"><i><u><span style="color:windowtext;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">Do you wish to proceed?</span></u></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0in;line-height:normal;text-indent:-4.5pt;"><b><u><span style="font-size:9pt;"><br><font face=Arial> </font></span></u></b><font face=Arial><b><span style="font-size:9pt;">2.c. <i>Statement in Step-</i>16</span></b><span style="font-size:9pt;">: “<i>Load all controllers used for the test.”</i></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0.25in;line-height:normal;text-indent:-4.5pt;"><span style="font-size:9pt;"><font face=Arial><span>&nbsp;</span><span>&nbsp;<strong>As</strong> <b>per verified software functionality, s</b></span><strong>tatement in step-16 needs to be modified as</strong>: “<i>Clear and load all controllers used for the test.”</i></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>3. Statement modification needed in Test case 5.2.14.a</strong><b>.</b></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In Test case 5.2.14.a, mentioned a <b>Popup warning message</b>:</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><i><u><span style="line-height:107%;font-size:9pt;"><font face=Arial>“Drop11/51” is being changed from “Virtual Controller” to “Controller” and originates one or more High Integrity Points.” <br> “This will place this drop (and any other drop which explicitly receives its High Integrity Points) into a reload-required state.”</font></span></u></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 0.25in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong> Pop Warning message needs to be modified </strong><strong>as</strong> <b>per verified software functionality</b><strong> </strong>.: </font><i><u><font face=Arial>“Drop Type” is being changed from “Virtual Controller” to “Controller” and originates one or more High Integrity Points.” <br> “This will place this drop (and any other drop which explicitly receives its High Integrity Points) into a reload-required state.”</font></u></i></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial><b><span style="line-height:107%;font-size:9pt;">4. Statement modification needed in Test case 5.2.14.b, Test case 5.2.15.b as per verified software functionality</span></b></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Test cases mentioned for Popup warning message while performing High Integrity configuration modification with conformation option for proceeding or cancel the modification. <br> Confirmation option needs to be modified as per software.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;&nbsp; </font></span><font face=Arial><b><span style="line-height:107%;font-size:9pt;">Statement in test case</span></b><span style="line-height:107%;font-size:9pt;">: “<i>…….Message <span>&nbsp;</span>“<u>Do you wish to proceed?</u>&quot; confirmation message </i></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;"><i><span style="line-height:107%;font-size:9pt;"><font face=Arial>appear on the screen. Choose option “<u>No</u>” to not perform the modification and verify that none status of drops within Developer Studio has changed.”</font></span></i></p><font face="Times New Roman" size=3> </font><span style="line-height:107%;font-size:9pt;"><font face=Arial><b>&nbsp; Statement in test case needs to be modified as</b> <strong>as</strong> <b>per verified software functionality</b>: “<i>……. Message </i></font></span><font face=Arial><i><u><span style="line-height:107%;font-size:9pt;">“Do you wish to proceed</span></u></i><i><span style="line-height:107%;font-size:9pt;">?&quot; confirmation message appear on the screen. Choose option <u>“Cancel”</u> to not perform the modification and verify<br>&nbsp;&nbsp;&nbsp;&nbsp; that none status of drops within Developer Studio has changed.”</span></i></font><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>5. Statement modification needed in Test case 5.2.14.e and Test case 5.2.15.e.</strong></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Test cases statement mentioned for Popup warning message while performing High Integrity configuration modification with conformation option for proceeding or cancel the modification. <br> <b>Statement in Test case</b>: “</font><i><font face=Arial>…. This time select option <u>“<b>Yes</b></u>” on the warning pop-up to continue <span>&nbsp;&nbsp;</span>with the change.”<br> </font></i></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;text-indent:-4.5pt;"><font face=Arial><span><strong><span>&nbsp;</span>Statement in test case needs to be modified as </strong><strong>per verified software functionality</strong>: “<i>…. This time select option <u>“<b>OK</b></u>” on the warning pop-up to continue with the change.”</i></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>6. Statement modification needed in Test case 5.2.15.a. </strong></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In Test case 5.2.15.a, mentioned a <b>Popup warning message</b> </font><i><u><font face=Arial>“Drop 32/82 is being changed from “Controller” to “Virtual Controller” and originates one or more High Integrity Points.”<br> “This will place this drop (and any other drop which explicitly receives its High Integrity Points) into a reload-required state.”</font></u></i></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;&nbsp;&nbsp;&nbsp; </font></span><font face=Arial><span><strong>Popup warning message mentioned in test case needs to be modified as </strong><strong>per verified software functionality</strong>:</span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>“</font><u><font face=Arial>Drop Type”</font><i><font face=Arial> is being changed from “Controller” to “Virtual Controller” and originates one or more High Integrity Points.”<br> “This will place this drop (and any other drop which explicitly receives its High Integrity Points) into a reload-required state.”</font></i></u></span></p><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><em><u><font face=Arial><br></font></u></em></span></p><span style="line-height:107%;font-size:9pt;"><font face=Arial><span style="line-height:107%;font-size:9pt;"><font face=Arial><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><br></font></span></p><span style="line-height:107%;font-size:9pt;"><font face=Arial><p style="margin:0in 0in 0pt;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>7. </strong></font></span><strong>Modification&nbsp;needed for&nbsp;verification&nbsp;of LP and DP point type quality.</strong></span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp; Test case 5.2.16, verifying the value and quality propagation between two controllers (point originated by Virtual Controller and received by Physical Controller) for following record type: <strong>LA, DA, LD, DD, LP, DP, PD</strong>.<br> </span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp; Control logic mentioned in Test case is valid for LP and DP point type verification also.</span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp; <strong>Quality for LP and DP point</strong>&nbsp;can be verified via <b>A3</b> record field:</span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp;<br></span><font face="Times New Roman"><font size=3><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;"><strong>&nbsp;&nbsp; A3 field (Invalidity Bits) <br> &nbsp;&nbsp; Description:</strong></span><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">&nbsp;</span></font><font size=3> </font></font><span style="color:windowtext;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">Any “forced” bit will cause the invalidity bit for that digital point to be SET.</span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp; Quality of LP and DP point type cannot be forced to Good/Bad/Fair/Poor as mentioned in the <b>test case 5.2.16.c</b>.</span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3> </font></p><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;"><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;">&nbsp;&nbsp;&nbsp;Hence verification procedure for quality of LP and DP point need to be updated in test case for reference as&nbsp;<font face="Times New Roman" size=3> </font></p><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><b><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">&nbsp;&nbsp;&nbsp; “Steps for verification of LP and DP point type,</span></b></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in -0.25in 0pt 0in;text-align:left;color:black;line-height:105%;font-style:normal;font-weight:normal;"><b><i><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">Force the value of pointA, verify that corresponding A3 bits of the point will be SET (value of 1 or TRUE).</span></i></b></li><font face="Times New Roman" size=3> </font><li style="margin:0in -0.25in 0pt 0in;text-align:left;color:black;line-height:105%;font-style:normal;font-weight:normal;"><b><i><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;">Verify that value of pointB and corresponding A3 bits (for quality) showing the same value as pointA.”</span></i></b></li></ul><span style="color:windowtext;line-height:105%;font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;"><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial><strong>8. Statement&nbsp; modification needed in Test case 5.3.5.b </strong></font></span></p><font face="Times New Roman" size=3></font><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Test cases statement says <em>&quot;Verify that for all High Integrity points configured for the drops used in the test&nbsp; the non-HIGH_INTEGRITY attribute is defined with value 0.&quot;</em></font></span></p><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Statement needs to changed as <em>&quot;Verify that for all non-High Integrity points configured for the drops used in the test the HIGH_INTEGRITY attribute is defined with value 0&quot;</em></font></span></p><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><br></span></p><p style="margin:0in 0in 0pt 13.5pt;"><font face=Arial><span><i><br></i></span></font></p></span><p style="margin:0in -0.25in 0pt 0in;text-align:left;color:black;line-height:105%;font-style:normal;font-weight:normal;"><br></p><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font></ul><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><font face="Times New Roman" size=3> </font><br><br><br></p></span><p align=left style="margin:0in 0in 0pt;text-align:left;line-height:105%;"><br></p><p style="margin:0in 0in 0pt 13.5pt;"><font face="Times New Roman" size=3><strong> <br></strong></font></p></font><p style="margin:0in 0in 0pt 13.5pt;"><br></p></span><p style="margin:0in 0in 0pt 13.5pt;"><br></p><p style="margin:0in 0in 0pt 13.5pt;"><br></p></font><p style="margin:0in 0in 0pt 13.5pt;"><br></p></span><p style="margin:0in 0in 0pt 13.5pt;"><br></p></font><p style="margin:0in 0in 0pt 13.5pt;"><br></p></span><p style="margin:0in 0in 0pt 13.5pt;"><br></p><p style="margin:0in 0in 0pt 13.5pt;"><span style="line-height:107%;font-size:9pt;"><em><u><font face=Arial><br></font></u></em></span></p><font face="Times New Roman" size=3> </font><font face=Arial size=3>&nbsp;</font><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/Engineering Tools/General/SVTP/STP | WFX in&nbsp; <strong>SVTP_rev1.5</strong> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | SVTP_rev1.5 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/22/17&gt; please continue testing with the&nbsp;resolutions proposed in the Description box. <br></font><font size=3> Note clearly in a comment field in your test record that you are using the proposed resolutions.&nbsp;<br> The SVTP should be modified with these changes at the end of the project.</font></span></p><p style="margin:0in 0in 8pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>VP&gt; Will fix in SVTP_rev1.5.</font></span></p><font face="Times New Roman" size=3> </font> | 11 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122423
39143 | FINDING | Trend Application: Trigger indication does not precisely match metadata from DEC Triggered Oscillography | Jain, Yukta AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 17:57 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 17:57 |  |  |  | 2017-07-19 17:57 |  |  |  | Wimer, Walter L EMR SYSS PWS PITT | 2017-04-25 14:52 |  | Looking at the DEC Triggered Oscillography raw metadata and comparing it to the Trend graph, there is a slight timing discrepancy.<div><br></div><div>Note that the user does not normally look at the raw metadata, so the user will trust the Trigger Position Indicator in the Trend Application, which may lead the user to false conclusions.<br><div><br></div><div>Metadata:</div><div><br></div><div><div>&nbsp; &nbsp; &nbsp; &lt;triggerVar&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;name&gt;tsig_input&lt;/name&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;value&gt;59.200001&lt;/value&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;/triggerVar&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;triggerVar&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;name&gt;tsig_rnd_slope&lt;/name&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;value&gt;0.583143&lt;/value&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;/triggerVar&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;triggerVar&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;name&gt;tsig_noise&lt;/name&gt;</div><div>&nbsp; &nbsp; &nbsp; &nbsp; &lt;value&gt;-0.596062&lt;/value&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;/triggerVar&gt;</div><div>&nbsp; &nbsp; &lt;/triggerInfo&gt;</div><div><br></div><div>&nbsp; &nbsp; &lt;eventInfo&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;startTime&gt;2017-04-25T14:39:13.384852538Z&lt;/startTime&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;duration&gt;30.000000000&lt;/duration&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;triggerTime&gt;2017-04-25T14:39:35.882664368Z&lt;/triggerTime&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;triggerIndex&gt;57600&lt;/triggerIndex&gt;</div><div>&nbsp; &nbsp; &nbsp; &lt;dataBufferEntries&gt;76800&lt;/dataBufferEntries&gt;</div></div><div><br></div><div><br></div><div>Trend graph (blue cursor line corresponds to above metadata values):</div><div><br></div><div><img src="http://tfs.emersonprocess.com/tfs/Quality/WorkItemTracking/v1.0/AttachFileHandler.ashx?FileNameGuid=61cbc94d-9672-44d7-afdd-1b47c7d1a865&amp;FileName=temp1493149926747.png" style="width:945px;"><br>&nbsp;<br></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Jain, Yukta AUTOSOL PWS NOIDA | Contento, James AUTOSOL PWS PITT | [8 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  |  |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Wimer, Walter L EMR SYSS PWS PITT | Development |  |  | 17 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | YJ: Retest in OVa3600022 + OPH360003. Still there is a slight timing discrepancy.&nbsp;<div>Snapshots are attached.</div><div><br></div><div>YJ: As per Walt, Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003.</div><div>Re-tested in Fp03</div> |  | FP2 |  |  | FINDING | [6 empty] | 116227
39144 | FINDING | Controller Triggered Event: “Re-trigger time (3 min)" functionality is not working. | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 15:03 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 15:03 | 76857 |  |  | 2017-07-17 14:53 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-25 15:26 |  | <p><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;">As per the specification, controller will enforce a “re-trigger time” of 3 minutes between 2 events which</span><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"> prevents the controller from attempting to send out triggered events in cases where the Trigger Point may be toggling/chattering.<span style="">&nbsp;</span></span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="">But controller&nbsp;is not considering re-trigger time and&nbsp;generating Triggered Event&nbsp;before 3 minutes re-trigger time gap.</span></span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><span style="">Snapshot is attached.</span></span></span></p><p><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;"><br></span></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | <p>OVA360FP2_U4</p><p>Drop4/54 (EMILY)</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ- Tested on FP03_U2 issue is fixed. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116060
39146 | FINDING | Controller Diagnostics Online help has to be updated for the latest Controller Overview enhancements. (Both Description & Image) | Gola, Megha EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 13:44 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 13:44 | [7 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-26 07:02 |  | Latest Controller Overview enhancements details like Controller &amp; Kernel (Patch/change stet) details, are to be updated in the online help&nbsp;. (Both Description &amp; Image). |  |  |  | <p>MG (April 27, 2017):&nbsp;Updated the Figure Controller Diagnostics window in section 24.4.1 To access the Controller Diagnostic tool&nbsp;&nbsp;and&nbsp; also updated the figure and description of the new fields in the Section 24.6 Controller Overview Panel in the Controller Diagnostic window. Please check&nbsp;online help (OvptStudio)&nbsp;in&nbsp;Ovation 3.6.0 FP2 U4&nbsp;build.</p><p>However, the topics were not shared&nbsp;with the standalone help for Controller diagnostics. Hence,&nbsp;the Figure Controller Diagnostics window in section 24.4.1 To access the Controller Diagnostic tool&nbsp;&nbsp;in the help. <font color="#222222">This will be fixed in Ovation 3.6.0 feature pack 3.</font></p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Diagnostics/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | All applicable EWS stations of OV3.6.0-fp2. |  | Ovation for Windows | Ovation | Controller/Diagnostics | Documentation | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>MG (April 27, 2017):&nbsp;Updated the Figure Controller Diagnostics window in section 24.4.1 To access the Controller Diagnostic tool&nbsp;&nbsp;and&nbsp; also updated the figure and description of the new fields in the Section 24.6 Controller Overview Panel in the Controller Diagnostic window. Please check&nbsp;online help (OvptStudio)&nbsp;in&nbsp;Ovation 3.6.0 FP2 U4&nbsp;build.</p><p>However, the topics were not shared&nbsp;with the standalone help for Controller diagnostics. Hence,&nbsp;the Figure Controller Diagnostics window in section 24.4.1 To access the Controller Diagnostic tool&nbsp;&nbsp;in the help. <font color="#222222">This will be fixed in Ovation 3.6.0 feature pack 3.</font></p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Click the online help of Controller Diagnostics. Right now it has the old details. |  | fp2 |  |  | FINDING | [6 empty] | 113069
39153 | FINDING | Event Trend: Memorize & Recall Button are not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:28 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:28 |  |  |  | 2017-06-15 13:28 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-26 17:27 |  | Event Trend: Memorize &amp; Recall Button are not working. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OV360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OV360FP2_U4 |  |  | FINDING | [6 empty] | 114360
39155 | FINDING | OV360FP2: Help option not available in Signal Diagram for LONGACC algorithm. | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2017-04-27 03:22 | [11 empty] | USPITTFSService | 2017-04-27 03:22 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-27 03:22 |  | <p>Help option is not available in menu available on Right Click over LONGACC algorithm in Signal Diagram.</p> <p>Please refer to attahced screenshot (LONGACC_Help_SignalDiagram.png) for more information.</p> <p>To access LONGACC help, we need to&nbsp;select some other algorithm help, then we can navigate to LONGACC algorithm refernce page.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Signal Diagram Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | Aditya, Abhinav AUTOSOL PWS NOIDA | [8 empty] | Implementation |  |  | Ovation 3.6.0 Database Server Drop100 on&nbsp;Net#36 in GEC&nbsp;updated with OV360FP2_U4 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Signal Diagram Viewer | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OV360FP2_U4 |  |  | FINDING | [6 empty] | 111769
39156 | FINDING | OV360FP2: SIS Diagnostics is unable to populate SIS CHARMs information | Raciborski, Mikolaj AUTOSOL PSS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-03 15:50 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-03 15:50 |  |  |  | 2017-05-03 15:50 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-27 03:52 |  | <p><font face=Arial><font color="#000000" size=2><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:105%;"><font size=2>SIS Diagnostics is unable to populate SIS CHARMs (CSLS and VCSLS) inform</font>ation.</span></font></font></p> <p><font face=Arial><font color="#000000" size=1><span style="FONT-SIZE:11pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;LINE-HEIGHT:105%;"><font size=2>Legacy SIS information is available though. Please refer to attached screenshot <em>SIS Diagnostics.png</em>.</font></span></font></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Safety Instrumented System/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ovation 3.6.0 Database Server Drop100 on Net#36 updated with OV360FP2_U4 |  | Ovation for Windows | Ovation | Controller/Safety Instrumented System | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | IC 5/3/17&gt; track as SDR #39224, list in DIR. | 4 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | OV360FP2_U4 |  |  | FINDING | [6 empty] | 112244
39159 | FINDING | OV360FP2: Ovation Developer Studio not allowing to Assign a new VCSLS without providing “Proof Test Interval (days)” to be more than “Proof Test remind alert due (days)“ | Hutchison, Steven EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 1 | USPITTFSService | 2017-04-27 04:09 | [11 empty] | USPITTFSService | 2017-04-27 04:09 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-04-27 04:09 |  | <p>While providing assign option to a VCSLS in Developer Studio, it is now mandatory to assign “Proof Test Interval (days)” to be more than “Proof Test remind alert due (days)“. Earlier these fields were left blank by default and no such message was observed.&nbsp;Without defining these parameters we are not able to assign the VCSLS to a MAC address. Please refer to attached screenshot &quot;Assign_ProofTest.png&quot;.</p> <p>&nbsp;</p> <p>The fields should either have default values equals 6 months, or they should be allowed to be blank if the automatic Proof Test is not configured.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/SIS/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | Ovation 3.6.0 Database Server Drop100 on Net#36 updated with OV360FP2_U4 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/SIS | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OV360FP2_U4 |  |  | FINDING | [6 empty] | 111783
39160 | FINDING | cbOperation application crashes during the import of Control Sheets on Ovation 3.6.0 FP2 U2 setup | Hutchison, Steven EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 13:42 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 13:42 | [7 empty] | Arora, Priyanka AUTOSOL PWS NOIDA | 2017-04-27 04:28 |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><font size=3><font color="#000000">An Ovation setup with Ovation3.6.0 FP2 U2 software was being prepared and importing approx. 22.5K Control sheets in 50 Controller Drops to make it Ovation setup with 500k points (approx. 330k points as user defined points and 170k algorithm points) while the user defined points were already imported on the setup. During these import operations, for two of the Drops, Drop23 and Drop24, the import operation failed due to crash of “cbOperation.exe” and only 10 and 46 sheets got imported out of 457 sheets respectively.</font><span style="COLOR:black;"> </span></font><font color="#000000" size=3>Till the time first cbOperation crash occurred, 9256 Control sheets got already imported on the setup</font><font size=3><span style="COLOR:#1f497d;">.</span></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font face=Calibri><i><font color="#000000" size=3><strong>Note:</strong></font></i><font size=3><font color="#000000"> The Control sheet import was performed through a script which imports Control sheets in 50 Controller Drops (On both Physical and Virtual Controllers) one by one. </font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>Please find the attached mini crash dumps of cbOperation for Drop23 and Drop24.&nbsp; &nbsp;&nbsp;</font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Control Options/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Zochowski, Piotr EMR SYSS RS WRSW | Kijanka, Pawel EMR SYSS RS WRSW | Gupta, Ankit EMR SYSS PWS NOIDA | Jindal, Deepak EMR SYSS PWS NOIDA | Mittal, Utkarsh AUTOSOL PWS NOIDA | Saklani, Rajnish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>DC+DB Server Drop200 (Windows2012 R2) With Ovation 3.6.0 FP2 U2 having 500K points</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>3 VCH - Drop251, Drop252 and Drop248 (Windows 7 SP1)</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font size=3><font color="#000000"><font face=Calibri>OPS- Drop201 (Virtual Machine having Windows2012 R2)</font></font></font></p> <p class=MsoNormal style="MARGIN:0in 0in 0pt;"><font color="#000000" size=3 face=Calibri>Controller Drops configured– 50 (6 Physical and 44 Virtual)</font></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Control Options | Software | In Validation | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Arora, Priyanka AUTOSOL PWS NOIDA | Software Quality |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [6 empty] | EPM Product Development | FP2 U2 |  |  | FINDING | [6 empty] | 113068
39162 | FINDING | Event Trend: Trigger indication on Time axis is not clear in Vertically Orientated graph. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:28 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:28 |  |  |  | 2017-06-15 13:28 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 08:44 |  | Trigger indication (T) on the time axis is not clear when graph is in Vertically Orientation.<div>Snapshot is attached.&nbsp;</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03 | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114361
39163 | FINDING | Event Trend: Horizontal & Vertical Chart Grid buttons are not working properly. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Contento, James AUTOSOL PWS PITT | 2017-06-08 12:20 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2017-06-08 12:20 |  |  |  | 2017-06-08 12:20 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 08:56 |  | Horizontal &amp; Vertical Chart Grid buttons are not working properly. There is problem in selection of buttons (for both Horizontal &amp; Vertical Chart Grid). <div><br> <div><br>As per design, the primary grid lines must be on, when the secondary grid lines are on.</div> <div>&nbsp;</div> <div>However, Primary grid lines can be on without the secondary grid lines being on.</div></div><div><br></div><div>YJ: What about the condition when s<span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">electing the secondary grid is displaying primary &amp; secondary&nbsp;</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">grid</span><font face="Times New Roman, serif"><span style="font-size:13.3333px;">. But un-selecting secondary grid is only making the secondary grid disappear. If button is selecting both then it should un-select&nbsp;both as well.</span></font></div><div><font face="Times New Roman, serif"><span style="font-size:13.3333px;">If secondary is selected, then Primary button can be greyed&nbsp;out and on un-selecting secondary, both should disappear.&nbsp;</span></font></div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">OVA360FP2_U4</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Way it Works (No plans to fix) | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Could not duplicate.&nbsp; Please retest.<div><p class=MsoNormal><span style="font-size:10.0pt;"><br></span></p><p class=MsoNormal><span style="font-size:10.0pt;">YJ: Please follow Steps to reproduce. </span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">Successfully recreated on Drop127.</span></p><p class=MsoNormal><font face="Times New Roman, serif"><span style="font-size:13.3333px;">1. Selecting the secondary grid is also displaying the primary grids. But un-selecting secondary grid is only making the secondary grid diapers. Primary grid is visible however&nbsp;user never opted for that. Select and un-select buttons should be in sync.</span></font></p><p class=MsoNormal><font face="Times New Roman, serif"><span style="font-size:13.3333px;">2. &nbsp;Similarly,&nbsp;</span></font><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">when secondary grid is selected and user un-select primary grid (which is always enabled by default with secondary) then both of the grids diaper. &nbsp;</span></p></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Format Tab --&gt; Ribbon Bar --&gt; Chart Grid --&gt; Horizontal &amp; Vertical Chart Grid buttons are not working properly.<div><br></div><div><table class=MsoTableGrid border=1 cellspacing=0 cellpadding=0 style="border-collapse:collapse;border:none;"> <tbody><tr> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>&nbsp;</p> </td> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-left:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>Primary Grid Line (Visibility)</p> </td> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-left:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>Secondary Grid Line(Visibility)</p> </td> </tr> <tr> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-top:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>Select Primary</p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal><span style="font-family:Wingdings;">ü</span></p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>X</p> </td> </tr> <tr> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-top:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>Un-Select Primary</p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>X</p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>X</p> </td> </tr> <tr> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-top:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>Select Secondary</p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal><span style="font-family:Wingdings;">ü</span></p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal><span style="font-family:Wingdings;">ü</span></p> </td> </tr> <tr> <td width=213 valign=top style="width:159.6pt;border:solid windowtext 1.0pt;border-top:none;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>If (Un-Select Primary)</p> <p class=MsoNormal>or</p> <p class=MsoNormal>If (Un-Select Secondary)</p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>X</p> <p class=MsoNormal>&nbsp;</p> <p class=MsoNormal><span style="font-family:Wingdings;">ü</span></p> </td> <td width=213 valign=top style="width:159.6pt;border-top:none;border-left:none;border-bottom:solid windowtext 1.0pt;border-right:solid windowtext 1.0pt;padding:0in 5.4pt 0in 5.4pt;"> <p class=MsoNormal>X</p> <p class=MsoNormal>&nbsp;</p> <p class=MsoNormal>X</p> </td> </tr> </tbody></table></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114037
39164 | FINDING | Event Trend: Time axis display is corrupting when time span is changed from lower time value to Full range (180 seconds). | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:29 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:29 |  |  |  | 2017-06-15 13:29 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 09:07 |  | Time axis display is corrupting when time span is changed from lower time value (2,6,10 seconds etc) to Full range (180 seconds).<div>This is observed for both Horizontal &amp; Vertical Graph.</div><div><div>Snapshot is attached.</div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03 | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114364
39165 | FINDING | Event Trend: Quick Access Toolbar is missing in Duplicate Trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 14:43 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 14:43 | 76922 |  |  | 2017-07-17 14:43 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 09:27 |  | Quick Access Toolbar is missing in Duplicate Trend.<div>Snapshot is attached.</div> |  |  |  | Retest.<div><br></div><div>YJ- Tested on FP03_U2+OPH360005. issue is fixed.<br></div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Could not duplicate.&nbsp; Please retest.<div><br><div><p class=MsoNormal><span style="font-size:10.0pt;">YJ: Please follow Steps to reproduce. &nbsp;</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">Successfully recreated on Drop127.</span></p><p class=MsoNormal><font face="Times New Roman, serif"><span style="font-size:10pt;">Live and Historical trend </span><span style="font-size:13.3333px;">duplicate</span><span style="font-size:10pt;">&nbsp;windows have quick bar but it is missing in Event trend </span><span style="font-size:13.3333px;">duplicate</span><span style="font-size:10pt;">&nbsp;window.</span></font></p></div></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Trend Menu --&gt; Click &quot;Launch duplicate&quot; --&gt; Quick Access Toolbar is missing in Duplicate Trend. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116056
39167 | FINDING | Event Trend: Not able to zoom out the Graph view. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-26 14:14 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-26 14:14 |  |  |  | 2017-06-26 14:14 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 09:58 |  | <font face="Times New Roman, serif"><span style="font-size:13.3333px;">Not able to zoom out the Graph view.</span></font><div><font face="Times New Roman, serif"><span style="font-size:13.3333px;">Not able to zoom out by either of Escape key, right click and Double click on graph.&nbsp;<br></span></font><div><font face="Times New Roman, serif"><span style="font-size:13.3333px;"><br></span></font></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Could not duplicate.&nbsp; Please retest. <div> <div>Please follow Steps to reproduce. &nbsp;Please note that issue exist with Controller Triggered Events.</div> <div>Successfully recreated on Drop127.</div> <div>&nbsp;</div> <div>Underlying thirdparty software slows down with excessive zooming and UI becomes sluggish. The UI will eventually recover after some time.</div></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Zoom in the graph view&nbsp;<span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">by- Left Click drag and CTRL+Left click drag --&gt; Try &quot;</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">Escape key, right click and Double click on graph&quot;&nbsp;</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">to zoom out. None of them is working.</span><font face="Times New Roman, serif"><span style="font-size:13.3333px;"><br></span></font><div><font face="Times New Roman, serif"><span style="font-size:13.3333px;"><br></span></font></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114840
39168 | FINDING | Controller Triggered Events: Controllers are going into Fail mode after reboot if there is an invalid Triggered event Point in Triggered Event. | Hatok, Alan M AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:56 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:56 | 76844 | [6 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 10:10 |  | Controllers are going into Fail mode after reboot if there is an invalid Triggered event Point added in Triggered Event.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | OVA360FP2_U4<div><br></div> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | &nbsp;<span style="color:rgb(34, 34, 34);font-size:10pt;">YJ: Active controller Controller is going into fail mode after load if there is an invalid trigger point in the controller triggered event.</span><p class=MsoNormal><span style="font-size:10.0pt;color:#222222;"><span style="box-sizing:border-box;">secondary controller also going into fail mode once primary is up after clear operation</span></span></p> <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;color:#222222;">Controller error-&nbsp;&nbsp;Subsystem Group 1 Error : OSC Error : 0x2 : 0x1e : 0x1 : 0x0.</span><div><font color="#222222" face="Times New Roman, serif"><span style="font-size:13.3333px;">Controllers are healthy after clear load but not able to get triggered event data.&nbsp;</span></font></div> | 6 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | Insert New Triggered event Point --&gt; Add&nbsp;Invalid Ovation Point &nbsp;--&gt; Load &amp; Reboot the controller --&gt; Controllers are going into fail mode.<div>Not able to recover the controller even after CLEAR - LOAD operation.</div><div>&nbsp;&nbsp;</div><div><br></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116222
39169 | FINDING | Event Trend: Controller Triggered Event Points are not displayed in correct PANE as per configured in Developer's Studio. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-28 14:59 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-28 14:59 | 76857 |  |  | 2017-07-28 14:59 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 10:17 |  | As per the specification document,&nbsp;Controller Triggered Event Points should be displayed in particular PANE as configured in Developer's Studio. <div>However in Event Trend, all points are in Pane A.</div> <div>&nbsp;</div> <div>Prashant - There are no trendPane and trendQuadrant fields in config XML. If present they should have value one of A, B, C, D.<br></div> <div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software | YJ- Tested on FP03_U2.<div>First 10 points are displaying in correct PANE as configured but rest of the points are plotting in PANE A.</div><div>YJ: Tested for Patch OPH360005 on Non Ovation machine. Issue is fixed.</div><div>Tested in FP03_U3 on CARL network. Issue is fixed.<br><div><br></div><div><div><br></div><div><br></div></div></div> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | Event Trend Application<div>OVA360FP2_U4<br></div> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 11 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Configure Event Points with PANE B,C and D in developer studio --&gt; Triggered the Event --&gt; Launch the triggered Event in Event Trend --&gt; Points are in PANE a Only,&nbsp; |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116717
39170 | FINDING | DEC - DEC Oscillography triggering of two events simultaneously causes errors and stops future events | Wimer, Walter L EMR SYSS PWS PITT | Released to Library | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Wimer, Walter L EMR SYSS PWS PITT | 2018-09-13 09:27 | [11 empty] | Wimer, Walter L EMR SYSS PWS PITT | 2018-09-13 09:27 | 87813 | [6 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 10:44 |  | <p>Triggering one event and then triggering another shortly after (while first is still collecting), causes error messages and the transfer of the second file is stuck in&nbsp;a loop and continously keeps transferring over and over.&nbsp; Both initial&nbsp;buffers make it to the scanner and to the OPH.&nbsp; Triggering another event does not work after this occurence.&nbsp; Refer to attached file.&nbsp; The first section shows the events and the error occuring. The second section shows the transfer completes.&nbsp; The third section shows the buffer keeps transferring</p><p>The module is reporting:</p><p>dlcapture_notify_ovation_controller: Controller response to request: ERROR -2<br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wimer, Walter L EMR SYSS PWS PITT | Jain, Yukta AUTOSOL PWS NOIDA | [8 empty] | Implementation | OVA360077 |  | Ovation 3.6.0 + FP2 U4 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Released to Library | 1 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | See SDR 42371:&nbsp;<a href="https://uspit-tfs-v.emrsn.org/tfs/Quality/SDR/_workitems/edit/42371" aria-label="CTRL+Click or CTRL+Enter to follow link https://uspit-tfs-v.emrsn.org/tfs/Quality/SDR/_workitems/edit/42371">https://uspit-tfs-v.emrsn.org/tfs/Quality/SDR/_workitems/edit/42371</a><div><br></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Trigger two simulatenous events. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 131864
39173 | FINDING | DEC - DEC Oscillography buffer enabling/disabling will not stay set if it is changed via Engineering tool. | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:15 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:15 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 13:56 |  | <p>From the Engineering tool of the DEC module, if you create a new buffer configuration, enable it and save the configuration.&nbsp; The enable does not stay.&nbsp; Opening the engineering tool again shows it is not enabled.&nbsp;&nbsp; Disabling the default buffers (currently enabled), saving and reengineering shows the same, it does not stay as set.</p><p><br></p><p>This can be remedied by modifying the 'active' flag to a 0 or 1 in the xml file itself. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0 + FP2 U4 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Try to disable one of the default buffer configuration through the DEC engineering tool |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116947
39174 | FINDING | DEC - DEC Oscillography configuration files are not getting to module currently | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-12 14:50 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-12 14:50 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 15:25 |  | <p>The DEC oscillography configuration xml files are not getting to the module.&nbsp; The DEC module record must be modified (tickled) to enable the transfer of the file from the controller to the module.&nbsp; This is currently not being done.&nbsp; If you manually modify the DEC module record and the configuration, and load the controllers, the file will appear in the primary module.&nbsp; I have not been able to get the configuration file to the secondary module, even with modifying it's module record and the configuration.&nbsp;</p><p><br></p><p>The configuration files are not currently used, so this won't affect operation.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Swartz, Mark EMR SYSS PWS PITT | Patel, Sunil EMR SYSS PWS PITT | [8 empty] | Implementation |  |  | 3.6.0 + FP2 U4 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  | <p>This issue has two parts:</p><p>(1) Modification of the DEC Oscillography configuration must also modify the module's associated RM point such that the point will be updated in the controller during the next load.&nbsp; This (as described above) is sufficient for the software in the controller to copy the file to the module.&nbsp; This portion is development complete and will be included in OVA360FP3.</p><p>(2) For redundant configurations, the DEC Oscillography configuration must also be copied to the partner DEC module.&nbsp; This may be similar to the functionality used to get configuration files to partner modules in redundant Profibus and ELC busmodules.&nbsp; This portion of the issue is likely controller (or controller driver) software functionality.</p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Modify the DEC Oscillography buffer configuration.&nbsp; Load the controller.&nbsp; Check the file in the module to see that it does not exist or if so, the modification is not present. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 112745
39175 | FINDING | DEC - DEC Oscillography configuration of the sampling frequency should be limited as defined in functional spec. | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:14 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:14 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 15:30 |  | <p>On the engineering tool for the DEC Oscillography buffers, the sampling frequency should be limited to the defined allowable frequencies in the spec. Currently any number can be entered. </p><p>The configuration files are not currently used, so this won't affect operation.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>3.6.0 + FP2 U4</p> |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use DEC engineering tool and modify to frequency to any number. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116945
39176 | FINDING | DEC - DEC Oscillography configuration should limit trigger position to 0 to 100 as it is a percentage | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:15 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:15 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 15:34 |  | <p>On the DEC engineering tool, the trigger position should be limited to 0 through 100 as it is a percentage.&nbsp; Currently numbers outside of this range can be configured. Perhaps an indication of percentage (%) can be displayed on the screen as well. </p><p><br></p><p>The configuration files are not currently used, so this won't affect operation.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>3.6.0 + FP2 U4</p> |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use DEC engineering tool to modify the trigger position.&nbsp; |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116946
39177 | FINDING | DEC - DEC Oscillography configuration file is not removed on a drop clear. | Silvaggio, Gregory W EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wimer, Walter L EMR SYSS PWS PITT | 2017-05-02 10:54 | [11 empty] | Wimer, Walter L EMR SYSS PWS PITT | 2017-05-02 10:54 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-04-27 16:01 |  | The DEC oscillography configuration file is sent to the controller on a load operation.&nbsp; It should be removed on a clear operation.&nbsp; It currently is not being removed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0 FP2 U4 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Load a&nbsp;DEC Oscillography configuration file to the controller.&nbsp; Verify it exists in the controller.&nbsp; Clear the controller.&nbsp; After reboot, verify file is still there. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 112071
39178 | FINDING | Event Trend: Controller Triggered Event Points are not displayed in trend as per configured in Developer's Studio. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-28 14:59 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-28 14:59 | 77483 |  |  | 2017-07-28 14:59 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 17:23 |  | Controller Triggered Event Points are not displayed in trend as per configured in Developer's Studio. As per the specification document, Event Trend should display only those Triggered Event Points which are configured to display. &nbsp;<div>Snapshot is attached.<div><br></div></div> |  |  |  | <p>Points configured to get displayed will be added to the trend upto a max of 32.</p> <p>&nbsp;</p> <p>If no point is configured for display, first 10 will be added.</p> <p>&nbsp;</p> <p>Retest.</p><p>YJ: Tested for Patch OPH360005 on Non Ovation machine. Issue is fixed.<br></p><p>Tested in FP03_U3 on CARL network. Issue is fixed.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Hatok, Alan M AUTOSOL PWS PITT | [9 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>A Refresh button is now provided to refresh event files and refresh the event trend.</p><p><br></p><p>YJ: Refresh Button is working but still triggered Event Points are not displayed correctly in trend (as per configured in Developer's Studio).</p><p><br></p><p>YJ: Retested in&nbsp;FP03_U2+OPH360005.</p><p>Trend always has first 10 points on launch and configuration is applicable to first 10 points only.&nbsp;</p><p>Trend should plot all the points which are configured to show up on launch.</p><p><br></p><p><br></p><div><br></div> | 15 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116718
39179 | FINDING | Controller Triggered Event: Newly inserted points in existing Triggered Event configuration are not updating in Event Trend. No Information is available after trigger. | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:13 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:13 | 76999 |  |  | 2017-07-19 16:13 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-04-27 17:45 |  | New points inserted&nbsp;in existing Triggered Event configuration is not updating in Event Trend. No information is visible/updating in Event trend after Trigger.&nbsp;<div>Newly added points are visible after a couple of Clear &amp; Load operation.</div> |  |  |  |  | 0 |  |  |  | <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">YJ:&nbsp;Issue Re-tested on Drop250 CARL network having Ov360 FP03_U2+OPH360005&nbsp;and is fixed</span> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Insert New Event Point --&gt; Load the controller --&gt; Trigger the event --&gt;No Information is available for newly added points in Event Trend.<div><br><div><br></div></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116216
39180 | FINDING | Descrepency of Macro parameter in online help and the right click menu has to be corrected in control buikder help. | Aditya, Abhinav AUTOSOL PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-07-17 05:45 | [11 empty] | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-07-17 05:45 | 76415 |  |  | 2017-07-17 05:45 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-04-28 00:39 |  | <p>While&nbsp;defining new &nbsp;macro in the control builder, after inserting the algorithm-&gt;select the algorithm-&gt;right click, select Add Parameter interface for defining parameter interface.</p><p>In the online help of control builder, under the section of &quot;To define a macro in the control builder&quot;, point 6.a describes this step.</p><p>In the manual it is described as &quot;Add Macro Parameter&quot;&nbsp; instead of &quot;Add&nbsp; parameter Interface&quot; in&nbsp; menu.</p><p>This word in online help has to be corrected.</p><p>Please find attached the snapshots for reference.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Documentation | <p><br></p><p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p><p>The updated manual is kept at:</p><p><a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p><p>Tested in build </p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p><p><br></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OV360FP3U1 |  | Online help of all EWS stations . |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  | <p>AA (04-28-17): Reassigning this finding to Linda, since, I am not responsible for the Control Builder online help nor the pdf for FP2 release.</p><p>Linda, kindly, look at the finding and re-assign to the correct person.</p><p><br></p><p><br></p><p><strong><br></strong></p><p>AA (06-07-2017): The issue has been fixed in the Control Builder manual and online help.</p><p>The updated manual (OW360_80V2) is kept at:</p><p><a href="file://\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals">\\Uspit-fp04\val\Tests\3.6.0\FP3\User_Manuals</a></p><p><br></p><p>&nbsp;TN-07-17-17:</p><p>Tested on U2 build &amp; verified the online help.</p><p>The issue is fixed. Thus closing the finding.</p><p><br></p><p><br></p> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p>Open a control sheet. file-&gt;new-&gt;control macro. add the selected algorithm. right click-&gt;select Add Parameter interface.</p><p>In the online help, the step is described as &quot;Add Macro Parameter.&quot;</p> |  | fp2 |  |  | FINDING | [6 empty] | 116030
39192 | FINDING | DEC - DEC Oscillography configuration does not limit the number of variables that can be added. | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 15:10 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 15:10 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-02 10:29 |  | The DEC Oscillography configuration should have a maximum number of variables that can be added (FS).&nbsp;&nbsp; Currently this is not limited.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>3.6.0 + FP2 U4</p> |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Add variables to a DEC Oscillography configuration and verify there is no limit. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116950
39193 | FINDING | Event Trend: "Duration filter" in Time Span filter criteria is not displaying correct Event Records. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:29 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:29 |  |  |  | 2017-06-15 13:29 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-02 10:58 |  | Duration filter&nbsp;&nbsp;(along with Start and End time filter)&nbsp;is not showing correct Event Records.<div>It is always displaying last Start &amp; End time filter criteria&nbsp;result. &nbsp;</div><div><br></div><div><div><br></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP02_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03.<br></div><div>DURATION FILTER REMOVED.</div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Use &quot;Start or End Time &amp; Duration&quot; filter criteria together in Browse Event window .<div><br><div>In Snapshot- Firstly Events were searched for past 24 months and then for 33.3 days duration (with end time - CT) but result is still displaying result for 24 month. In same way, Use any duration and result will always be displayed for 24 months.</div><div>Combination of Start time &amp; Duration filter are behaving same way.</div><div><br></div></div> |  | OVA360FP02_U4 |  |  | FINDING | [6 empty] | 114363
39194 | FINDING | Event Trend: 'OK' button in Event type filter criteria should be greyed out if no event type is selected. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Bargaje, Prashant C EMR SYSS PWS PITT | 2017-05-10 08:04 | [11 empty] | Bargaje, Prashant C EMR SYSS PWS PITT | 2017-05-10 08:04 |  |  |  | 2017-05-10 08:04 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-02 11:06 |  | 'OK' button in Event type filter criteria should be greyed out if no event type is selected. However button is working fine. If there is no selection then it is by default selecting both Event types.<div>For example- 'OK' button in Historian filter criteria is working as expected, OK button is greyed out if no Historian is selected.<br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OVA360FP02_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Works as Designed (Explanation given) | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>For Hisorians, it is logical to select a particular historian or more than one if necessary. In practical scenario, it will be usually one. So user has to be forced to select explicitly.</p> <p>&nbsp;</p> <p>For Event Types, the default is * means all event types. So if user does not select any, it means select all.</p> | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Event Trent --&gt; Event Browser --&gt; Event Type filter --&gt; Clear all selection --&gt; 'OK' button is enable. |  | OVA360FP02_U4 |  |  | FINDING | [6 empty] | 112581
39195 | FINDING | Event trend: 'Network/Unit' filter is not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 |  |  |  | 2017-06-15 13:30 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-02 11:15 |  | 'Network/Unit' filter is not working.<div>initially it seems to be a cosmetic problem and Finding 39099 has details of it, but on investigation I found out that it is not working at all.</div><div>i have updated <a href="https://uspit-tfs-v.emrsn.org/tfs/Quality/FINDING/_workitems/edit/39099" class=caption style="box-sizing:border-box;color:rgb(0, 122, 204);cursor:pointer;font-family:&quot;Segoe UI Light&quot;, &quot;Segoe UI&quot;, Tahoma, Arial, Verdana;font-size:18px;white-space:nowrap;">FINDING 39099</a>&nbsp;.&nbsp;</div><div><div><br></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP02_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed.<div><br></div><div>YJ: Retested in OVA360022. Not fixed.</div><div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03.<br></div> | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Event Trend Browser. |  | OVA360FP02_U4 |  |  | FINDING | [6 empty] | 114365
39196 | FINDING | Event trend: 'Source Drop' filter criteria is not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 |  |  |  | 2017-06-15 13:30 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-02 11:20 |  | 'Source Drop' filter criteria is not working.<div>Can not filter the event based on Source Drop and there is no Source drop column in Event record result.</div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP02_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed. <div>YJ: Retested in OVA360022. Not fixed. Only working when all drops are selected.<br></div> <div>Make sure that latest OPH360003 is installed on OPH server.</div><div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Event Trend Browser --&gt; Select Drop in Source Drop filter --&gt; No filtering based on drop. |  | OVA360FP02_U4 |  |  | FINDING | [6 empty] | 114366
39199 | FINDING | DEC - DEC Oscillography configuration tool is not parsing the event trigger for validity. | Patel, Sunil EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Wimer, Walter L EMR SYSS PWS PITT | 2017-05-02 13:09 | [11 empty] | Wimer, Walter L EMR SYSS PWS PITT | 2017-05-02 13:09 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-02 13:05 |  | The DEC Oscillography configuration tool should be parsing the event trigger for valid expressions and reporting an error of invalid.&nbsp; This does not appear to be implemented as an invalid expression is able to be saved.<div><br></div><div>(This is a known issue. &nbsp;The plan is to fix it in OVA360FP3.)</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | 3.6.0 + FP2 U4 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use DEC Oscillography configuration tool to enter an invalid trigger expression and save the configuration. Note that no error is reported. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 112104
39205 | FINDING | Safety Shell- Ovation System Viewer- Drop Fault Report does not show expected fault parameters detail for safety shell fault alarm. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 08:10 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 08:10 | 75861, 76707 |  |  | 2017-07-10 03:39 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-03 01:30 |  | <font face="Times New Roman" size=3><p><font face=Arial>In system viewer -Ovation Drop Fault Report,&nbsp;incomplete information available for&nbsp;safety shell fault alarm.</font></p><p> <font face=Arial>Following information available in System viewer -Ovation Drop Fault Report:</font></p><p> For Fault Parameter 1: Description not available (only text available)</p><ol type=1 style="margin-top:0in;" start=1> <li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;">For Fault Parameter 2: Description not available (only text available)</li> <li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;">For Fault Parameter 3: Description and text not available</li> <li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;">For Fault Parameter 4: Description and text not available. </li> <li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;font-style:normal;font-weight:normal;">&nbsp;</li> </ol><p> <font face=Arial>Verified the above observation for all type of safety shell fault alarm scenario:&nbsp;Invalid Source, Repeated Sequence, Out of Sequence Fault, Invalid CRC and Delayed DDB fault.</font></p><p> <font face=Arial>Screenshot is attached for reference.</font></p><p> <br></p></font><p><br></p><span style="color:windowtext;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><p><br></p><p style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><br></p><p style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><font face="Times New Roman" size=3> <br></font></p></span><p style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  | follow the steps to reproduce.&nbsp;&nbsp; fault code 4 not displaying is an issue with a support file not having the information. this may or may not have been fixed when this test is run. | 0 |  |  |  | <p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">VP-08/10- Retested the issue&nbsp;in regression test cycle. system is loaded with &nbsp;OVA360FP3_U4</span></p><p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Verified&nbsp;for <span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Fault parameter 1, <span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Fault parameter </span>2, <span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Fault parameter </span>3 and <span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Fault parameter 4 that&nbsp;<br><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Ovation system viewer- drop fault report display detail description and text&nbsp;for </span><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">Fault parameters</span><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;">.</span></span></span></span></span></span></p><p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><br></span></p> | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Costlow, Kim EMR SYSS PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Burgoon, Frank AUTOSOL PWS PITT | Sharma, Satish AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Lupu, Mircea F AUTOSOL PWS PITT |  |  | Implementation | OVA360FP3_U0,OVA351128, OVA360FP3_U2 |  | <p>OV360FP2_U4</p><p><br></p> |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Steps performed: </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Using error Injection tool, generate&nbsp;Repeated Sequence Fault Alarm</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Verified result in System viewer.</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Expected fault code for repeated sequence fault: Fault code = 66, fault ID = 9, fault parameter 1= 0x0C (12), FP2= 1 (indicate Safety shell fault), FP3=2 (Indicate Repeated sequence fault), </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial><span style=""><font size=3>&nbsp;</font></span><font size=3>FP4= 102 (Indicate DDB Originating drop).</font></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><font face=Arial size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Observed result in&nbsp;System Viewer, </font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Upon Clicking Fault Id, Ovation Drop Fault Report appears where only detail of Fault code and Fault Id appear, there is</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Fault&nbsp;Code&nbsp;:66;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Fault Code: 9;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in -9pt 0pt 0in;"><font face=Arial size=3>Fault Parameter 1: Value 12 (0x00C): Refer to&nbsp;fault parameter 2,3 and 4 to find the specific fault;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Fault Parameter 2:&nbsp;Value 1 (0x0001): Refer to&nbsp;fault parameter 3 and 4 to find the specific fault;&nbsp;&nbsp;&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Fault Parameter 3 detail not available;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><font face=Arial size=3>Fault Parameter 4 detail not available.</font></p><font face="Times New Roman" size=3> </font> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 117179
39207 | FINDING | Safety Shell- Safety shell fault limit parameters of SS_Status algorithm accept less than zero value. | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 00:19 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-09 00:19 | 75704 |  |  | 2017-06-13 21:45 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-03 02:23 |  | <p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>For&nbsp;algorithm SS_Status, observed that safety shell fault limit parameters accept less than zero value. </font></span></p><p><font face=Calibri size=3>These Parameters&nbsp;<span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"> should not accept as minimum value for the parameter is 0.</span></font></p><p><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><br></span></font></p><p><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Verified&nbsp;that issue mentioned (Parameters accept less than zero value )&nbsp;for all type of Safety shell fault limit parameters.</span></font></p><p><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Safety shell fault limit parameters are:</span></font></p><p><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><strong>BSFL:</strong> <span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">Bad source fault limit;</span></span></font></p><p><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"></span></span></font><font face=Calibri size=3><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">RSFL: Repeated sequence fault limit;</span></span></font></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">OSFL: Out of sequence fault limit;</span></font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">BCFL: Bad checksum fault limit;</span></span></font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;"><span style="line-height:107%;font-family:&quot;Times New Roman&quot;,serif;font-size:11pt;">DDFL: Delayed DDB fault limit.</span></span></span></font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><br></font><font size=3> Note: </font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>After loading of controller with above control (Fault limit parameters configured with less than zero value), verified in signal diagram that these negative value (less than zero) </font></span></p><p><font face="Times New Roman" size=3> </font><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>for the parameters treated as zero. </font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><font face="Times New Roman" size=3> <span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>In signal diagram, verified that Fault limit tuning parameters not accept less than zero value (minimum zero value), works as expected. </font></span></font></span></font></p><p><font face="Times New Roman" size=3><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="font-family:&quot;Calibri&quot;,sans-serif;"><br></span></font></span></font></p><p><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Screenshots&nbsp;of &nbsp;observations are attached.</span><br></p><p><br></p><p><br></p><p><br></p><p><br></p> |  |  |  |  | 0 |  |  |  | <p>08/09/2017&gt;Retested&nbsp;for Regression testing.<br>Final build FP3_U4 loaded on system.&nbsp;</p><p>Verified that safety shell fault limit parameters of <strong>SS_Status</strong> algorithm not accept less than zero value.<br>Minimum value 0 for fault limit parameters .</p><p>Following parameters verified<br>BSFL: Bad source fault limit; <br>RSFL: Repeated sequence fault limit;<br>OSFL: Out of sequence fault limit;<br>BCFL: Bad checksum fault limit;<br>DDFL: Delayed DDB fault limit.</p> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lupu, Mircea F AUTOSOL PWS PITT | Long, Michelle J External Artech | Capani, Innocenzo AUTOSOL PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Sharma, Satish AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW |  |  |  | Implementation | OVA360FP3 |  | OVA360FP2 |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p><br></p> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>In Control builder- created a control using SS_Status algorithm, observed that safety shell fault limit tuning parameters accept less than zero value. <br></font><font size=3> </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><br></font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Load&nbsp;the controller with above controls (Fault limit parameters configured with less than zero value), verified in signal diagram that these negative value (less than zero) </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>for the parameters treated as zero. </font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><br></font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="line-height:105%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">In signal diagram, verified that Fault limit tuning parameters not accept less than zero value (minimum zero value). works as expected. </span></font></span></p><font face="Times New Roman" size=3> </font> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 117117
39208 | FINDING | Safety shell-Fault Parameter 3 [FG] field not updated with expected value for safety shell fault scenario. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 08:01 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-10 08:01 | 75669 |  |  | 2017-06-13 22:41 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-03 03:20 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>In Point Info-Fault Parameter 3 </font></span><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>[<span style="">FG</span></font><font size=3>] field not updated with expected value for safety shell fault scenario.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><br></font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Fault scenarios are: Invalid Source, repeated sequence, Out of sequence Invalid CRC, Delayed ddb</font></span></p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><ul><li><div style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:12pt;">For&nbsp;Invalid Source fault, FP3 updated with value unknown value <b>6684673</b> instead of expected value <b>1</b></span><font face="Times New Roman"></font><font face="Times New Roman"> </font></div></li><li style="margin:0in 0in 0pt;color:black;line-height:18pt;font-size:11pt;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">For repeated sequence fault, FP3 updated with value unknown value <b>6684674</b> instead of expected value <b>2</b></span></li><font face="Times New Roman"></font><li style="margin:0in 0in 0pt;color:black;line-height:18pt;font-size:11pt;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">For out of sequence fault, FP3 updated with unknown value <b>6684675</b> instead of expected value <b>3</b></span></li><font face="Times New Roman"></font><li style="margin:0in 0in 0pt;color:black;line-height:18pt;font-size:11pt;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">For invalid CRC fault, FP3 updated with unknown value <b>6684676</b> instead of expected value <b>4</b></span></li><font face="Times New Roman"></font><li style="margin:0in 0in 0pt;color:black;line-height:18pt;font-size:11pt;font-style:normal;font-weight:normal;"><span style="font-family:&quot;Calibri&quot;,sans-serif;">For delayed ddb fault, FP3 updated with unknown value <b>6684677</b> instead of expected value <b>5</b></span></li></ul><font size=3><p style="margin:0in 0in 0pt;">Point Info only reports what is in point record. This is a controller issue.</p><p style="margin:0in 0in 0pt;"><br></p><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:12pt;"><p style="margin:0in 0in 0pt;"><br></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"><br></font></p></span><p style="margin:0in 0in 0pt;"><br></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:12pt;"><br></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><b><br></b></span></p><font face="Times New Roman"> </font><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 0pt;"><br></p></span><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><br></font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><font color="#666666">VP-08/10- Retested the issue with regression test cycle. system is loaded with &nbsp;OVA360FP3_U4. </font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><font color="#666666">Verified that Fault parameter 3 [FG] field is updated with expected value for Safety shell faults.</font></span></p><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><font color="#666666">Following are&nbsp;verified&nbsp;scenario with results.</font></span></p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:10pt;"><font color="#666666"><p>Scenario-1: Injected repeated sequence more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):2, FH(FP4):102,&nbsp; <br></p><p>Scenario-2: Injected Out of sequence/less than error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):3, FH(FP4):102,&nbsp; <br></p><p>Scenario-3:Injected Invalid source error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):1, FH(FP4):102,<br></p><p>Scenario-4: Injected CRC error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):4, FH(FP4):102,<br></p><p>Scenario-5: Injected Delayed ddb error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):5, FH(FP4):102<br></p></font><p style="margin:0in 0in 0pt;"><br></p></span><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Long, Michelle J External Artech | Capani, Innocenzo AUTOSOL PWS PITT | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Gupta, Chandresh EMR SYSS PWS NOIDA |  |  |  | Implementation | OVA360FP3 |  | OVA360+FP2_U4 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 10 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Steps:&nbsp;</font></span><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Using Error Injection tool, generated Repeated Sequence Fault. </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Verified receiving drop go in Alarm.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Point Information application- open drop point for receiving controller drop.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Observation: FP3 field not updated with expected value i.e. <span style="">2 </span></font><font size=3>for repeated sequence fault scenario. It is updating with unknown value </font><span style=""><font size=3>6684674</font></span></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Following are the expected fault code and parameters for repeated sequence fault </font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>Fault code = 66, fault ID = 9, fault parameter 1= 0x0C (12), FP2= 1 (indicate Safety shell fault),&nbsp;<span style="">FP3=2 (Indicate Repeated sequence fault)</span></font><font size=3>, FP4= 102 (Indicate DDB Originating drop).</font></span></p><font face="Times New Roman" size=3> </font> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 117178
39209 | FINDING | Description for [Fault code: 66, Fault ID: 10, FP1: 7] contains invalid "&amp;apos;s" characters. | Wozniak, Diane M EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-02 05:50 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-08-02 05:50 | 75861 |  |  | 2017-08-02 05:50 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-03 04:14 |  | <p>Perform reboot of controller drop from developer studio. </p><p>In Ovation System Viewer- select and open drop fault report for the rebooted controller&nbsp;drop&nbsp;, Fault Code: 66; Fault ID: 10; Fault Parameter1:&nbsp;&nbsp;7 (0x0007) appear.</p><p>Description for Fault parameter1 appear as&nbsp;&quot;The drop was commanded to reboot from Ovation Developer&amp;amp;apos;s Studio&quot; appeared.</p><p>Observation: description of fault parameter1 contain some invalid characters. &nbsp;</p><p>For reference, screenshot is attached.</p><p><br></p> |  |  |  | See the steps to reproduce | 0 |  |  |  | <p>VP 08/02/17 &gt; Retested finding &nbsp;in FP3_U3.</p><p>Verified that statement does not contain invalid characters.</p><p>&nbsp;in System Viewer statement&nbsp;appear as&nbsp;&quot;The drop was commanded to reboot from Ovation Developer's Studio&quot;.</p><p>Screenshot is attached for reference.</p> | 0 |  | Ovation for Windows/Operator Station/System Viewer/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Kumar, Shailendra EMR SYSS PWS NOIDA | [9 empty] | Implementation | OVA360FP3_U0,OVA351128 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/System Viewer | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>Perform reboot of controller drop from developer studio. </p><p>Open Ovation System Viewer- Open drop fault report for the rebooted controller drop.</p> |  | OV360FP2 |  |  | FINDING | [6 empty] | 116876
39213 | FINDING | Fault parameter values for FP3 and FP4 do not get cleared after acknowledge and cleared controller drop fault alarm. | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-06-14 05:21 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-06-14 05:21 | 75671 |  |  | 2017-06-14 05:21 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-03 10:15 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style="font-size:10pt;"><font face=Arial>Fault parameter values for FP3 and FP4 do not get cleared after acknowledge and cleared controller drop fault alarm.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style="font-size:10pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;line-height:normal;"><span style="font-size:10pt;"><font face=Arial>If user performs acknowledge and clear for Controller drop fault alarms/ safety shell fault alarms from any Ovation application [e.g. Point Information/ Alarm], </font></span></p><p style="margin:0in 0in 0pt;line-height:normal;"><span style="font-size:10pt;"><font face=Arial>it is observed that fault code and parameters <u>FC, FK, FP1, FP2 get cleared</u>, fault parameters <u>FP3 and FP4 not cleared</u> (<u>FP3 and FP4 retain previous value)</u>.</font></span></p><font face="Times New Roman" size=3> </font><ul style="margin-top:0in;"><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);line-height:normal;font-style:normal;font-weight:normal;"><u><span style="font-size:10pt;">FP1, FP2 do get cleared</span></u><span style="font-size:10pt;">, value of the parameters become zero.</span></li><font face="Times New Roman" size=3> </font><li style="margin:0in 0in 0pt;color:rgb(0, 0, 0);line-height:normal;font-style:normal;font-weight:normal;"><u><span style="font-size:10pt;">FP3 and FP4 do not get cleared</span></u><span style="font-size:10pt;">, retain their previous value. </span></li><font face="Times New Roman" size=3> </font></ul><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | <p>VP 06/14/2017&gt; Loaded FP3_U1 on safety shell system.</p><p>Verified Fault parameters status&nbsp;for following safety shell alarm&nbsp;scenario:</p><p>Scenario-1:&nbsp; Injected repeated sequence more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):2, FH(FP4):102,&nbsp; <br>Acknowledged and cleared alarm. All fault parameters (including FP3nd FP4) cleared.</p><p><br></p><p>Scenario-2: Injected Out of sequence/less than error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):3, FH(FP4):102,&nbsp; <br>Acknowledged and cleared alarm. All fault parameters (including FP3nd FP4) cleared.</p><p><br></p><p>Scenario-3: Injected Invalid source error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):1, FH(FP4):102.<br>Acknowledged and cleared alarm. All fault parameters (including FP3nd FP4) cleared.</p><p><br></p><p>Scenario-4: Injected CRC error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):4, FH(FP4):102<br>Acknowledged and cleared alarm. All fault parameters (including FP3nd FP4) cleared.</p><p><br></p><p>Scenario-5: Injected Delayed ddb error more than limit.<br>FC:66, FK:9, FS(FP1):12, FO(FP2):1, FG(FP3):5, FH(FP4):102<br>Acknowledged and cleared alarm. All fault parameters (including FP3nd FP4) cleared.</p><p><br></p><p>FP3 and FP4 get cleared after acknowledge and clear&nbsp;operation of controller drop fault alarm.&nbsp;</p> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Lupu, Mircea F AUTOSOL PWS PITT | Burgoon, Frank AUTOSOL PWS PITT | Long, Michelle J External Artech | Capani, Innocenzo AUTOSOL PWS PITT | Sharma, Satish AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation | OVA360FP3 |  | OVA360+FP2_U4 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <font face=Arial><font size=3><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-size:10pt;">Step-1: </span><span style="line-height:105%;font-size:10pt;">Using error injection tool on EWS drop102, generated repeated sequence fault alarm on receiving controller drop 31/81.Drop31 go in safety shell alarm. <br></span><span style="line-height:105%;font-size:10pt;">Following are the expected fault code for repeated sequence fault.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-size:10pt;">Fault code = 66, fault ID = 9, fault parameter 1= 0x0C (12), FP2= 1 (indicate Safety shell fault), FP3= 2 (Indicate Repeated sequence fault), FP4= 102 (Indicate DDB Originating drop).</span></p><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-size:10pt;"><br></span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-size:10pt;">Step-2: </span><span style="line-height:105%;font-size:10pt;">Performed Acknowledge and Clear of Controller drop Fault alarm on drop31.</span></p><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-size:10pt;">Observation:</span></p><ul><li><div style="margin:0in 0in 0pt;"><span style="line-height:105%;font-size:10pt;"></span><u><span style="line-height:105%;font-size:10pt;">FC, FK, FP1, FP2 get cleared</span></u><span style="line-height:105%;font-size:10pt;">, value of the parameters become zero.</span></div></li><li><div style="margin:0in 0in 0pt;"><span style="line-height:105%;font-size:10pt;"></span><u><span style="line-height:105%;font-size:10pt;">FP3 and FP4 not cleared (FP3 retains value 2 and FP4 retains value 102)</span></u><span style="line-height:105%;font-size:10pt;">.</span></div></li></ul><p style="margin:0in 0in 0pt;"><font face="Times New Roman"><br></font></p></font><p style="margin:0in 0in 0pt;"><br></p></font><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 114259
39214 | FINDING | Event Trend: "Add All Points" option should be greyed out if there is no point to add. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:30 |  |  |  | 2017-06-15 13:30 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 10:57 |  | &quot;Add All Points&quot; option is active even when there is no point available to add to trend. &nbsp;It should be greyed out as there is nothing to add.<div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Event Trend</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>Fixed.</p> <p>&nbsp;</p> <p>Appropriate message will be displayed.</p><p>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Event Trend Application --&gt; Trend Tab --&gt; Points tab --&gt; Click on Add Button --&gt; &quot;Add all Points&quot; option is active however there not a single point in list to add.<div>&nbsp;</div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114367
39215 | FINDING | Event Trend: 'Add All Points' button is not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 |  |  |  | 2017-06-15 13:31 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 11:01 |  | Event Trend: 'Add All Points' button is not working. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Event Trend</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed.<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <p class=MsoNormal><span style="font-size:10.0pt;">Event Trend Application --&gt; Trend Tab --&gt; Points tab --&gt; Click on Add all Button --&gt; &quot;Add all Points&quot; option is not working.</span></p> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114368
39216 | FINDING | Event Trend: 'Black Background' chart option is not applicable on Event Detail tab. | Kumar, Shailendra EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:46 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:46 |  |  |  | 2017-05-04 09:46 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 11:07 |  | <p>'Black Background' chart option is not applicable on Event Detail tab. Background is not changing to black for&nbsp;&nbsp;Event Detail tab.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Event Trend</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | SVTP/STP | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Reopen finding with Problem type-SVTP.&nbsp;<div>Need to Add this testcase under 5.3.2 SVTP-3.6.0FP2_SRF2242_SVTP_rev1.0_YJ.dox</div> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p class=MsoNormal><span style="font-size:10.0pt;">Event Trend Application --&gt; Format Tab --&gt; Chart Options --&gt; Enable Black background --&gt; changes are not&nbsp;</span>not applicable on Event Detail tab.</p> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116287
39218 | FINDING | Event Trend: 'Delete all' option is not deleting points. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 |  |  |  | 2017-06-15 13:31 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 13:20 |  | Event Trend: 'Delete All points' option is not deleting points. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | <p class=MsoNormal><span style="font-size:10pt;">OVA360FP2_U4</span></p><span style="font-size:10pt;font-family:&quot;Times New Roman&quot;, serif;">Event Trend</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed.<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-size:13.3333px;">Event Trend Application --&gt; Trend Tab --&gt; Points tab --&gt; Click on Delete all point option --&gt; it is not deleting&nbsp;points</span> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114369
39219 | FINDING | Event Trend: Some information is missing in exported pdf file of Event detail tab. | Bargaje, Prashant C EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:45 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:45 | 76922 | [6 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 13:50 |  | Some information is missing in exported pdf file of Event detail tab. All the information in Event Detail tab is not available in exported pdf file.<div>Also, Start &amp; End time information in first two lines of exported pdf file create confusion if export is done when graph is zoomed in.</div><div>&nbsp;See attached PDF &amp; Comments.<br><div><br></div></div> |  |  |  | Retest<div><br></div><div>YJ: Retested in Ov360 FP03_U2+OPH360005. Issue still persist.</div><div>1. DEC Triggered event Export- &nbsp;</div><div>a) Start &amp; End time information in first two lines of exported pdf file has two time stamps when graph is zoomed in. Event detail export file should not displayed zoomed time duration as this is only event detail and there is no graph to refer zoom time.&nbsp;</div><div>b) Trigger information is missing in exported pdf.</div><div>2. Controller Triggered event Export- &nbsp;<br></div><div>a) Start &amp; End time information in first two lines of exported pdf file has two time stamps when graph is zoomed in. Event detail export file should not displayed zoomed time duration as this is only event detail and there is no graph to refer zoom time.&nbsp;<br></div><div>Please refer snapshot.</div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | <p class=MsoNormal><span style="font-size:10pt;">OVA360FP2_U4</span></p><span style="font-size:10pt;font-family:&quot;Times New Roman&quot;, serif;">Event Trend</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 9 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-size:10pt;">Event Trend Application --&gt; Launch Any Event in Trend --&gt; &nbsp;Zoom In Graph --&gt; Go to &nbsp;Event Detail Tab --&gt; Export --&gt; Compare the Event Detail&nbsp;</span>tab in Trend with Exported file.. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116286
39220 | FINDING | Event Trend: "Full Page & Half Page" Next are not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:32 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:32 |  |  |  | 2017-06-15 13:32 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 14:00 |  | &quot;Full Page &amp; Half Page&quot; Next option are not working.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Event Trend.</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Zoom in the graph --&gt; go to Trend Tab --&gt; Try Full page or half page Next button.&nbsp; |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114372
39221 | FINDING | Event Trend: Back Button Options are not working. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:31 |  |  |  | 2017-06-15 13:31 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-03 14:04 |  | <b>Back button options like-&nbsp;</b>&quot;Full Page &amp; Half Page&quot; back option are not working.&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | <table class=MsoNormalTable border=1 cellpadding=0 width="90%" style="width:90.0%;border:solid #F1EFE2 1.0pt;"> <tbody><tr> <td valign=top style="border:solid #F1EFE2 1.0pt;padding:.75pt .75pt .75pt .75pt;"> <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <p class=MsoNormal><span style="font-size:10.0pt;">Event Trend.</span></p> </td> </tr> </tbody></table> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <table class=MsoNormalTable border=1 cellpadding=0 width="90%" style="width:90.0%;border:solid #F1EFE2 1.0pt;"> <tbody><tr> <td valign=top style="border:solid #F1EFE2 1.0pt;padding:.75pt .75pt .75pt .75pt;"> <p class=MsoNormal><span style="font-size:10.0pt;">Event Trend --&gt; Zoom in the graph --&gt; go to Trend Tab --&gt; Try Full page or half page Back Option.&nbsp;</span></p> </td> </tr> </tbody></table> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114371
39226 | FINDING | STABLE97: In STABLE97 algorithm there is discrepancy in the name of units for input/output pressure and atmospheric pressure. | Plamowski, Sebastian EMR SYSS PWS WRSW | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Lal, Ramesh External | 2017-05-16 22:39 | [11 empty] | Lal, Ramesh External | 2017-05-16 22:39 | 75657 |  |  | 2017-05-16 22:39 |  |  |  | Lal, Ramesh External | 2017-05-04 09:21 |  | <p>&nbsp;STABLE97 algorithm symbol there is following discrepancy in the name of units for input pressure/output pressure and atmospheric pressure:</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Pressure input unit: KP/CM2</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Pressure output unit: KP/CM^2</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Atmospheric pressure&nbsp;unit: KP/CM2</p><p>It should be corrected.</p><p>Please refer the attached snapshot.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | APC build U2 |  | <p>DBS Drop100 (Win Server 2012R2), Controller Drop25/Drop75 (OCR1100G01)</p> |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Lal, Ramesh External | Validation |  | 5/17/17: RL - Tested after installation of APC3.6.0 Update 1_U2 build. Unit names are found corrected, hence finding is closed. | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>- Open a control sheet of STABLE97 algorithm in Control Builder or Signal Diagram and click on the STABLE97 symbol.</p><p>- Observe the unit names for input pressure, output pressure, atmospheric pressure.</p> |  | OVA360FP2-U4 |  |  | FINDING | [6 empty] | 112938
39236 | FINDING | Event Trend: 'Processing Type' should not be displayed for Triggered Events. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:32 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:32 |  |  |  | 2017-06-15 13:32 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 10:06 |  | As per the SRF2007, Processing Types should not be supported by Trend for Triggered Events.<div>However&nbsp;'Processing Type' is displayed in 'Details Panel' for Triggered events Variables.</div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Event Trend</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Launch the Controller's Triggered Event in Trend --&gt; Check Details Panel. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114373
39237 | FINDING | Event Trend: End Values are disappearing on adding point in Event Trend. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 13:42 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 13:42 | 76922 |  |  | 2017-07-18 13:42 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 10:43 |  | End Values are disappearing if user adds point by right click menu in Event Trend. |  |  |  | Retest<div><br></div><div>YJ: Fixed.</div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | OVA360FP2_U4<div>Event Trend</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Launch controller Event in Event Trend --&gt; Select any point --&gt; Do Right Click &amp; select 'Trend' &nbsp;--&gt; The point will launch in same Event Trend window but there will be no plot (Point Not Found) --&gt; Observe the end Value for rest of the Event Variables. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116109
39251 | FINDING | OPH is not storing Controller Triggered Event Description. | Silvaggio, Gregory W EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2017-05-15 10:26 | [11 empty] | USPITTFSService | 2017-05-15 10:26 | [7 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 15:03 |  | &nbsp;OPH is not storing Controller Triggered Event Description.<div><br></div><div>Verified in Event Trend &amp; History console.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | FP3 |  | OVA360FP2_U4 +&nbsp;OPH360002 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | 1) To verify in Trend-&nbsp;<div>Browse Controller Event in Event Trend --&gt;Description is missing in Event Records (Refer snapshot- Event Description)</div><div>2) To verify in History Console-</div><div>sql Commend = select * from events;</div><div>&nbsp;Description column is NULL. (Refer snapshot- History Console)</div><div><br></div> |  | FP2 |  |  | FINDING | [6 empty] | 112807
39252 | FINDING | Controller Triggered Events: No Drop Alarm when controller has no connection with scanner drop. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 3 | USPITTFSService | 2017-07-31 16:11 | [11 empty] | USPITTFSService | 2017-07-31 16:11 |  |  |  | 2017-07-31 14:41 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 16:19 |  | As per SRF2242, There should be a Drop Alarm if there is no connection with scanner drop.<div>During testing, no drop alarm has been observed when event is triggered and there is no communication between Event Scanners and Controller. &nbsp;&nbsp;<br><div><br></div></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OVA360FP2_U4<div>Controller Drop- 4/54</div><div>Scanner Drop- 126,127</div><div>Network- Emily</div> |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | More Information Supplied | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Need to modify &nbsp;testcase 5.2.6 of triggered event svtp rev 1.0 to specify the controller drop alarm instead of scanner drop alarm. | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Stop OPH services on Scanner drop 126 &amp; 127 --&gt; trigger Event --&gt; Observe Drop 4.<div>Stop OPH services on Scanner drop 126 &amp; 127 --&gt; trigger Event --&gt; Observe Drop 4 in graphics for any drop alarm and error logs.<br></div><div>Please find the attached snapshot for more detail.</div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116794
39253 | FINDING | Controller Triggered Event: Controller is not sending most recent Event data to OPH scanner upon re-connection. | Hatok, Alan M AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-05-10 06:11 | [11 empty] | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-05-10 06:11 | [7 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 16:29 |  | As per SRF 2242, Controller should send most recent Event data to OPH scanner upon re-connection with scanner.<div><p class=MsoNormal><span style="font-size:10.0pt;">Controller 4/54 did not send most recent triggered event to OPH scanner when scanner brought back to healthy state.&nbsp;</span></p></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <table class=MsoNormalTable border=1 cellpadding=0 width="90%" style="width:90.0%;border:solid #F1EFE2 1.0pt;"> <tbody><tr> <td valign=top style="border:solid #F1EFE2 1.0pt;padding:.75pt .75pt .75pt .75pt;"> <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <p class=MsoNormal><span style="font-size:10.0pt;">Controller Drop- 4/54</span></p> <p class=MsoNormal><span style="font-size:10.0pt;">Scanner Drop- 126,127</span></p> <p class=MsoNormal><span style="font-size:10.0pt;">Network- Emily</span></p> </td> </tr> </tbody></table> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Stop OPH services on Scanner drop 126 &amp; 127 --&gt; trigger Event --&gt; Start OPH&nbsp;</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">services on Scanner drop 126 &amp; 127 --&gt;&nbsp;</span><font face="Times New Roman, serif"><span style="font-size:13.3333px;">&nbsp;Controller is not sending most recent Event data upon re-connection.</span></font> |  | OVA360Fp2_U4 |  |  | FINDING | [6 empty] | 112548
39254 | FINDING | Event Trend is not displaying more then 48 Event Variables for Controller's Triggered Event. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:33 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:33 |  |  |  | 2017-06-15 13:33 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 16:37 |  | Event Trend is not displaying more then 48 Event Variables&nbsp;for Controller's Triggered Event.&nbsp;<div>where maximum number of Event Variable that can be added in triggered event is 50.&nbsp;</div> |  |  |  | Test that no more than&nbsp;32 points can be added to event trend.<div>YJ: Issue fixed AS PER TEST RECOMMENDATION in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p><p class=MsoNormal><span style="font-size:10.0pt;">Event Trend</span></p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Max number that can be added is 32. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Add controller Triggered Event with 50 event variables --&gt; trigger Event --&gt; Browse in Event Trend and observed Event variable tab or add points tab. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114374
39255 | FINDING | Event trend: "Back & Next Page" Buttons are not working in Quick Access Tool Bar. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:33 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:33 |  |  |  | 2017-06-15 13:33 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-05 16:54 |  | &quot;Back &amp; Next Page&quot; Buttons are not working in Quick Access Tool Bar. &nbsp;&nbsp; |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p><p class=MsoNormal><span style="font-size:10.0pt;">Event Trend</span></p> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114375
39265 | FINDING | Event Trend: Packed Point Event variables are not handled properly. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:14 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:14 | 76922 |  |  | 2017-07-18 16:14 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-08 11:18 |  | Packed Point Event variables are not handled properly in event trend Graph view.<div>Graph is turning into blank white screen if a packed Point variable is made visible on graph. It is also blocking display of other event variables.&nbsp;</div><div>&nbsp;</div> |  |  |  | <p>Retest.</p> <p>&nbsp;</p> <p>Also test addition, deletion of packed points. Same packed point with different bitmask is now allowed to be added.</p> | 0 |  |  |  | YJ: LP point is plotted in graph and is not blocking display of other event variables.&nbsp;<div>Retested in Ov360 FP03_U2 on Carl network.</div> | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | OVA360FP2_U4 |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Event Trend --&gt; Browse Controller Event --&gt; Add packed point Event variable in graph (if it is not in first 10 display point)--&gt; Graph is turning into blank white screen blocking display of other event variables. --&gt; Removing the Packed point plot is bring the graph screen back.<div><div><br></div></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116130
39268 | FINDING | Controller Triggered Event: Digital Event variable's data are not available when quality is bad. | Silvaggio, Gregory W EMR SYSS PWS PITT | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 2 | USPITTFSService | 2017-05-11 15:04 | [11 empty] | USPITTFSService | 2017-05-11 15:04 | [7 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-08 16:35 |  | In Controller's Triggered Event, Digital Event variable's data are not available when quality is bad.&nbsp;<div>However can see the point values for same time span in historical review or Hist trend.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | FP3 |  | OVA360FP2_U4 +OPH360002 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Trigger controller Event --&gt; Make sure event has some digital points and quality must be bad --&gt; Observe the Graph in Event trend --&gt; there is no value available for Digital event variables with bad quality.<div><br></div> |  | FP2 |  |  | FINDING | [6 empty] | 112707
39269 | FINDING | Test Case Algorithm Functions Using Graphics: some tests are NA as no option for digital BIAS entry is available in custom graphics. | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-05-09 03:29 | [11 empty] | USPITTFSService | 2017-05-09 03:29 | [7 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-05-09 03:18 |  | <p>In TR <span style="font-family:&quot;Arial&quot;,sans-serif;font-size:9pt;-ms-layout-grid-mode:line;">3.6.0FP2_U3_BASIC_FUNCTIONS_SVTP_rev1.R_HS, t</span><font face="Times New Roman" size=3>es</font>t case 5.3: <a name=_Toc285105671><span style="font-family:&quot;Times New Roman&quot;,serif;font-size:10pt;">Algorithm Functions Using Graphics</span></a>&nbsp;contain sub test 5.3.1. In this sub test&nbsp;for algorithms MASTATION and XMA2&nbsp; test case for bias input cannot be tested as bias entry option is not available in custom graphics so marked these tests as NA.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Kumar, Shailendra EMR SYSS PWS NOIDA | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 112430
39273 | FINDING | Event Trend: "Triggered Events" check box option under "Visibility" section is not working properly. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 |  |  |  | 2017-06-15 13:34 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 10:42 |  | &quot;Triggered Events&quot; check box option under &quot;Visibility&quot; section is not working properly.<div>In Live trend- It is not enabling display of Event Marker on Graph when 'Checked'.</div><div>In Historical trend- It is not disabling display of Event Marker on Graph when 'Un-checked'.<br></div><div>In Event trend- It is not disabling display of Event Marker on Graph when 'Un-checked'.<br></div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Event Trend, Controller Events</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Fixed<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Trigger Controller Event --&gt; Launch it in Event trend --&gt; Go to Format tab --&gt; Visibility section --&gt; Check &amp; Un-check&nbsp;&quot;Triggered Events&quot; . |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114376
39274 | FINDING | Event Trend: Point Graph is not changing colour for Non-good Quality. | Hatok, Alan M AUTOSOL PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:45 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:45 | 76922 | [6 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 10:50 |  | Point Graph is not changing colour for Non-good Quality Event Variables of Controller Triggered Events. |  |  |  | Retest | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Event Trend, Controller Events</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">Change the quality of controller's triggered event </span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:13.3333px;">variable</span><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">/variables to bad --&gt; Trigger Event --&gt; Launch it in Event trend --&gt; Observe the Graph, Color of non-good quality points is not changing.</span> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116285
39275 | FINDING | Event Trend: Event Marker is not visible in all PANEs. | Kumar, Shailendra EMR SYSS PWS NOIDA | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:53 | [11 empty] | Contento, James AUTOSOL PWS PITT | 2017-07-20 13:53 |  |  |  | 2017-05-10 07:58 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 10:54 |  | Event Marker is not visible in all panes. It is only marked in PANE A. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | <p class=MsoNormal><span style="font-size:10.0pt;">OVA360FP2_U4</span></p> <span style="font-size:10.0pt;font-family:&quot;Times New Roman&quot;,serif;">Event Trend, Controller Events</span> |  | Ovation for Windows | Ovation | Operator Station/Trend | SVTP/STP | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | The Event Markers are displayed only in Pane A, to reduce clutter.<div><br></div><div>YJ: Need to modify testcase 5.3.2 (i) to add this information.</div><div>Event Markers are displayed only in Pane A however&nbsp;<span style="font-family:Calibri, sans-serif;font-size:11pt;">if no point to display in PANE A then there is no event marker at all in the Graph. &nbsp;So&nbsp;</span><span style="font-family:Calibri, sans-serif;font-size:11pt;">If Pane A is not there, user needs to move some points to it.</span></div><p class=MsoNormal><span style="font-size:11.0pt;font-family:&quot;Calibri&quot;,sans-serif;"></span></p><div><br></div> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Refer the attached snapshot. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116288
39276 | FINDING | Event Trend: User should not be able to launch the Triggered Events if Events are not Enabled in Trend option. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 |  |  |  | 2017-06-15 13:34 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 11:06 |  | User should not be able to launch the Triggered Events from Event Browser if Events are not Enabled in Trend option. &nbsp;<div>As per the SRF, user can open the saved Event in Trend when Events are not Enabled in Trend option but after doing it, Event browser button is available to access other past events.</div><div>Event browser button should be greyed out if Events are not Enabled in Trend option.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Event Trend</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Event Browse button will be diabled, if Event Trending is not enabled.<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div> | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114377
39277 | FINDING | Digital Points are not updating quality in Front display Bar. | Augustine, Lisa EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:11 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:11 | 76545 |  |  | 2017-07-18 16:11 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 14:23 |  | Digital Points are not updating quality in Front display Bar of Point information application.<div>Refer snapshot for more detail.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Point Information/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3_U2 |  | OVA360FP2_U4<div>Point information Application</div> |  | Ovation for Windows | Ovation | Operator Station/Point Information | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Follow these steps to recreate the issue-<div>Open Multiple points in PI (atleast 1 digital point) --&gt; Change the quality of one of the digital point in the list --&gt; Quality displays for the first time user load the digital point --&gt; Load some other point from the list --&gt; Now Re-load the same digital point (with bad quality) from the list--&gt; Quality disappears from PI&nbsp;Front display Bar.&nbsp;</div><div>Please refer attached snapshot.</div><div><br></div><div>YJ: Retested. Issue is fixed in Ov360 FP03_U2.<br><div><br></div></div> |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116129
39279 | FINDING | Event Trend: Time axis markings are missing in Zoomed in Graph. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:34 |  |  |  | 2017-06-15 13:34 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-09 16:03 |  | Time axis markings are missing in Zoomed in Graph.<div>Time axis markings are visible for only current display graph. &nbsp;Refer snapshot for more details.<br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA360FP2_U4<div>Controller's Triggered Events</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | Could not duplicate.&nbsp; Please retest.<div><br></div><div><div>Please follow Steps to reproduce. &nbsp;Able to recreated on Drop127.</div></div><div>Issue is not always existing but &nbsp;can be seen after multiple zoom.</div><div>please see the attached snapshot &amp; exported trend.</div><div><br></div><div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03<br></div><div><br><div><br></div><div><br></div></div> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Launch Controller Triggered Event --&gt; Zoom in time axis --&gt; Move the scroll bar --&gt; Axis markings are missing. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 114378
39288 | FINDING | Safety Shell Testing Tool document "SRF 2228 Safety Shell Testing Tool Rev 1 "needs to be revised with additional steps for User permission in the section “Installation of Custom Windows DDB Driver”. | Burgoon, Frank AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-23 05:57 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-23 05:57 |  |  |  | 2017-05-23 05:57 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-10 08:46 |  | <p><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>Safety Shell Testing Tool provided by development for Validation Testing.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>Safety Shell Testing Tool Revision 1 document contains detail of Installation instructions for Safety Shell Test Tool.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>On Validation setup installation steps for testing tool were&nbsp;performed.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>During Installation of Testing Tool on Validation setup, issue for downloading of&nbsp;EWS drop was observed.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>As per development recommendations, validation performed following&nbsp;additional steps&nbsp;&nbsp;</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>Open registry editor (regedit)</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><ul style="list-style-type:disc;direction:ltr;"><li style="font-style:normal;font-weight:normal;"><p style="font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Navigate to <a href="file://hkey_local_machine/SYSTEM/CurrentControlSet/Services/DDB/Parameters"><font color="#0563c1">\\HKEY_LOCAL_MACHINE\SYSTEM\CurrentControlSet\Services\DDB\Parameters</font></a></span></p></li><li style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Right click on the “Parameters” subkey in the tree on the left.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Select “Permissions…”</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Highlight “Users” in the “Group or user names:” list box. If “Users” does not appear click the “Add…” button and add “Users”.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">In the “Permissions for Authenticated Users” list box click the “Full Control” checkbox in the “Allow” column to give “Users” full control permissions.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Click the “OK” button.</span></p></li></ul><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>After performing above additional steps EWS drop download issue got resolved.</font></span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>&nbsp;Safety Shell Testing Tool document&nbsp;needs to be enhanced&nbsp;by adding above steps in&nbsp;the section “<b>Installation of Custom Windows DDB Driver”</b><span style="">. </span></font></span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  | <p>VP&gt;05/23: <br>Verified that Revision 2 of document placed into Safety Shell area of Product Development sharepoint site.</p><p>Rev2 document updated with additional steps mentioned in the description field.</p><p>Hence finding is closed.</p> | 0 |  | Ovation for Windows/Engineering Tools/General/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Burgoon, Frank AUTOSOL PWS PITT | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Gupta, Chandresh EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA |  |  |  |  | Implementation |  |  | <p>OVA360FP2</p><p>EWS drop102</p> |  | Ovation for Windows | Ovation | Engineering Tools/General | Documentation | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Revision 2 of document placed into Safety Shell area of Product Development sharepoint site | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p><u>Refer Safety Shell Testing Tool document &quot;SRF 2228 Safety Shell Testing Tool Rev 1</u></p><p><u>Perform Installation of Safety Shell testing Tool.</u></p><p><u>Download EWS drop on which Tool installed.</u></p><p><u>Drop can not be downloaded.</u></p> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 113182
39292 | FINDING | Event scanner is not recording Controller Triggered event variables' quality. | Hatok, Alan M AUTOSOL PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:22 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-18 16:22 | 76857 | [6 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-10 15:18 |  | Event scanner is not recording Controller Triggered event variables' quality.&nbsp;<div>Can not see quality of Event point in Event Trend.</div> |  |  |  |  | 0 |  |  |  | YJ: Retested on CARL Network Ov360 FP03_U2. Issue still persist.<div>Tested LA, LD, DA and DD point. BAd Quality is not recorded. &nbsp;</div><div><div><br></div></div> | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | OPH360002 + OVA360FP2_U4<div>Event trend application</div><div>Event type- Controller Triggered events&nbsp;</div> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Failed Retest | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 8 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Change the quality of Event variables to BAD --&gt; Triggered the controller event --&gt; Launch the event in Trend --&gt; There is no information about quality.<div><br></div> |  | FP2 |  |  | FINDING | [6 empty] | 116135
39293 | FINDING | STABLE97: Test procedure SRF2229_STABLE97_SVTP_rev1.1 for steam table needs corrections for units of enthalpy and entropy. | Lal, Ramesh External | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Lal, Ramesh External | 2017-05-29 04:40 | [11 empty] | Lal, Ramesh External | 2017-05-29 04:40 | [7 empty] | Lal, Ramesh External | 2017-05-11 00:29 |  | <p>Following corrections should be done for units of enthalpy and entropy&nbsp;in the Test procedure SRF2229_STABLE97_SVTP_rev1.1:</p><p>1. Section 5.2.2 J):&nbsp;&nbsp;&nbsp; &nbsp;&nbsp;&nbsp; <font face="Times New Roman" size=3>&nbsp;&nbsp; &nbsp;</font><font face=Calibri size=3></font><font face="Times New Roman" size=3> </font><font face=Calibri size=3>i. HIUNT&nbsp; : psi/lbm/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm</font></p><p><font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 8pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;&nbsp;&nbsp;&nbsp; &nbsp;ii<font face=Calibri size=3>. HOUNT : psi/lbm/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm</font></p><font face=Calibri size=3><p>2. Section 5.2.2 K):&nbsp;<font face="Times New Roman" size=3>&nbsp;&nbsp; </font><font face=Calibri size=3>i. SIUNT&nbsp; : psi.ft3/lbm/R should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</font></p><p><font face="Times New Roman" size=3></font></p><p style="margin:0cm 0cm 8pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ii. SOUNT : psi.ft3/lbm/R &nbsp;should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</p><font face=Calibri size=3><p style="margin:0cm 0cm 8pt;">3. Section 5.7.1 J):&nbsp;&nbsp;&nbsp;<font face="Times New Roman" size=3> </font><font face=Calibri size=3>i. HIUNT&nbsp; : psi/lbm/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;ii<font face=Calibri size=3>. HOUNT : psi/lbm/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm</font></font>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;</p><font face=Calibri size=3><p>4. Section 5.7.1 K):&nbsp;<font face="Times New Roman" size=3>&nbsp;&nbsp; </font><font face=Calibri size=3>i. SIUNT&nbsp; : psi.ft3/lbm/R should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</font></p><p><font face="Times New Roman" size=3></font></p><p style="margin:0cm 0cm 8pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;ii<font face=Calibri size=3>. SOUNT : psi.ft3/lbm/R &nbsp;should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</font></p></font></font><p style="margin:0cm 0cm 8pt;">5. Section 5.5.3.1:&nbsp;&nbsp;&nbsp;&nbsp; <font face="Times New Roman" size=3>SPECIFIC ENTHALPY:&nbsp;<font face=Calibri> psi/lb/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm<br><font face="Times New Roman" size=3><font face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; </font>SPECIFIC ENTROPY:&nbsp;&nbsp;&nbsp;&nbsp; <font face=Calibri>psi.ft3/lbm/R &nbsp;should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</font></font></font></font></p></font><p style="margin:0cm 0cm 8pt;"><font face=Calibri size=3><font face=Calibri size=3>6. Section 5.5.3.2:&nbsp;&nbsp;&nbsp; <font face="Times New Roman" size=3>SPECIFIC ENTHALPY:&nbsp;<font face=Calibri> psi/lb/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm<br><font face="Times New Roman" size=3><font face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;</font>SPECIFIC ENTROPY:<font face=Calibri>psi.ft3/lbm/R &nbsp;should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R<br>7. Section 5.5.3.3:&nbsp;&nbsp;&nbsp; <font face="Times New Roman" size=3>SPECIFIC ENTHALPY:&nbsp;<font face=Calibri> psi/lb/ft3 should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm<br><font face="Times New Roman" size=3><font face=Calibri>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;</font>SPECIFIC ENTROPY:<font face=Calibri>psi.ft3/lbm/R &nbsp;should be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R</font></font></font></font></font></font></font></font></font></font></p><font face="Times New Roman"><p><font face=Calibri size=3><br></font></p></font><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><font face="Times New Roman"> <br></font></p><p style="margin:0cm 0cm 8pt;"><br></p><p><font face="Times New Roman" size=3> &nbsp;</font><font face="Times New Roman" size=3> </font></p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><p><font face="Times New Roman" size=3><br></font></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>5/11/17: RL - The unit for enthalpy&nbsp; psi/lb/ft3 will be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm in the final SVTP document at the following places:</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;Section 5.2.2 j), 5.2.2 k), 5.5.3.1, 5.5.3.2, 5.5.3.3</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; The unit for entropy&nbsp; psi.ft3/lbm/R will be changed to psi<span style="color:red;">a</span>.<span style="color:red;">ft3</span>/lbm/R in the final SVTP document at the following places:</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;Section 5.2.2 j), 5.2.2 k), 5.5.3.1, 5.5.3.2, 5.5.3.3</p><p><br></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/22/17&gt; please continue testing with the proposed resolution. <br></font><font size=3> Note the proposed resolution clearly in a comment field in your test record.&nbsp;<br> The SVTP should be modified with this change at the end of the project.</font></span></p> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2-U4 |  |  | FINDING | [6 empty] | 113447
39294 | FINDING | STABLE97: Test procedure SRF2229_STABLE97_SVTP_rev1.1 needs corrections for typographical errors. | Lal, Ramesh External | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-23 09:10 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-23 09:10 | [7 empty] | Lal, Ramesh External | 2017-05-11 03:14 |  | <p>Following typographical errors should be corrected in the test procedure SRF2229_STABLE97_SVTP_rev1.1 for the Steam Table algorithm:</p><p>Section 5.4.8.3: Scenario : AccuracyTest\AlgTestScenario\S_T_REG4_SL&nbsp; should be changed to AccuracyTest\AlgTestScenario\V_T_REG4_SL&nbsp; </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;AccuracyTest\AlgTestScenario\S_T_REG4_SV&nbsp; should be changed to AccuracyTest\AlgTestScenario\V_T_REG4_SV&nbsp; </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; AccuracyTest\AlgTestScenario\S_P_REG4_SL&nbsp; should be changed to AccuracyTest\AlgTestScenario\V_P_REG4_SL&nbsp; </p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; AccuracyTest\AlgTestScenario\S_P_REG4_SV&nbsp; should be changed to AccuracyTest\AlgTestScenario\V_P_REG4_SV </p><p>Section 5.5.1.1:&nbsp;&nbsp;&nbsp; &nbsp;PSAT_P should be changed to PSAT_T</p><p>Section 5.5.2.9:&nbsp;&nbsp; &nbsp;&quot;To generate INF&quot; is described twice. The last appearance should be deleted.&nbsp;</p><p>Section 5.5.3.1:&nbsp;&nbsp;&nbsp;&nbsp; PRESSURE: FUNC=TSAT_P should be changed to FUNC=HSV_TP</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; SPECIFIC ENTHALPY: FUNC=TSAT_P should be changed to FUNC=TP_HS</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; SPECIFIC ENTROPY: FUNC=TSAT_P should be changed to FUNC=TP_HS</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ATMOSPHERIC PRESSURE: FUNC= HSV_TP&nbsp;should be noted.</p><p>Section 5.5.3.2:&nbsp;&nbsp;&nbsp; &nbsp;PRESSURE: FUNC=TSAT_P should be changed to FUNC=HSV_TP</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; SPECIFIC ENTHALPY: FUNC=TSAT_P should be changed to FUNC=TP_HS</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;SPECIFIC ENTROPY: FUNC=TSAT_P should be changed to FUNC=TP_HS</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; SPECIFIC VOLUME : FUNC= HSV_TP&nbsp;should be noted.</p><p>Section 5.5.7.4:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; c), b) c) should be corrected to b), c), d).</p><p>Section 5.5.7.5:&nbsp;&nbsp;&nbsp; &nbsp;&nbsp;c), b) c) should be corrected to b), c), d).</p><p>Section 5.6.1:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;Input pin VI should be removed.</p><p>Section 5.6.2:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;&quot;... STABLE97 algorithm has is set to INF or NaN&quot; should be&nbsp;corrected to&nbsp; &quot;... STABLE97 algorithm&nbsp;is&nbsp;set to INF or NaN&quot;.</p><p>Section 5.6.3: c).&nbsp;&nbsp;&nbsp; ATM = 0 MPa should be corrected to PATM = 0 MPa</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; e).&nbsp;&nbsp;&nbsp; Inputs: SI = 3 kJ/Kg*K should be changed to Inputs: SI = 3 kJ/Kg/K </p> |  |  |  |  | 0 |  |  |  | IC 5/22/17&gt; Changed &quot;Assigend To&quot; to be Ramesh since he's the SVTP author, set Planned Release to FP3. | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3. |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Lal, Ramesh External | Validation |  | <p>5/11/17:RL - Typographical errors in following sections as mentioned above will be corrected in the final SVTP documents:</p><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Sections: 5.4.8.3, 5.5.1.1, 5.5.2.9, 5.5.3.1, 5.5.3.1, 5.5.3.2, 5.5.7.4, 5.5.7.5, 5.6.1,5.6.2, 5.6.3, </p><p><br></p> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2-U4 |  |  | FINDING | [6 empty] | 113210
39298 | FINDING | STABLE97: Test procedure SRF2229_STABLE97_SVTP_rev1.1 needs changes for a few test cases. | Lal, Ramesh External | Will Fix in Future Update | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-23 09:13 | [11 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-23 09:13 | [7 empty] | Lal, Ramesh External | 2017-05-11 04:26 |  | <p>Test description&nbsp;for following test cases &nbsp;should be modified as described below:</p><p>Section 5.5.1.3:&nbsp; &quot;<span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">Repeat the tests mentioned above in section 5.5.1.1 and 5.5.1.2 with RREG = ALL. Verify that the output pin REGION displays the correct region for each test.&quot;</span></p><span style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;This&nbsp;should be modified to: <font face="Times New Roman" size=3> </font></p><p style="margin:0cm 0cm 8pt;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;Repeat the tests mentioned above in section 5.5.1.1 and 5.5.1.2 only for the function HSV_TP (which can operate in different regions) for RREG = 1, RREG = 2, <br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; RREGE = 3 and RREG = 5 with RREG = ALL. Verify that the output pin REGION displays the correct region for each test.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Note: TP_HS, PSAT_T, TSAT_P and HSV_TP (RREG=4) are designed to&nbsp;operate only in Region 4 and automatic region indication&nbsp;is not required.&quot;</p><span lang=EN-US style=""><p style="margin:0cm 0cm 8pt;">Section 5.5.2.7: &quot;NOTE: Use Test g) from Excel sheet &quot;STABLE97 Validation Data&quot; [5] where STAT=66&quot; <br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; This should be modified to:&nbsp;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;&quot;NOTE: Use Test g) from Excel sheet &quot;STABLE97 Validation Data&quot; [5] where STAT=194.<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Manually decrease PI value from 99.8 MPa to 99.0 MPa. Check that STAT=66.&quot;</p><p style="margin:0cm 0cm 8pt;">Section 5.9.1:&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;3. Open Signal&nbsp; Diagram and verify that the algorithm runs without errors.&quot;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;This should be modified to:<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &nbsp;&quot;3. Open the Signal Diagram and verify that any other STABLE97 algorithm existing in the same control sheets runs without errors.&quot;</p><p style="margin:0cm 0cm 8pt;"><br><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p><span lang=EN-US style="font-family:&quot;Times New Roman&quot;,serif;"><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><br></p></span><p style="margin:0cm 0cm 8pt;"><br></p><p style="margin:0cm 0cm 8pt;"><font face="Times New Roman" size=3> </font><br><br><br></p></span><p style="margin:0cm 0cm 8pt;"><span lang=EN-US style="line-height:107%;font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;"><span style=""><br></span></span></p></span><p><br></p> |  |  |  |  | 0 |  |  |  | IC 5/22/17&gt; Changed &quot;Assigend To&quot; to be Ramesh since he's the SVTP author, set Planned Release to FP3. | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | Issue Needs Fixed | 0 |  |  | Lal, Ramesh External | Validation |  | 5/11/17:RL - Test sections 5.5.1.3, 5.5.2.7 and 5.9.1 of SRF2229_STABLE97_SVTP_rev1.1 will be modified as described above in the final SVTP.<br><br><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/22/17&gt; please continue testing with the&nbsp;resolutions proposed in the Description box. <br></font><font size=3> Note clearly in a comment field in your test record that you are using the proposed resolutions.&nbsp;<br> The SVTP should be modified with these changes at the end of the project.</font></span> | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2-U4 |  |  | FINDING | [6 empty] | 113212
39309 | FINDING | OV360FP2: SRF2250 SVTP needs few corrections | Brown, Sean EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-05-12 13:28 | [11 empty] | USPITTFSService | 2017-05-12 13:28 | [7 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-05-12 13:28 |  | <p>SRF2250 SVTP needs following corrections:</p> <p>&nbsp;</p> <p>Test 5.1.3.2 a to h<br>Repeated tests, should be deleted</p> <p>&nbsp;</p> <p>Test 5.1.4 c<br>Following statement should be removed as it is not true: and it does not increase i.e. accumulation has also halted.</p> <p>&nbsp;</p> <p>Test 5.1.6<br>Test is not applicable for Control Builder hence should be deleted.<br></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OV360FP2_U4 |  |  | FINDING | [6 empty] | 112741
39310 | FINDING | DEC - DEC Oscillography configuration does not appear to calculate buffer size requirements | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:14 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:14 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-12 13:57 |  | <p>The DEC Oscillography configuration is to calculate the required memory for a buffer configuration.&nbsp; This does not appear to be happening.&nbsp; A large buffer was created that should have exceeded the available memory and no warning/error message was displayed. </p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>3.6.0 + FP2</p> |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Create a buffer&nbsp;(or multiple buffers)&nbsp;with many points, a fast frequency and for a long period of time. |  | OVA360FP2 |  |  | FINDING | [6 empty] | 116944
39311 | FINDING | Controller Triggered Event configuration is not getting to controller without reboot. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-27 11:15 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-27 11:15 |  |  |  | 2017-07-27 11:15 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-12 14:55 |  | Controller Triggered Event configuration is not getting to controller without reboot.<div>Controller needs reboot after every new triggered event configuration or any modification in triggered event configuration.</div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  | OVA360FP2_U4<div>OCR1100</div> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Add new configuration or modify existing one. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116641
39312 | FINDING | Event Trend: Bit Mask in not available for Packed Points. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 14:59 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 14:59 | 76922 |  |  | 2017-07-17 14:59 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-12 15:01 |  | Bit Mask in not available in event Trend for Packed Point Event variables (Controller Triggered Event). |  |  |  | Retest | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3, OPH360005 |  | <div>Event Type-Controller Triggered Event\<br></div><div>Application- Event Trend</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ- Tested on FP03_U2+OPH360005. issue is fixed. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Check Trace Properties. |  | OVA360FP2-U4 |  |  | FINDING | [6 empty] | 116058
39317 | FINDING | Safety Shell SVTP-Procedure for verification of PD point Value and Quality propagation needs to be modified. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 |  |  |  | 2018-01-10 04:31 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-15 09:10 |  | <span style="color:windowtext;"><font face=Times size=3><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">Procedure for verification of PD point Value and Quality propagation needs to be modified </span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">In test cases, verifying the value propagation of points between controller using control with assign algorithm in receiving controller drop.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">For Point Type: LA, DA, LD, DD, LP, DP, PD.</span></p><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;"><br></span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">Test case 5.2.4, verifying the value propagation from <u>Originating Controller OCR1100</u> to receiving controller drops <u>Virtual OCR1100</u> and <u>OCR400</u>.</span></p><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">Test 5.2.16, verifying the value and quality propagation from Originating Virtual Controller 1100 to receiving controller OCR1100.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;"><br></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:105%;font-family:&quot;Times&quot;,serif;font-size:14pt;">In the SVTP, test cases verifying the PD point propagation using “Assign” algorithm in receiving controller drop. During testing, it is observed that the value propagation cannot be verified using “Assign” algorithm.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="color:windowtext;font-size:14pt;">Validation verified that<b style=""> ETIM1</b> pin of SOFT SOE algorithm supports PD point.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="color:windowtext;font-size:14pt;">Verification for PD points propagation (Value and Quality) will be performed using SOFT SOE algorithm and SHC_DEMO utility.</span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> </font><span style="color:windowtext;font-size:14pt;"><br></span></p><p style="margin:0in 0in 0pt;"><span style="color:windowtext;font-size:14pt;">Detail steps and procedure&nbsp;for PD point verification is attached in the document “Procedure for PD Point verification.docx”. </span></p><p style="margin:0in 0in 0pt;"><font face="Times New Roman"> <br></font></p></font><p style="margin:0in 0in 0pt;"><br></p></span><p style="margin:0in 0in 0pt;"><br></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Gupta, Chandresh EMR SYSS PWS NOIDA |  | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA |  |  |  |  | Implementation | SVTP_rev1.5 |  | <p><br></p> |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | Proposed resolution is attached in document &quot;Procedure for PD Point verification.docx&quot;.<br><font face="Times New Roman" size=3> <br></font><p style="margin:0in 0in 8pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/22/17&gt; please continue testing with the proposed resolution. <br></font><font size=3> Note clearly in a comment field in your test record that you are using the attached procedure.<br> The SVTP should be modified with this change at the end of the project.</font></span></p><p style="margin:0in 0in 8pt;"><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><strong>VP&gt; Will fix in SVTP_rev1.5.</strong></font></span></font></span></p><font face="Times New Roman" size=3> </font> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122424
39326 | FINDING | DEC - DEC Oscillography buffer configuration does not allow for buffer to be duplicated. | Patel, Sunil EMR SYSS PWS PITT | Development Complete | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:55 | [11 empty] | Patel, Sunil EMR SYSS PWS PITT | 2017-08-03 14:55 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-15 14:19 |  | Functional spec states that an existing buffer can be cloned/duplicated and renamed.&nbsp; This is not currently available. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | 3.6.0 + FP2 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | Development Complete | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use the DEC Engineering tool to try to duplicate an existing buffer configuration. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 116949
39327 | FINDING | DEC - DEC Oscillography buffer configuration does not allow for importing or exporting of configurations. | Wimer, Walter L EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-05-15 14:22 | [11 empty] | USPITTFSService | 2017-05-15 14:22 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-15 14:22 |  | Functional spec states that capture buffer configurations can be imported and exported.&nbsp; This is currently not available. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Patel, Sunil EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | 3.6.0 + FP2 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Use DEC Engineering tool to attempt to import and export a configuration. |  | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 112841
39339 | FINDING | Controller Triggered Events: Issue with Fully qualified point name in controller Triggered Event. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:03 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-19 16:03 | 76212 |  |  | 2017-07-19 16:03 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-17 12:55 |  | Fully qualified Point name (with Network alias) is not recognised in Triggered Events.<div><br></div> |  |  |  | <p>The affected area is in the way the software propagates the user-entered point name to an internal attribute which contains the object key of the referenced point.</p><p>This&nbsp;change also affects all analog point alarm limits (where the limit is specified as another analog point), including all plant mode alarm limits for deluxe analog points.</p><p>This change also affects all fields where a point name can be specified as an alarm cutout, including all plant mode alarm limits for deluxe versions of points.</p> | 0 |  |  |  | YJ:&nbsp;Issue tested on Drop250 CARL network having Ov360 FP03_U2+OPH360005&nbsp;and found fixed. | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  | Controller Triggered Event<div>Controller-40/90</div><div>Newly inserted Triggered event</div><div><br></div> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | <p>The software will be changed to find the associated point when the user specified a name&nbsp;which is&nbsp;fully qualified with the Network alias.&nbsp; However, once saved, the fully qualified name will be shown as with the network name in the database hierarchy (as will the Triggered Event point UIs once refreshed) -- not the user entered network alias.<br></p> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Insert new controller trigger event --&gt; Add Trigger point &amp; Fully qualified Event Variable (must use network alias) --&gt; Load the controller --&gt; triggered Event is not working.<div>&quot;<span style="font-family:&quot;Courier New&quot;;font-size:10pt;">trigEvent.XML</span>&quot; file misses Event point name &amp; SID is always 0x000000.</div> |  | OVA360022 |  |  | FINDING | [6 empty] | 116214
39340 | FINDING | Event Trend: Refresh Button popup text needs modification. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:35 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-15 13:35 |  |  |  | 2017-06-15 13:35 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-17 13:01 |  | Event Trend-Refresh Button popup text needs modification. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | Event Trend<div>OVA360022<br></div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH36003 &amp; Ov360 FP03 | 4 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | Open Event Trend --&gt; Open Event --&gt; Click on refresh Button. |  | OVA360022 |  |  | FINDING | [6 empty] | 114379
39342 | FINDING | Sometimes Event Trend double click does not restore chart | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2017-07-04 07:50 | [11 empty] | Agarwal, Gaurav EMR SYSS PWS NOIDA | 2017-07-04 07:50 | 76308 |  |  | 2017-07-04 07:50 |  |  |  | Bargaje, Prashant C EMR SYSS PWS PITT | 2017-05-17 14:12 |  | When a chart is zoomed and scroll bar is visible, and original display ratio is small like 2:1, double click operation may not restore the chart. |  |  |  |  | 0 |  |  |  | <p>GA:-</p><p>Date:- 7/4/2017</p><p>Used build:- Ov 3.6.0_U1</p><p><br></p><p>Issue, which is described in the finding is not observed in Ov 3.6.0_FP3_U1 build. Hence finding is closed.</p><p><br></p> | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Bargaje, Prashant C EMR SYSS PWS PITT | Agarwal, Gaurav EMR SYSS PWS NOIDA | [8 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  |  |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Bargaje, Prashant C EMR SYSS PWS PITT | Development |  | cg 6/12/17 : Findings reassigned to Gaurav. Please retest the fix. | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP3 |  |  | FINDING | [6 empty] | 115222
39345 | FINDING | DEC - DEC Oscillography event cannot be triggered from DXCSTATUS algorithm. | Wimer, Walter L EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-17 14:59 | [11 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-17 14:59 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-17 14:59 |  | Though this is not called out in the functional spec, it was discussed in the FS review meeting.&nbsp; It was mentioned that a DEC oscillography event can be triggered from the dxcstatus algorithm.. It would always trigger the first buffer configuration.&nbsp;&nbsp; This currently can't be done.&nbsp;&nbsp; If this is no longer the case, the finding can be closed. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Silvaggio, Gregory W EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | <p>3.6.0 + FP2</p> |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2_U4 |  |  | FINDING | [6 empty] | 112992
39347 | FINDING | OCR400 controller is not coming up after download in OV3.6.0 FP3. | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Garg, Amit AUTOSOL PWS NOIDA | 2017-06-07 03:56 | [11 empty] | Garg, Amit AUTOSOL PWS NOIDA | 2017-06-07 03:56 | 76162 |  |  | 2017-06-07 03:56 |  |  |  | Garg, Amit AUTOSOL PWS NOIDA | 2017-05-18 05:34 |  | <p>Drop 16/66 (OCR 400 ) was working fine in Ovation 3.6.0 FP1 ( NET 26).&nbsp;</p><p>After loading OVA360FP3_U0 patch on Net 26,&nbsp;drop 16/66&nbsp;is not coming up after download and clear operation.&nbsp;&nbsp;</p><p><br></p> |  |  |  | Verify ocr400 comes up after downloading/rebooting. | 0 |  |  |  | Successfully downloaded and Rebooted the OCR400 controller Drop16/66 and it&nbsp;is working fine. | 0 |  | Ovation for Windows/Controller/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Benzvi, Mati EMR SYSS PWS PITT | [7 empty] | Implementation | OVA360FP3_U1 |  | <p>OV3.6.0 with FP3_U0 patch</p><p>OCR400 G02 controller</p> |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Garg, Amit AUTOSOL PWS NOIDA | Validation |  | Corrected the ocr400linkNonDebug file. | 7 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [5 empty] | <p>1.Drop 16/66 (OCR 400 ) was working fine in Ovation 3.6.0_FP1 set up ( Drop 220 -DBS : Net # 26).</p><p>2. Install FP3_U0 patch on&nbsp;Net# 26&nbsp;( DBS :Drop220 and all workstations) as per given instruction. </p><p>3. Download&gt;Clear the drop16/66.</p><p>4. It&nbsp;is observed that after completing&nbsp;clear operation,&nbsp; controller&nbsp;pings for few secs ( approx. 40-50&nbsp;) and then stops pinging.</p><p>5.&nbsp; The result is same after clearing the&nbsp;controller flash and download &gt; reboot of controller. &nbsp;</p><p>&nbsp;&nbsp;&nbsp; This issue is not seen with&nbsp;OCR 1100.&nbsp;&nbsp;&nbsp;</p><p>Error log file is attached for your reference.</p><p><br></p> |  | OVA360FP3_U0 |  |  | FINDING | [6 empty] | 113874
39355 | FINDING | Safety Shell- Fault code file does not have any information for the fourth parameter. | Lupu, Mircea F AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-07-10 03:56 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-07-10 03:56 | 76707 |  |  | 2017-07-10 03:56 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-19 08:21 |  | <p><font face="Times New Roman" size=3> <br></font></p><p><a name=_GoBack></a><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">Fault code file does not have any information for the fourth parameter.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-family:&quot;Segoe UI&quot;,sans-serif;font-size:9pt;">&nbsp;</span><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">Detail of Fault parameters also retrieving in other Ovation applications e.g. System Viewer, Point Info etc.</span></p><p><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3><br></font></p><p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">Finding#39205 already reported for system viewer that&nbsp;Drop Fault Report does not show expected fault parameters detail for safety shell fault alarm.</span></p><p><font face="Times New Roman" size=3> <br></font></p><p><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">Note: For resolution of finding#39205 Fault code file needs to be fixed.</span></p><p><font face="Times New Roman" size=3> <br></font></p> |  |  |  |  | 0 |  |  |  | <p><font face="Times New Roman" size=3>VP: 7/10/17&gt;&nbsp; Loaded the OVA360FP3_U2.</font></p><p><font face="Times New Roman" size=3>Retested the Finding#39205, verified that&nbsp; System viewer display information of all Fault parameters for Safety Shell Fault alarm&nbsp;including Fourth parameter.&nbsp;<br></font></p><p><font face="Times New Roman" size=3>Verified that System viewer report display&nbsp;text and description for the Safety Shell fault alarm. <br>Verified the scenario for&nbsp;Bad DDB&nbsp;Source error. Following detail observed i</font><font face="Times New Roman" size=3><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">n<strong> System Viewer: Fault Code:66, Fault ID:09, FP1: 12</strong></span><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">, <b style="">FP2: 01, FP3: 01; FP4: 102.</b></span></font></p><p><font face="Times New Roman" size=3><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;"><span style="font-family:&quot;Arial&quot;,sans-serif;font-size:11pt;">After&nbsp;above verification, finding#39205&nbsp;was&nbsp;closed.&nbsp;</span></span></font></p><p><font face="Times New Roman" size=3><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">For reference, Screenshot of System Viewer is attached.</span></font></p><p><font face="Times New Roman" size=3><span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">Hence, finding#39355&nbsp;is closed.</span><br></font></p> | 0 |  | Ovation for Windows/Controller/General/Software | ovationerrorcodes.xml was updated to reflect the correct data type for FP4. |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Gupta, Chandresh EMR SYSS PWS NOIDA | Costlow, Kim EMR SYSS PWS PITT | Sharma, Satish AUTOSOL PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Zochowski, Piotr EMR SYSS RS WRSW | Wozniak, Diane M EMR SYSS PWS PITT |  |  | Implementation | OVA360FP3_U2 |  | OVA360FP2 |  | Ovation for Windows | Ovation | Controller/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  |  | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 115481
39359 | FINDING | SVTP - update AMS tests to include "Add DD" test | Gupta, Chandresh EMR SYSS PWS NOIDA | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-05-19 09:37 | [11 empty] | USPITTFSService | 2017-05-19 09:37 | [7 empty] | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 09:37 |  | Update AMS Device Mnager section of the latest version of OPTIONAL_SW_SVTP (on sharepoint) to have an &quot;Add DD&quot; test.<br>Gil Morris requested this. Please email him if further info is required. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Development |  |  | 2 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP3 |  |  | FINDING | [6 empty] | 113060
39360 | FINDING | MHM Plotting: test use IP Port of Ovation Switch | Sachan, Pallavi EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Cunningham, Jeffrey S EMR SYSS PWS PITT | 2022-07-18 16:25 | [11 empty] | Cunningham, Jeffrey S EMR SYSS PWS PITT | 2022-07-18 16:25 |  |  |  | 2022-07-18 16:25 |  |  |  | Capani, Innocenzo AUTOSOL PWS PITT | 2017-05-19 10:13 |  | The MHM Plotting communication is intended to use an IP port on the Ovation switch. <br>This should be noted in the&nbsp;MHM plotting SVTP and tested. |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP4 |  |  |  | Ovation for Windows | Ovation | Controller/MHM | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Capani, Innocenzo AUTOSOL PWS PITT | Development |  |  | 3 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP2 |  |  | FINDING | [6 empty] | 189861
39366 | FINDING | Alignment of QNOT,QOR and COMPARATOR algorithms (SRF 2264) in standard/ Booleans with Quality library is not correct | Matthew Cimino | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-24 01:13 | [11 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-24 01:13 | 76882 |  |  | 2017-07-24 01:13 |  |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-05-22 06:38 |  | <p>Alignment of QNOT,QOR and COMPARATOR algorithms (SRF 2264)&nbsp;in standard/ Booleans with Quality library is not correct.&nbsp;</p><p>The IN and OUT pins of the algorithms&nbsp;are appearing out of the pane. </p><p>Please refer the attachments for more details.</p> |  |  |  |  | 0 |  |  |  | <p>HS-07/24:Tested in U2, issue is fixed so closing the finding</p> | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/Control Sheet Editor/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [7 empty] | Implementation | OVA360FP3_U1 |  | <p>OV3.6.0 with FP3_U0 patch</p><p>Drop 220 (DBS)</p> |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/Control Sheet Editor | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  |  | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>Open Developer Studio and cb editor of any controller.</li><li>&nbsp;click on Add Control Algorithm option available&nbsp;in the toolbar.</li><li>Go to <strong> standard</strong>/ <strong>Booleans with Quality</strong> library&nbsp;under the&nbsp;Algorithm Symbols.</li><li>Alignment of Algorithms&nbsp;<strong>QNOT,QOR and COMPARATOR</strong> is not correct.</li></ol> |  | OVA360FP3_U0 |  |  | FINDING | [6 empty] | 116404
39395 | FINDING | DEC - DEC Oscillography task failure is not being reported in module record. | Wimer, Walter L EMR SYSS PWS PITT | Open | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-05-24 14:47 | [11 empty] | USPITTFSService | 2017-05-24 14:47 | [7 empty] | Perdeus, Matthew AUTOSOL PWS PITT | 2017-05-24 14:47 |  | <p>The DEC module is to detect failure of the oscillography task(s) and report the failure in the module's D register.&nbsp;&nbsp; This is not currently occuring.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/DEC/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wimer, Walter L EMR SYSS PWS PITT | [9 empty] | Implementation |  |  | 3.6.0 + FP2 |  | Ovation for Windows | Ovation | Controller/DEC | Software | Standard Release | 3.6.0 |  |  | New Issue | 0 |  |  | Perdeus, Matthew AUTOSOL PWS PITT | Validation |  |  | 2 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <p>kill the oscillography tasks in the module (td command) and see no error is reported in the modules D register bit 15. </p> |  | OVA360FP2 |  |  | FINDING | [6 empty] | 113304
39406 | FINDING | Safety Shell - SVTP - Procedure in Testcases 5.5.6, 5.5.24, 5.5.25 needs to be modified. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Goyal, Ashish EMR SYSS PWS NOIDA | 2018-01-10 21:24 | [11 empty] | Goyal, Ashish EMR SYSS PWS NOIDA | 2018-01-10 21:24 |  |  |  | 2018-01-10 21:24 |  |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | 2017-05-25 15:03 |  | <span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;LINE-HEIGHT:107%;"> <p class=MsoNormal style="BACKGROUND:white;MARGIN:0in 0in 8pt;LINE-HEIGHT:normal;"><a name=_GoBack></a><b><u><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;">Modification in SVTP Test case 5.5.6</span></u></b><font face=Arial><span style="FONT-SIZE:10pt;COLOR:black;">&nbsp;</span><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Segoe UI&quot;,sans-serif;COLOR:#1e1e1e;"></span></font></p> <p class=MsoNormal style="BACKGROUND:white;MARGIN:0in 0in 8pt;LINE-HEIGHT:normal;"><span style="FONT-SIZE:10pt;COLOR:#1e1e1e;"><font face=Arial>D31_S_HI_RF_CHANGEDOUT is assigned to OUT pin of Comparator algorithm output. But with test case statement we cannot achieve objective if we monitor Output of Comparator (D31_F_HI_RF_CHANGEDOUT). <br>In test we should monitor output of first Assigned i.e. D31_S_HI_RF_ASSIGNEDOUT to achieve our test case objective. The reason is that when Drop102 is disconnected from Highway, inputs of comparator go 0 and Bad Quality and output of comparator algorithm go High (both inputs are 0) quality is Good.</font></span></p> <p class=MsoNormal style="BACKGROUND:white;MARGIN:0in 0in 8pt;LINE-HEIGHT:normal;"><span style="FONT-SIZE:10pt;COLOR:#1e1e1e;"><font face=Arial>Similarly we should monitor D31_F_HI_RF_ASSIGNEDOUT&nbsp;in place of D31_F_HI_RF_CHANGEDOUT.</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"></span>&nbsp;</p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><u><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;LINE-HEIGHT:107%;">Modification in SVTP Test case 5.5.24</span></u></b><font face=Arial><span style="FONT-SIZE:10pt;COLOR:black;LINE-HEIGHT:107%;">&nbsp;</span></font></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-SIZE:10pt;COLOR:#1e1e1e;LINE-HEIGHT:107%;"><font face=Arial>In SVTP Testcase 5.5.24.c.2, the primary controller will be in <i>Off-Highway</i> state and secondary controller will be in <i>In-Control state</i>. Hence testcase should be modified as below:</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><i><span style="FONT-SIZE:10pt;COLOR:red;LINE-HEIGHT:107%;"><font face=Arial>Verify that FB field of drop points show correct status of active controller “In Control” initially which was in backup.</font></span></i></b></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><i><span style="FONT-SIZE:10pt;COLOR:red;LINE-HEIGHT:107%;"><font face=Arial>&nbsp;</font></span></i></b></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><u><span style="FONT-SIZE:10pt;FONT-FAMILY:&quot;Calibri&quot;,sans-serif;COLOR:black;LINE-HEIGHT:107%;">Modification in SVTP Test case 5.5.25</span></u></b></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-SIZE:10pt;COLOR:#1e1e1e;LINE-HEIGHT:107%;"><font face=Arial>In SVTP Testcase 5.5.25, the receiving drop is mentioned as drop32/82, whereas the receiving drop is drop31/81. Hence testcase should be modified as below:</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><i><span style="FONT-SIZE:10pt;COLOR:red;LINE-HEIGHT:107%;"><font face=Arial>Verification that Controller failover to backup is bumpless. Verification on receiving drop31/81.</font></span></i></b></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><span style="FONT-SIZE:10pt;COLOR:#1e1e1e;LINE-HEIGHT:107%;"><font face=Arial>In SVTP Testcase 5.5.25.c.2, the primary controller will be in <i>Off-Highway</i> state and secondary controller will be in <i>In-Control state</i>. Hence testcase should be modified as below:</font></span></p> <p class=MsoNormal style="MARGIN:0in 0in 8pt;"><b><i><span style="FONT-SIZE:10pt;COLOR:red;LINE-HEIGHT:107%;"><font face=Arial>Verify that FB field of drop points show correct status of active controller “In Control” initially which was in backup.</font></span></i></b></p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Gupta, Chandresh EMR SYSS PWS NOIDA |  | Pandey, Vijay EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA |  |  |  |  | Implementation | SVTP_rev1.5 |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | In Validation | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Goyal, Ashish EMR SYSS PWS NOIDA | Validation |  | <p>Proposed resolution is attached in document &quot;Test case 5.5.6.docx&quot;<br><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/31/17&gt; please continue testing with the proposed resolution. <br></font><font size=3> Note clearly in a comment field in your test record that you are using the attached procedure.<br> The SVTP should be modified with this change at the end of the project.</font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>VP&gt; Fix available in SVTP_rev1.5</font></span></p> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122474
39417 | FINDING | Event Trend is not displaying 50th Event Variables for Controller's Triggered Event. | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 16:41 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 16:41 | 76857 |  |  | 2017-07-17 16:41 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-26 14:57 |  | Maximum Event variables that can be configured for an Event is 50.<div>Event Trend is not displaying 50th Event Variables. Event Trend is displaying 49 Event Variables + Trigger Point.</div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | Ov360+OVA360022<div>OPH360+OPH36002 &amp; OPH360003</div><div>Event Trend on Drop127</div><div>Controller Triggered Event&nbsp;</div><div>Controller Drop-4/54</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP03_U2 | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Trigger the Event having 50 variables --&gt; Observe the Triggered Event in Event Trend --&gt; 50th variable is missing.<div><br></div> |  | OVA360022 |  |  | FINDING | [6 empty] | 116064
39418 | FINDING | Event Trend- Trigger Variable information under Event Details needs modification. | Hatok, Alan M AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 16:41 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-07-17 16:41 | 77000 |  |  | 2017-07-17 16:39 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-26 16:28 |  | 1. Trigger Variable under Event Details is displayed as SID. It would be easy to understand, search or use this information of Trigger Variable if there is a Point Name.<div>2. Value Tab is empty. Value of Trigger point is always True (1) whenever Event happen.&nbsp;</div><div><br></div><div><br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | 3.6.0 FP3 |  | Event Trend<div>OVA360022 + OPH360003<br></div><div>Controller Triggered Event.</div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP03_U2 | 6 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | OVA360022 |  |  | FINDING | [6 empty] | 116065
39420 | FINDING | Bool Alg Qual: Online help for QNOT algorithm is not available. | Hutchison, Steven EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 3 | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-31 01:24 | [11 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-31 01:24 | 77331 |  |  | 2017-07-31 01:24 |  |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-05-29 06:27 |  | <p>Online help for QNOT algorithm is not available.</p><p>When it is&nbsp;try to open QNOT help from control sheet or signal diagram it gets navigate to AND algorithm help instead of QNOT.</p> |  |  |  |  | 0 |  |  |  | HS (7-31-17) : Tested in U3 build of FP3 and issue find to be fixed so closing the finding. | 0 |  | Ovation for Windows/Engineering Tools/Control Builder/General/Software | <p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">AA (05-30-17): The issue with the online help is due to some problem in merging the Qt&nbsp;Algorithm Online&nbsp;help files with the software. </font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">&nbsp;</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">The Contex ID for AND is 8007, which is an Advanced algorithm.</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">The Context ID for ONOT is 8334, which is a Standard algorithm.</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">&nbsp;</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Re-assigning this finding to Steve.</font></span></p> |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | [7 empty] | Implementation |  |  | OV3.6.0 with FP3_U0 patch |  | Ovation for Windows | Ovation | Engineering Tools/Control Builder/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font face="Times New Roman" size=3> </font><font size=3> <p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">AA (05-30-17): The issue with the online help is due to some problem in merging the Qt&nbsp;Algorithm Online&nbsp;help files with the software. </font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">&nbsp;</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">The Context ID for AND is 8007, which is an Advanced algorithm.</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">The Context ID for ONOT is 8334, which is a Standard algorithm.</font></span></p><font face="Times New Roman" size=3></font><p><span style="font-size:10pt;"><font color="#666666" face="Times New Roman">Re-assigning this finding to Steve.</font></span></p></font> | 8 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [5 empty] | <ol><li>&nbsp;Create a sheet using QNOT algorithm.</li><li>Select and right click on QNOT algorithm from Control sheet and click on &quot;Help&quot; option</li><li>This will navigate to AND algorithm help.</li></ol><p>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; Same issue is also seen in cb viewer.</p> |  | OVA360FP3_U0 |  |  | FINDING | [6 empty] | 116725
39421 | FINDING | Bool Alg Qual: QNOT algorithm is not working properly, output toggles continuously irrespective of input value | Matthew Cimino | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-13 05:07 | [11 empty] | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-07-13 05:07 | 76857 |  |  | 2017-07-13 05:07 |  |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | 2017-05-29 06:55 |  | <p>QNOT algorithm is not working properly, its output value&nbsp;toggles continuously irrespective of input value.</p><p>There is no effect of input value on this algorithm.</p><p>Please refer attachments. ( QNOT_toggles_1.jpg and QNOT_toggles_1.jpg )</p><p><br></p><p>HS 7/13/17 : Tested in <span style="font-family:&quot;Calibri&quot;,sans-serif;font-size:11pt;">3.6.0 FP3 U2 build </span>and QNOT algorithm is working fine so closing the finding.</p> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Sahay, Madhukar EMR SYSS PWS NOIDA | Jayarajan, Jayakumari EMR SYSS PWS NOIDA | Singhal, Harshita AUTOSOL PWS NOIDA | Silvaggio, Gregory W EMR SYSS PWS PITT | [5 empty] | Implementation | 3.6.0 FP3 |  | OV3.6.0 with FP3_U0 patch |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Singhal, Harshita AUTOSOL PWS NOIDA | Validation |  | Changeset&nbsp;<span style="color:rgb(34, 34, 34);">76302 which includes the fix has not been merged to integration or released to library.</span> | 13 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <ol><li>Open Developer Studio and&nbsp;control sheet&nbsp;of any controller.</li><li>&nbsp;click on Add Control Algorithm option available&nbsp;in the toolbar.</li><li>Go to <strong> standard</strong>/ <strong>Booleans with Quality</strong> library&nbsp;under the&nbsp;Algorithm Symbols.</li><li>&nbsp;Add QNOT algorithm to sheet and assign any algorithms input&nbsp;( DVALGEN, XOR etc)&nbsp;to it&nbsp;&amp; Output page connector.</li><li>Save &amp; compile the Sheet and Load the Controller.</li><li>Open the loaded&nbsp;sheet in&nbsp;cb viewer&nbsp;application.</li><li>The output of QNOT algorithm&nbsp;toggles continuously by it own&nbsp;irrespective of its input value.</li></ol> |  | OVA360FP3_U0 |  |  | FINDING | [6 empty] | 115740
39428 | FINDING | SafetyShell-Editorial changes need to be done in SVTP section 5.6 “Status Algorithm for Safety Shell” | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 |  |  |  | 2018-01-10 04:31 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-05-31 02:25 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><span style="line-height:107%;font-size:9pt;"><font face=Arial>Modification-I </font></span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>“Test case 5.6.6:</font><a name=_Ref462123683><font face=Arial> Verify that SS_STATUS algorithm reports High Repeated Sequence Faults alarm.</font></a><font face=Arial>”</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>For Repeated sequence error scenario, <br> In SS_Status algorithm, Value change is expected only for [RSCT] output. No value change is expected for other outputs.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>There is editorial correction is needed in statement of Test case <b style="">5.6.6.b, 5.6.6.c, 5.6.6.d, 5.6.6.f</b> and<b style=""> 5.6.6.g</b>. <br> <br> Test case statement mentioning for verification of value change for “<b style="">RSCT</b>” and “<b style="">OSC</b>T” output of SS-Status algorithm due to Repeated sequence error injection.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In Repeated sequence error scenario, Change of RSCT output is expected and correctly mentioned in the test cases but change of OSCT error is not expected so verification of <b style="">OSCT </b>output value should be removed.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Note: <span style="">&nbsp;</span>For reference Correct repeated sequence verification mentioned in test case <b style="">5.6.4.e</b> and <b style="">5.6.4.t</b></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Affected test cases: Test case <b style="">5.6.6.b, 5.6.6.c, 5.6.6.d, 5.6.6.f and 5.6.6.g</b>.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><b style=""><span style="line-height:107%;font-size:9pt;"><font face=Arial>Modification-II</font></span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>In Note section of Test case 5.6.5, it is mentioned that “Verification of Drop being in alarmed state shall be done through <b style="">Ovation System Viewer</b> application<b style="">, Alarm</b> application, <b style="">Point Information</b> application and <b style="">Ovation Error Log</b> application.”</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 8pt 0in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>As per development, <b style="">Ovation Error Log</b> application does not support verification for drop alarm state.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 8pt 0in;"><span style="line-height:107%;font-size:9pt;"><font face=Arial>Hence, reference of <b style="">Ovation Error log</b> application for verification of drop alarm state needs to be removed from the note section.</font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | Zochowski, Piotr EMR SYSS RS WRSW | Gupta, Chandresh EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC 5/31/17&gt; please continue testing with the&nbsp;resolution proposed in the Description box. <br></font><font size=3> Note clearly in a comment field in your test record that you are using the proposed resolution.&nbsp;<br> The SVTP should be modified with these changes at the end of the project.</font></span></p><p><span style="font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><strong>VP&gt; Will fix in SVTP_rev1.5.</strong></font></span></font></span></p> | 7 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | FP2 |  |  | FINDING | [6 empty] | 122425
39435 | FINDING | EIO: The Alarm Group Mask Bits 12-15 are not set when Redundany Mode is changed from Legacy to Standard | Swartz, Mark EMR SYSS PWS PITT | Moved to Next Release | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Rick P EMR SYSS PWS PITT | 2017-08-30 11:52 | [11 empty] | Brown, Rick P EMR SYSS PWS PITT | 2017-08-30 11:52 | [7 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-05-31 12:22 |  | An RN point was assigned to an Ethernet I/O RNC.&nbsp; At some point the Redundancy Mode was Legacy (which does not have a partner RNC).&nbsp; The Redundancy Mode was later changed to Standard, but the partner bits didn't report alarms.<br><br>Touching the RN points corrected the Alarm Group Mask.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [8 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Not Critical for This Release | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  |  | 5 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP3_U0 |  |  | FINDING | [6 empty] | 117709
39436 | FINDING | EIO: Please make three unused Ethernet I/O fields read-only. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2017-10-05 14:22 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-10-05 14:22 | 78140 |  |  | 2017-10-05 14:22 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2017-05-31 13:11 |  | Three fields under a controller are not used when <span style="font-style:italic;">Network Connectivity = Ovation Network</span> and could be read-only:<br><br>Ethernet Remote Interface:Network Port<br>Ethernet Remote Interface:IP Address<br>Ethernet Remote Interface:IP Address (Partner)<br> |  |  |  | <p>The affected area is in the software reponsible for updating attributes/fields based on changes to the EIO Network Connectivity attribute.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | [8 empty] | Implementation | OVA360026 |  |  |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>The Engineering Tools will be changed to empty (and make read-only) the mentioned fields when the EIO Network Connectivity is set to Ovation Network.</p><p>In addition to the above mentioned fields, the following will also be changed to read-only:</p><p>Ethernet Remote Interface: IP Address (Shared)</p><p>Ethernet Remote Interface: Interface Mode (Primary Drop)</p><p><br></p> | 11 |  | 2958100.75 | Cat 5 - Enhancement Request | [7 empty] | FP3_U0 |  |  | FINDING | [6 empty] | 118891
39437 | FINDING | EIO: Junction temperature for backup RNC is in Sensor Alarm | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Brown, Sean EMR SYSS PWS PITT | 2017-06-05 11:40 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-06-05 11:40 | 76349 |  |  | 2017-06-05 11:40 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2017-05-31 13:38 |  | The A2 bits for Node 1’s RN point show both junction temperatures as Normal.&nbsp; The analog value for the RNC in Control looks reasonable, but the value for the Backup RNC is in Sensor Alarm.<br><br>The information below is from a Mike Durbin email.<br><br>It looks like the HD field for one of the junction temp points is incorrect.<br><br>Primary RNC HD: 0x2080<br>Partner RNC HD: 0x2081<br><br>The primary/partner bit is bit 8:<br><br> <p class=MsoNormal><a name=_GoBack></a><span style="font-family:&quot;Courier New&quot;;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ---------------------------------------------------<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; bit&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; value&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; description<br> &nbsp;&nbsp;&nbsp;&nbsp; ---------------------------------------------------<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 0-3&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 0&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; junction temperature &quot;register&quot;<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; d&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; node status &quot;register&quot;<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 4-6&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 0&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; unused<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 7&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; remote node bit<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 8&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; note b&nbsp;&nbsp;&nbsp;&nbsp; primary/partner node&nbsp; (new bit defintion)<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 9&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 0&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; unused<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 10-12&nbsp;&nbsp;&nbsp;&nbsp; note a&nbsp;&nbsp;&nbsp;&nbsp; node<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 13&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; group write or remote node bit<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 14&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; note a&nbsp;&nbsp;&nbsp;&nbsp; node<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 15&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 0&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; unused<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ---------------------------------------------------<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; note a: node numbers are 0-15. there are 4 total<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; node bits but for backward compatibility<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; they are not contiguous.<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; note b: 0: primary node<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; 1: partner node<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; in legacy redundancy mode bit 8 will always<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; indicate &quot;primary node&quot;<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; in standard redundancy mode there will still<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; only be one RN record. it should indicate<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;primary node&quot; even though some bits come<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; from the primary node and some come from<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; the partner node.<br> &nbsp;&nbsp;&nbsp;&nbsp;&nbsp; ---------------------------------------------------</span></p> |  |  |  | <p>Affected area is in the software responsible for calculating the hardware address of analog points directly assigned to Ethernet Remote Nodes.</p><p>No specific test recommendations other than what would be considered to be obvious.</p> | 0 |  |  |  | Resolved in Ovation 3.6.0 Feature Pack 3-06022017141858.<br> | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | [9 empty] | Implementation | OVA360FP3_U1 |  | <p><br></p> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/Hardware and I/O Interfaces | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | Hardware address of analog point assigned to partner RNC junction temperature (for standard redundancy) should have bit 8 set (the primary/partner bit) instead of an offset of 1 from the primary hardware address. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP3_U0 |  |  | FINDING | [6 empty] | 113772
39438 | FINDING | RPACNT and RPAWIDTH algorithms reference the MQ field | Silvaggio, Gregory W EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Brown, Sean EMR SYSS PWS PITT | 2017-08-17 13:12 | [11 empty] | Brown, Sean EMR SYSS PWS PITT | 2017-08-17 13:12 | 76862 |  |  | 2017-08-17 13:12 |  |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | 2017-05-31 14:53 |  | Please verify the RPACNT and RPAWIDTH algorithms for Pulse Accumulator Modules work on Local I/O and have not been adversely impacted by the changes to the MQ offset that were made to support Ethernet I/O. &nbsp;Additionally, verify the algorithms work when using Ethernet I/O. |  |  |  |  | 0 |  |  |  | Verified with Ovation 3.6.0 Feature Pack 3-08022017105009.<br> | 0 |  | Ovation for Windows/Controller/Algorithms/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Sahay, Madhukar EMR SYSS PWS NOIDA | Wood, Thomas T AUTOSOL PWS PITT | Brown, Sean EMR SYSS PWS PITT | [7 empty] | Implementation | 3.6.0 FP3 |  |  |  | Ovation for Windows | Ovation | Controller/Algorithms | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Silvaggio, Gregory W EMR SYSS PWS PITT | Development |  | cg (6/29/17) - Finding reassigned to Madhukar for testing. | 6 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [7 empty] | FP3U0 |  |  | FINDING | [6 empty] | 117363
39439 | FINDING | Controller Triggered Event: Able to add blank "Trigger Event" in Developer Studio, No error message even if Trigger point name is missing. | Swartz, Mark EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:24 | [11 empty] | Jain, Yukta AUTOSOL PWS NOIDA | 2017-06-01 13:24 | 75746 |  |  | 2017-06-01 13:24 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-31 15:08 |  | Developer studio is allowing to add blank &quot;Trigger Event&quot;. No error popup If user does not enter any trigger point name.<br><div><span style="font-family:&quot;Times New Roman&quot;, serif;font-size:10pt;">There should be an appropriate error message as per&nbsp;</span>SRF#2242.&nbsp;</div> |  |  |  | <p>The affected area is the definition of this particular attribute.&nbsp; The attribute will now be required.</p><p>No specific test recommendation other than what would be considered to be obvious.</p><p><br></p><p>YJ: Retested in FP03. Issue fixed.</p> | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360FP3 |  | Ovation-OVA360FP2+OVA360022<div>Developer Studio</div> |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | The definition of the event trigger point attribute (on the Event object) will be altered to make it a required field (i.e., the field cannot be left blank/empty).&nbsp; | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | <span style="font-size:10pt;font-family:&quot;Times New Roman&quot;, serif;">Controller --&gt; Configuration --&gt; Controller --&gt; Triggered Events --&gt;</span><span style="font-size:10pt;font-family:&quot;Times New Roman&quot;, serif;">&nbsp;&nbsp;</span>Insert new &quot;Trigger Event&quot; --&gt; Do not enter Trigger Point&nbsp;name--&gt; Apply --&gt; Developer studio is not generating error and adding blank trigger event. |  | OVA360022 |  |  | FINDING | [6 empty] | 113643
39440 | FINDING | Event Trend: "Show Trace Value Cursor" is not working for DEC oscillography Events. | Bargaje, Prashant C EMR SYSS PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 1 | Gupta, Chandresh EMR SYSS PWS NOIDA | 2017-08-08 22:38 | [11 empty] | Gupta, Chandresh EMR SYSS PWS NOIDA | 2017-08-08 22:38 |  |  |  | 2017-07-17 16:36 |  |  |  | Jain, Yukta AUTOSOL PWS NOIDA | 2017-05-31 16:06 |  | &quot;Show Trace Value Cursor&quot; option in Table View tab of Event Trend is not working properly for DEC oscillography Events.<div>&quot;Show Trace Value cursor&quot; is showing Trace value cursor in Graph for initial few values in the list but not working for rest of the values.<br></div> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Operator Station/Trend/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation | OVA360022, 3.6.0 FP3, OPH360003 |  | OVA36022 &amp; FP03<div>Event Trend</div><div>DEC oscillography Events.<br></div><div><br></div> |  | Ovation for Windows | Ovation | Operator Station/Trend | Software | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Jain, Yukta AUTOSOL PWS NOIDA | Validation |  | YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP02+OVA360022, OPH360003<div>YJ: Issue fixed in&nbsp;&nbsp;Ov360 FP03+ OPH360005<br></div> | 7 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Trigger&nbsp;DEC oscillography Event --&gt; Launch in Event Trend --&gt; Go to Table View Tab --&gt; scroll down the list and try &quot;Show Trace Value cursor&quot; option. |  | OVA36022 & FP3 |  |  | FINDING | [6 empty] | 117109
39445 | FINDING | EIO: Adding/removing EIO node(s) and loading the OCR before a query/download/reboot causes an OCR failure. This must be documented. | Jain, Swati EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | USPITTFSService | 2017-10-31 11:53 | [11 empty] | USPITTFSService | 2017-10-31 11:53 |  |  |  | 2017-10-31 11:53 |  |  |  | Brown, Sean EMR SYSS PWS PITT | 2017-06-01 07:57 |  | When an EIO node is added or removed, the controller must be queried/downloaded/rebooted before a controller load may be performed.&nbsp; If the controller load is performed first, the controller will fail.&nbsp; This is in reference to Redundancy Mode = Standard.<br><br>Users must be made aware of this.<br> |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Controller/Third Party Communications/Documentation |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Wood, Thomas T AUTOSOL PWS PITT | Brown, Rick P EMR SYSS PWS PITT | Swartz, Mark EMR SYSS PWS PITT | [7 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | Controller/Third Party Communications | Documentation | Standard Release | 3.6.0 |  |  | Added to User Manual | 0 |  |  | Brown, Sean EMR SYSS PWS PITT | Validation |  | <p>More information required for the case of the removal of a remote node:&nbsp; If a remote node is in use (i.e., one or more points assigned to hardware on the node) and the node is removed via Ovation Developer Studio, will a simple query/download/reboot &quot;work&quot;?&nbsp; (Or is a query/download/clear required?)</p><p><br></p><p>I don't see how a node that is in use can be removed.&nbsp; &quot;Removed&quot; in the Description field refers to a node that had points and hardware assigned to it, but these were removed before the node was deleted.<br></p> | 18 |  | 2958100.75 | Cat 2 - Loss of Significant Functionality | [7 empty] | FP3_U0 |  |  | FINDING | [6 empty] | 119890
39446 | FINDING | FP3- online help of Ovation license Manager does not open by clicking view Help in the Ovation license Manager window. | Spillane, Donal AUTOSOL PWS PITT | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Spillane, Donal AUTOSOL PWS PITT | 2017-06-20 16:05 | [11 empty] | Spillane, Donal AUTOSOL PWS PITT | 2017-06-20 16:05 |  |  |  | 2017-06-20 16:05 |  |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | 2017-06-01 08:31 |  | FP3 Installed EWS - online help of Ovation license Manager does not open by clicking view Help in the&nbsp; Ovation license Manager window. |  |  |  |  | 0 |  |  |  |  | 0 |  | Ovation for Windows/Engineering Tools/Ovation Developer Studio/General/Software |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | [9 empty] | Implementation |  |  | All EWS drops of OV3.60-FP3 |  | Ovation for Windows | Ovation | Engineering Tools/Ovation Developer Studio/General | Software | Standard Release | 3.6.0 |  |  | Created SDR and Added Note to DIR | 0 |  |  | N, Thamaraiselvi AUTOSOL PWS NOIDA | Validation |  |  | 4 |  | 2958100.75 | Cat 3 - Loss of Some Functionality | [5 empty] | Developer studio-&gt;License-Licensing-Ovation license Manager window opens. Click on the help-view help. Online help does not open. |  | OVA360FP3_U0 |  |  | FINDING | [6 empty] | 114617
39461 | FINDING | Safety Shell-Editorial changes need to be done in SVTP section 5.5 “Controller Support” | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:35 |  |  |  | 2018-01-10 04:32 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-06-04 06:57 |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 8pt 0in;"><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Following editorial changes needs to be done&nbsp;section 5.5 “Controller Support”</span></p><p style="margin:0in 6.95pt 8pt 0in;"><b><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">1.</span></u></b><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> </span></b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">In Test 5.5.1,<b> </b></span><font face=Arial size=3>Item -3 of section “Goal of the test” needs to be modified </font></p><font face="Times New Roman" size=3> </font><p align=left style="margin:0in -40.5pt 0pt 0in;text-align:left;"><span style="color:windowtext;font-family:&quot;Times&quot;,serif;font-size:12pt;">Statement in Item-3</span><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;"> say “High Integrity points are assigned to non-High Integrity DDB (from receiver perspective) on receivers OCR400, Virtual OCR1100”</span></p><font face="Times New Roman" size=3> </font><p align=left style="margin:0in -40.5pt 0pt 0in;text-align:left;"><span style="color:windowtext;font-family:&quot;Times&quot;,serif;font-size:12pt;">It is observed during testing that</span><font face=Calibri><font size=3>&nbsp;in OCR 400 and Virtual 1100,&nbsp;receiving <span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">High Integrity DDB in ddbStatusAll are marked by having additional counters for faults.</span>&nbsp;</font></font></p><font face=Calibri><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"><p style="margin:0in 0.1in 0pt 0in;">Hence, statement may be revised as <span style="font-family:&quot;Calibri&quot;,sans-serif;"><strong><em>“</em></strong></span><b style=""><i><span style=""><font face=Times>High Integrity points are assigned to DDB with High Integrity DDB structure (having additional counters) on receivers OCR400, Virtual OCR1100.”.</font></span></i></b></p><font face=Calibri><p style="margin:0in 0.1in 0pt 0in;"><br></p></font></span></font><p style="margin:0in 0.1in 0pt 0in;"><b><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">2.</span></u></b><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> </span></b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">In <b>Test case 5.5.1</b>- following items in section</span><span style="line-height:107%;font-size:10pt;"><font face=Arial> “<b>procedure for verification that shall be executed for Drop31/81, Drop32/82, Drop41/91 and Drop11</b>.” needs modification.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0.1in 0pt 0in;"><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">&nbsp;</span></b></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0.1in 0pt 0in;"><b><i><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">2. a</span></u><font face=Arial size=3>:</font></i></b><i><font size=3><font face=Arial><span>&nbsp; </span><span>&nbsp;</span></font></font></i><b><span style="color:black;line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Item -7</span></b><span style="color:black;line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> needs to be updated with steps used during testing for running SidToPN.exe.</span><b><i><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> <br> </span></u></i></b><span style="color:black;line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Item-7 say</span><i><font face=Arial size=3> “</font></i><i><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Run SidToPN application from cmd as follows SidToPN “C:\tmp\sids.txt” “C:\tmp\sidsWithPN.txt”.”</span></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in -58.5pt 0pt 0in;"><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">During testing SidToPN.exe needs to run manually from C:\Ovation\OvationBase instead of cmd.</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in -58.5pt 0pt 0in;"><span style="color:black;line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Hence, Item -7 needs to be updated with following steps used for running SidToPN.exe</span></p><font face="Times New Roman" size=3> </font><p style="margin:0in -58.5pt 0pt 0in;"><font size=3><font face=Arial><b><i>“</i></b><i>Run </i></font></font><b><i><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">SidToPN</span></i></b><i><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> application manually from location </span><font face=Arial><b><font size=3>C:\Ovation\OvationBase</font></b><font size=3> and load the file </font><b><font size=3>sid.txt</font></b><font size=3> then click for save the result file.</font></font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 0pt 0in;"><i><font face=Arial><font size=3>Result <b>SIDToPN_Result.csv</b></font><font size=3> saved at location </font><b><font size=3>C:\Ovation\OvationBase</font></b><font size=3>.”</font></font></i></p><font face="Times New Roman" size=3> </font><p style="margin:0in 6.95pt 8pt 0in;"><font face=Arial size=3>&nbsp;</font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0.1in 0pt 0in;"><b><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">2.b.</span></u></b><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> Item-10.b</span></b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">. says “Broadcast frequency settings shall match for points and DDB”.</span></p><font face="Times New Roman" size=3> </font><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;">During testing it is observed that verification of <span>&nbsp;</span>Broadcast frequency settings can be done only for the DDB in originating drop, not on the receiving drop. </span></p><font face="Times New Roman" size=3> </font><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;">Hence, a note may be added in Item-10.b. that “<em>Note: Broadcast frequency settings verification shall be done&nbsp; for originating DDB.&quot;</em></span></p><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;"><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><br></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><b><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">2.c.</span></u></b><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> Item-10.c.iii.</span></b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> says “<i>OCR400 receiving High Integrity point from OCR1100 shall be assigned to non-High Integrity received DDB</i>.”</span></p><font face="Times New Roman"><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span><font face=Times>During testing, it is observed via ddbStatusAll command that OCR 400&nbsp;receiving High Integrity DDB from OCR1100 are marked by having additional counters for faults.&nbsp;<br> Hence, statement <b>Item-10.c.iii</b>. needs to be revised as “<i>OCR400 receiving High Integrity point from OCR1100 shall be assigned to received DDB with High Integrity structure.”.</i></font></span></p></font><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"><br></font></p></span><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;"><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><b><u><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">2.d.</span></u></b><b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> Item-10.c.iv.</span></b><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"> says “<span style="display:none;"></span></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> </font><span style="font-family:&quot;Times&quot;,serif;font-size:12pt;">Virtual OCR1100 receciving High Integrity point from OCR1100 shall be assigned to non-High Integrity received DDB</span></p><font face="Times New Roman"><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span><font face=Times>During testing, it is observed via ddbStatusAll command that Virtual OCR1100&nbsp;receiving High Integrity DDB from OCR1100 are marked by having additional counters for faults.&nbsp;</font></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"> <span><font face=Times>Hence, statement in <b>Item-10.c.iv.</b> &nbsp;needs to be revised as “<em>Virtual OCR1100 receiving High Integrity point from OCR1100 shall be assigned to received DDB with High Integrity structure.”.</em></font></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"> <span><font face=Times><br>Additional clarification&nbsp;for <b>Item: 2.c and 2.d.</b></font></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"> <font face=Times><u><span>OCR400 and VC1100 do not check for High Integrity</span></u><span>:</span></font></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"> <span><font face=Times>High Integrity DDB originating in drop102 (EWS with custom ddb driver) receiving by drops41/91 (OCR 400) and drop11(VC1100). Following verified for VC1100 and OCR400 via ddbStatusAll command for receiving ddb: DDBs are marked by having additional Error counters for faults. Those Error counters do not get incremented upon injecting error (using Error injection tool on originating drop102) in the HI DDB.</font></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"> <br></p></font><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span><strong><u>3.</u> </strong>In description section of</span><span style="font-family:&quot;Times&quot;,serif;"> Test 5.5.22 </span><span style="color:black;line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Point name needs to be modified.</span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> </font><span style="font-family:&quot;Times&quot;,serif;">“<em>D31_S_HI_FO_ASSIGNEDOUT</em>” needs to be replaced with “<em>D31_S_HI_FO_CHANGEDOUT</em>” </span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> </font><span style="font-family:&quot;Times&quot;,serif;">“<em>D31_F_HI_FO_ASSIGNEDOUT</em>” needs to be replaced with “<em>D31_F_HI_FO_CHANGEDOUT</em>” </span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> <br></font></p><p style="margin:0in 6.95pt 0pt 0in;"><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"><strong><u>4.</u></strong> <span style="color:black;">&nbsp; </span></span><span style="font-family:&quot;Times&quot;,serif;">Test 5.5.18:&nbsp;Verifying the scenario for Invalid CRC for received DDB frame.&nbsp;&nbsp;<br>&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; <span style="color:black;">In description section,&nbsp;&nbsp;</span>Statement&nbsp;for expected result says&nbsp; &quot;<em>Verify that the ddbStatusAll command show&nbsp;bad source counter increased&nbsp;by 5</em>&quot; needs to be corrected as </span></p><p style="margin:0in 6.95pt 0pt 0in;"><span style="font-family:&quot;Times&quot;,serif;">&nbsp;&nbsp;&nbsp;&nbsp;&nbsp; &quot;<em>Verify that the ddbStatusAll command show&nbsp;<span style="color:black;font-family:&quot;Times&quot;,serif;font-size:12pt;">bad ss checksum&nbsp;</span>counter increased&nbsp;by 5</em>&quot;</span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> </font><span style="font-family:&quot;Times&quot;,serif;"><br></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span style="font-family:&quot;Times&quot;,serif;"><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;"><strong><u>5.</u>&nbsp; </strong>Description section of Test case 5.5.54, 5.5.54.a.2, 5.5.54.b.2, 5.5.54.c.2, 5.5.55, 5.5.55.a.2, 5.5.55.b.2, 5.5.55.c.2</span></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><span style="font-family:&quot;Times&quot;,serif;"><span style="line-height:107%;font-family:&quot;Times&quot;,serif;font-size:12pt;">Contain a statement &quot;<em>injection of repeat message</em>&quot; is mentioned that is not correct,&nbsp;it should be corrected as &quot;<em>injection of&nbsp;Out of Sequence/less than&nbsp;messages</em>&quot;&nbsp;</span></span></p><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman"> <br></font></p></span><p align=left style="margin:0in 0.1in 0pt 0in;text-align:left;"><font face="Times New Roman" size=3><br></font></p> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | [10 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC &gt;&nbsp;Please continue testing with the&nbsp;resolutions proposed in the Description box. <br></font><font size=3> Note clearly in&nbsp;your test record that you are using the proposed resolutions. <br> The SVTP should be modified with these changes at the end of the project.</font></span></p><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><strong>VP&gt; Will fix in SVTP_rev1.5.</strong></font></span></font></span></p><font face="Times New Roman" size=3> </font> | 15 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122426
39462 | FINDING | Safety Shell SVTP- Section 5.5- Control logic for Quality monitoring of LP point needs minor changes. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 0 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:36 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:36 |  |  |  | 2018-01-10 04:32 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-06-04 08:32 |  | <font face=Arial><font size=3><p style="margin:0in 0in 8pt;"><span style="line-height:107%;">Safety Shell SVTP- Section 5.5- Control logic for Quality monitoring of LP point needs minor changes.</span></p></font></font><p style="margin:0in 0in 8pt;"><font face=Arial><font size=3>In section <b style="">Configuration for testing Controller receiver function for High Integrity LD and LP points”, </b></font><font size=3>existing Control logic for Quality monitoring good for LD point. </font><span style="line-height:107%;"><font size=3>Control logic for Quality monitoring of LP point needs following mentioned changes.</font></span></font></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><u><span style="line-height:107%;"><font face=Arial size=3>Control logic for Quality monitoring of LP point</font></span></u></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial size=3>The verification of the “quality” will be done by QUALITYMON. The QUALITYMON algorithm input will be connected to the page connector who pass the value of originated point (in drop102). It will be configured to set output as 1 in case the input quality is ‘Not good’. Output of QUALITYMON will be high when Input point go Timed out.</font></span></p><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial size=3>Output of the QUALITYMON algorithm will be connected to SOFTSOE algorithm which will generate message on input value change from 0 to 1.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial><font size=3>Existing Control logic for Quality monitoring may be renamed to <u>Control logic for Quality monitoring of LD point.</u></font><font size=3> And, above described </font><u><font size=3>Control logic for Quality monitoring of LP point</font></u></font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial size=3>may be added to the section.</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial size=3>&nbsp;</font></span></p><font face="Times New Roman" size=3> </font><p style="margin:0in 0in 0pt;"><span style="line-height:107%;"><font face=Arial><font size=3>Affected test cases: <b style="">Test case 5.5.58</b></font><font size=3> and </font><b style=""><font size=3>Test case 5.5.59</font></b><font size=3> </font></font></span></p><font face="Times New Roman" size=3> </font> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech |  | Gupta, Chandresh EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA |  |  |  |  | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC &gt;&nbsp;Please continue testing with the&nbsp;resolution proposed in the Description box. <br></font><font size=3> Note clearly in&nbsp;your test record that you are using the proposed resolution. <br> The SVTP should be modified with these changes at the end of the project.</font></span></p><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><strong>VP&gt; Will fix in SVTP_rev1.5.</strong></font></span></font></span></p><font face="Times New Roman" size=3> </font> | 6 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122427
39463 | FINDING | Safety Shell-SVTP- Test case 5.2.13, Verification procedure needs to be enhanced. | Pandey, Vijay EMR SYSS PWS NOIDA | Closed | [10 empty] | 35 | FINDING |  |  |  |  | 2 | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:36 | [11 empty] | Pandey, Vijay EMR SYSS PWS NOIDA | 2018-01-10 04:36 |  |  |  | 2018-01-10 04:32 |  |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | 2017-06-04 11:45 |  | <font face="Times New Roman" size=3> </font><font face=Times><span><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>&nbsp;</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><font size=3><span style="color:black;font-family:&quot;Times&quot;,serif;">Safety Shell-SVTP- Test case 5.2.13, </span><font face="Times New Roman"><span style="">Verification procedure needs to be enhanced</span></font><span style="font-family:&quot;Times&quot;,serif;">. </span></font></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="font-family:&quot;Times&quot;,serif;"><font size=3>&nbsp;</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="font-family:&quot;Times&quot;,serif;"><font size=3>Test case Verifying that Ovation Drop will report Consistency Check Error in case it originates High Integrity points configured to Aperiodic frequency.</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>&nbsp;</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="font-family:&quot;Times&quot;,serif;"><font size=3>To verify the test case scenario following steps performed, </font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Times&quot;,serif;">Export the Database that configured with Aperiodic points (Non-High Integrity). </span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Times&quot;,serif;">Modify the exported file manually to make aperiodic point as High Integrity point.</span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Times&quot;,serif;">Import the modified exported file back to the system. </span></p></li><li style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Times&quot;,serif;">After Import, verify in Developer Studio that consistency error appears upon loading or downloading the drop in which aperiodic point is configured with High Integrity configuration.</span></p></li></ol><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:36.9pt;"><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>&nbsp;</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:0.25in;"><span style="font-family:&quot;Times&quot;,serif;"><font size=3>Validation Observation</font></span><span style="font-family:&quot;Times&quot;,serif;"><font size=3>: Import operation gives warning message “<b><i>Attribute BROADCAST FREQUENCY cannot be modified unless system is in offline mode</i></b></font><font size=3>” for point which attribute was modified. For reference screenshot of Import session is attached.<br></font><font size=3> This warning message is expected.</font><span style=""><font size=3>&nbsp; </font></span><font size=3>This scenario is similar to modification of frequency for a point that is not allowed when system with Offline mode disabled. This consistency error scenario can be verified only through addition of steps for making studio </font><b><font size=3>Offline Mode</font></b><font size=3> enable.</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><p style="margin-right:0.25in;"><span style="font-family:&quot;Times&quot;,serif;"><font size=3>Test case need enhancement by verification of following scenarios.</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font></p><ol style="list-style-type:decimal;direction:ltr;"><li style="color:black;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="font-family:&quot;Times&quot;,serif;">Import operation using modified file gives warning “<b><i>Attribute BROADCAST FREQUENCY cannot be modified unless system is in offline mode</i></b>” for the point that was modified in exported file.</span></p></li><li style="color:black;font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;"><p style="color:rgb(0, 0, 0);font-family:&quot;Times New Roman&quot;,serif;font-size:12pt;font-style:normal;font-weight:normal;margin-top:0in;margin-bottom:0pt;"><span style="color:black;font-family:&quot;Times&quot;,serif;">Import operation using further modified file (added step for enabling the system attribute OFFLINE_MODE so that Import can be performed without warning message and verification for the scenario “Ovation Drop will report Consistency Check Error in case it originates High Integrity points configured to Aperiodic frequency” can be done.</span></p></li></ol><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font><span style="color:black;font-family:&quot;Times&quot;,serif;"><font size=3>Proposed enhancement procedure “Test5.2.13_Enhanced procedure for verification of High Integrity points configured to Aperiodic frequency.docx&quot; is attached.</font></span></p><p style="margin:0in 36.9pt 0pt 0in;"><font face="Times New Roman" size=3> </font><br></p></span><p style="margin:0in 36.9pt 0pt 0in;"><br></p></font><p style="margin:0in 36.9pt 0pt 0in;"><br></p> |  |  |  |  | 0 |  |  |  | Verified SRF2228_SafetyShell_SVTP_rev1.5.docx. Finding is closed. | 0 |  | Ovation for Windows/General/SVTP/STP |  |  | 32 | FINDING\Release 1\Sprint 1 |  |  | FINDING | Gupta, Chandresh EMR SYSS PWS NOIDA | Goyal, Ashish EMR SYSS PWS NOIDA | Sharma, Satish AUTOSOL PWS NOIDA | Capani, Innocenzo AUTOSOL PWS PITT | Long, Michelle J External Artech | [5 empty] | Implementation |  |  |  |  | Ovation for Windows | Ovation | General | SVTP/STP | Standard Release | 3.6.0 |  |  | Confirmed to be fixed | 0 |  |  | Pandey, Vijay EMR SYSS PWS NOIDA | Validation |  | <font face="Times New Roman" size=3> </font><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3>IC &gt;&nbsp;Please continue testing with the&nbsp;resolutions proposed in the Description box and in the attachment. <br></font><font size=3> Note clearly in&nbsp;your test record that you are using the proposed resolutions. <br> The SVTP should be modified with these changes at the end of the project.</font></span></p><p style="margin:0in 0in 8pt;"><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><span style="color:black;font-family:&quot;Calibri&quot;,sans-serif;"><font size=3><strong>VP&gt; Will fix in SVTP_rev1.5.</strong></font></span></font></span></p><font face="Times New Roman" size=3> </font> | 9 |  | 2958100.75 | Cat 4 - Cosmetic Problem | [7 empty] | OVA360FP2 |  |  | FINDING | [6 empty] | 122428