Ovation 
SRF 2347
Standalone Controller & Tools

Software Validation Test Procedure

Software Validation Test Procedure Revision 1.4

SW Version: Standalone Controller & Tools

Start Date:        ____________

Tester Name:    ____________

Product Development Department

Emerson Automation Solutions

Power & Water Solutions

200 Beta Drive

Pittsburgh, PA 15238

This document contains information that is proprietary to Emerson Automation Solutions; it is intended for internal Emerson Automation Solutions use only. This document, and the information that it contains, are to be held against public access and should not be disclosed or transmitted, in whole or in part, without the written authorization of Emerson Automation Solutions.

Document Revisions Index

| Rev | Date | Section | Description | Reviser |
| --- | --- | --- | --- | --- |
| 1.0 | 05-May-2022 | All | Original. | DJ |
| 1.1 | 10-Jun-22 | All | Implemented comments from Mark and Scott | DJ |
| 1.2 | 11-Jul-22 | All | Implemented comments from Mark and Lisa | DJ |
| 1.3 | 20-Jul-22 | 5.4.1,5.9.2 | Implemented comments from Lisa and Mark | DJ |
| 1.4 | 26-10-22 |  | Added/updated tests for Subscription license and APC | DJ |

Table Of Contents

1.0	SVTP Identifier	9

2.0	Purpose	9

3.0	Approach	9

4.0	Features To Be Tested And Pass/Fail Criteria	10

5.0	Procedure Steps	12

5.1	Installation	13

5.2	Licensing	15

5.3	Testing constraints and limitations of Standalone Controller & Tools	17

5.4	Testing external interfaces to Standalone Controller & Tools	19

5.5	Performance Testing	32

5.6	Testing hardware and software environment	34

5.7	Security testing	35

5.8	Documentation	36

5.9	Testing Functional Specification	37

5.9.1	Controller	37

5.9.2	Tools	42

5.9.3	HMI	63

5.9.4	Communication Protocols testing	66

5.10	IEC62443 4-2 Security Level 1 testing	67

5.11	Miscellaneous tests	83

6.0	Approvals	84

7.0	Test Sign-Off Form	86

- SVTP Identifier

This document is the  SRF 2347 Software Validation Test Procedure.

- Purpose

The purpose of this test procedure is to detail the tests, which are to be done to validate the above mentioned software functionality.

- Approach

The test will be conducted as described below.

- An Ovation database must be created. This database will contain points necessary to exercise the features listed in section 4.

- Perform appropriate tests as listed in section 4. Section 5 details these tests.

- Any problems found will be reported as findings.

- As needed or upon completion, a status shall be generated by the validators and sent to the appropriate personnel via email.

- The standard documentation on the company Intranet will be referenced throughout the testing. Any recommended changes will be reported as findings for the Product Documentation Group.

- Features To Be Tested And Pass/Fail Criteria

Please refer to the appropriate documentation for details on the features to be tested. Refer
to section 5.0 for details on the testing of these features. If the features don’t function as described, the test fails. The results should be marked by “Pass”, “Fail”, or “NA” (not applicable).

  - Installation

  - Licensing

  - Testing constraints and limitations of Standalone Controller & Tools

  - Testing external interfaces to Standalone Controller & Tools

    - Human-Machine Interfaces

    - Software Interfaces

    - Hardware Interfaces

  - Performance Testing

  - Testing hardware and software environment

  - Security testing

  - Documentation

  - Testing Functional Specification

    - Controller

    - Tools

    - HMI

    - Communication Protocols

  - IEC62443 4-2 Security Level 1 testing

  - Miscellaneous Tests

- Procedure Steps

Test Configuration:

The following software configuration is needed to perform the tests in this procedure.

- Different version of Window 10

- Different type of Controllers

- Ensure that the associated software packages are at the proper released level.

Test Setup:

The following test setup must be performed before this test procedure can be run.

- Single SAC station & SAC Controller

- Multiple SAC station & Single SAC Controller

- Ensure that the system has database (points) applicable to the features being tested.

  - Installation

SRF Notes The computer on which the tool for Standalone Controllers is installed will not be considered an Ovation drop – and installation of the software will not be permitted on an Ovation drop. The installation of the tools for Standalone Controller will include the installation of Microsoft SQL Server Express, which will be used to configure a Standalone Controller.

| - Test : Installation of Standalone Controller & Tools software Installation of Standalone Controller & Tools software on an non-server grade, non Ovation & non domain machine. Record the date, initials for each installation done. Record any issues as findings. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Ensure that the Machine on which Ovation Standalone & Tools software to be installed is a non-server grade, non Ovation & non domain machine |  | P/F/F#/NA: |
| - Verify correct license is available before installation. |  | P/F/F#/NA: |
| - Validate installation steps are correct and Record any issues or descrepencies as findings. Verify that installation succeeded without any error or warning |  | P/F/F#/NA: |
| - Launch Ovation Standalone & Tools software GUI, verify that the tool launched successfully, and no error or warning appeared. |  | P/F/F#/NA: |
| - Verify that the Ovation Standalone & Tools will require license activation. |  | P/F/F#/NA: |
| - Verify Ovation Standalone & Tools should not work without licenses. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Uninstallation of Standalone Controller & Tools software Ensure that Uninstallation of Standalone Controller & Tools software can be done without any issues. Record the date, initials for each installation done. Record any issues as findings. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Uninstall Standalone Controller & Tools software to check that there is no issue in un-installation. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Installation of Standalone Controller & Tools software update Ensure that new updates of the SW can be installed correctly. Record the date, initials for each installation done. Record any issues as findings. |  |  |
| --- | --- | --- |
| Date(s): | Initials: | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Clean installation of Standalone Controller & Tools software Perform the fresh installation (reload OS or on machine where software wasn’t installed previously) of Standalone Controller & Tools software and check that no error is observed |  |  |
| --- | --- | --- |
| Date(s): | Initials: | P/F/F#/NA: |
| Comments: |  |  |

  - Licensing

| SRF Notes The Standalone Controller & Tools present some new aspects related to licensing as compared to a traditional Ovation system. In a traditional system, the licensing information is generated and entered on the Database Server. In a Standalone configuration, however, there is no Database Server. Because of this, licensing will be done differently. - A license will be needed for the instance of the tools running on the user’s laptop/PC. - A license will be needed for the Standalone Controller - Licensing for the APC toolkit will be associated with the controller - Licensing for SCADA/CPS protocols will be associated with the controller - Locking codes for the controller license will be generated based upon the controller MAC address - The OCC100 point tiers for the OCC100 (OMC100 future) version will be implemented the same as in a Traditional Ovation System. |  |  |
| --- | --- | --- |
| - Test : Verify PC based and Controller MAC ID based licensing required for Standalone Controller & Tools |  |  |
| Date(s): | Initials: |  |
| - Verify that able to get Laptop/PC based locking code by running license.exe from C:\Ovation\Ovation base. |  | P/F/F#/NA: |
| - Verify that PC based license is needed to run tools like Control Builder, Graphics builder etc. Once license is installed user should be able to use these tools without any kind of license related issues |  | P/F/F#/NA: |
| - Verify that able to get Controller MAC id based locking code by running license.exe from Ovation Developer studio |  | P/F/F#/NA: |
| - Verify that Controller MAC id based license is needed for the Standalone Controller. Verify that after installation of license, from licensing perspective features are working as expected without any kind of license related issues. |  | P/F/F#/NA: |
| - Verify that able to work with Database obtained from a different SAC station (as that station have different license as PC is different) and facing no issue related to licensing |  |  |
| Comments: |  |  |

| - Test : Verify that subscription based tools (For SAC tools, Ovation Developer studio, Control builder, Graphic builder tools) license works as per subscription conditions |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Veify that able to install subscription based tools license for SAC(For SAC tools, Ovation Developer studio, Control builder, Graphic builder tools). |  | P/F/F#/NA: |
| - Verify that subscription based tools license expires as per expiry date |  |  |  | P/F/F#/NA: |  |  |
| - Verify that able to install Perpetual (never expiry) and it works properly |  |  |  |  |  |  |
| - Verify that by changing time zone, regional setting etc (which changes date format to mm/dd to dd/mm or vice versa) doesn’t effect License working |  |  |  |  |  |  |
| - Verify that Setting the date ahead of SAC station doesn’t effect License working |  |  |  |  |  |  |
| - Verify that setting date back of SAC station will be treated as tempering and license shouldn’t work with back dated SAC station |  |  |

| - Test : Verify licensing requirements for using APC toolkit software with Standalone Controller & Tools software |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that for APC only OvSCST software is required and no additional software (e.g. APC Toolkit) is required |  | P/F/F#/NA: |
| - Verify that license obtained on the basis of Controller’s MAC id based locking code is installed successfully and allow Adavanced alorithms to be available in Control builder |  |  | P/F/F#/NA: |  |
| - Verify that only licensed advanced algorithms are available for use in Control builder |  |  | P/F/F#/NA: |  |

| - Test : Verify licensing requirements for using CPS protocols with Standalone Controller & Tools software |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Get the required CPS protocols license based on SAC Controller MAC id and try to install CPS3.3 software on the machine where Standalone software is installed. |  | P/F/F#/NA: |
| - Install the license and ensure that from licensing perspective CPS protocols is working as expected. |  | P/F/F#/NA: |

| - Test : Verify OCC100 point tiers based licensing requirements for using OCC100 Controller with Standalone Controller & Tools software |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that OCC100 point tiers based licensing is required for using OCC100 Controller and its associated with controller(based on Controller MAC id) license. |  | P/F/F#/NA: |
| - Install the license and ensure that OCC100 point tiers based licensing is working as expected from licensing perspective |  | P/F/F#/NA: |

| - Test : Verify tier based OCR3000 Licensing suppport |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that able to install tier based OCR3000 License and it shows correct information |  | P/F/F#/NA: |
| - Verify that OCR3000 tier license works as per below table- Standalone OCR3000 Tier; Advertised I/O Point Limit; Warning; Error 125%. 1; 500; 500; 625. 2; 1000; 1000; 1250. 3; 2000; 2000; 2500. 4; 3000; 3000; 3750. 5; 3000+; n/a. | P/F/F#/NA: |

  - Testing constraints and limitations of Standalone Controller & Tools

| SRF Notes The main limitation of the Standalone Controller & Tools is that it is intended for a single controller. The controller will not be able to receive Ovation points from other Ovation drops. Runtime data could be shared between 2 or more Standalone Controllers by establishing a datalink connection (i.e. Modbus) between the Standalone Controller. The Tools used for programming a Standalone Controller are NOT compatible with programming controllers that are already a part of an Ovation System. |  |  |
| --- | --- | --- |
| - Test : Verification of DataLink connection between the Standalone Controller using Third-Party I/O drivers Determine if Runtime data could be shared between 2 or more Standalone Controllers by establishing a datalink connection (i.e. Modbus) between the Standalone Controller |  |  |
| Date(s): | Initials: |  |
| - Configure two standalone Controller setups with OCC100 or OCR3000. |  | P/F/F#/NA: |
| - Establishconnection between these two Standalone Controllers using Third-Party I/O drivers (i.e. Modbus) |  | P/F/F#/NA: |
| - Verify if Runtime data could be shared between these 2 SAC Controller by using points originating in other SAC controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verification of DataLink connection between the Standalone Controller using the Embedded Ethernet Links provided by the CPS Determine if Runtime data could be shared between 2 or more Standalone Controllers by establishing a datalink connection (i.e. Modbus) between the Standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure two standalone Controller setups with OCC100 or OCR3000. |  | P/F/F#/NA: |
| - Establish connection between these two Standalone Controllers using the Embedded Ethernet Links provided by the CPS and verify if runtime data could be shared |  | P/F/F#/NA: |
| - Verify if Runtime data could be shared between these 2 SAC Controller by using points originating in other SAC controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verification that other than Standalone Controller, no other drop can be created on OvSACS setup |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try to insert drop in the hierarchy but option for the same shouldn’t be available. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that the tools used for programming a Standalone Controller are NOT compatible with programming controllers that are already a part of an Ovation System. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Install Standalone Controller tools on an Ovation EWS Drop |  | P/F/F#/NA: |
| - Try connecting and programming any existing Controller drop on this Ovation setup using Standalone Controller tools. Standalone Controller tools shouldn’t be compatible for programming Ovation Controller drop. |  | P/F/F#/NA: |
| Comments: |  |  |

  - Testing external interfaces to Standalone Controller & Tools

The Standalone Controller & Tools have several external interfaces that are described below.  These are not external interfaces only, and do not include the internal interfaces used within the software to communicate between the Standalone Controller & Tools.

    - Human-Machine Interfaces

| SRF Notes The Standalone Controller & Tools will utilize the same type of Human-Machine Interfaces used in a traditional Ovation system. This includes: - Ovation Operator Graphics - Ovation Developer’s Studio - Ovation Alarm System - Ovation Control Builder - Ovation Graphics Builder - Ovation Signal Diagram Viewer - Ovation Trend - Point Information - Point Review - Ovation Machine Works - Sensor Calibrate - Controller Diagnostics |  |  |
| --- | --- | --- |

      - Ovation Operator Graphics

| - Test : Verify the basic functionalities of graphics and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD | Slow OPP LP |  | Slow OPPDA | Slow OPPDD | Slow OPPDP | DU |  |
| a-Scan Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| b-Enter Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| c-Scan On |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| d-Go into Alarm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e-Alarm Ack |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f-Alarm Reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| g-Alarm Chk Off |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| h-Alarm Chk On |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| i-HW Value Update |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| j- Bad HW Value |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Test: Using dual Opcons display 8 different Custom Graphics, 4 on one Opcon and 4 on the other. Verify correct operation. NOTE: for Ovation 3.2.0 and newer, display 16 total. 8 on one Opcon and 8 on the other. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  | Pass/Fail |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| - Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# |  |  |  |  |  |
| MASTATION | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: |  | Other Basic Functionality: |
| XMA2 | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias (NA for Sol Sys): | Digital Entry Output : |  | Other Basic Functionality: |
| SETPOINT | NA | NA |  | Raise/Lower Output: | NA |  |  | Other Basic Functionality: |
| PID | NA | NA |  | NA | NA | NA |  | Other Basic Functionality: |
| Comments: |  |  |  |  |  |  |  |  |

| - Test: Run the listed tests using custom graphics. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Findings# |  |  |  |
|  | KEYBOARD | HIGHLOWMON | TRANSFER | ONESHOT |  |
| Basic Functionality |  |  |  |  |  |
| Comments: |  |  |  |  |  |

      - Ovation Developer Studio

| - Test : Verify that the basic functionalities of Ovation Developer Studio and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Alarm System

| - Test: Run the listed tests using while monitoring the Alarm List. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |  |
| Operation | Fast OPP LA | Fast OPPLD |  | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD |  | Slow OPPDP | DU |  |
| a- Cause point to go into Alarm. Verify the alarm appears on Alarm List |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| b- Cause analog point to have an incremental alarm Cause Packed points to have other bits go into alarm. Verify the alarm changes appears on the Alarm List |  | N/A |  |  |  |  | N/A |  |  | N/A |  |  |  | N/A |  |  |  |  |
| c- Cause point to return from Alarm. Verify the return appears on Alarm List |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| e-Alarm Ack |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| f-Alarm Reset |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NA |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Test: Fail/Reboot Primary Controller drop and make secondary drop is in Control. Verify if respective alarm comes in alarm list |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Test: Fail/Reboot Controller drop and check if respective alarm comes in alarm list |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| - Test : Verify other functionalities of Ovation Alarm System and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Alarm avlanche- Generate very high number of alarms (around 1000 alarms ) and check that able to see those alarms in alarm ist |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Alarm avlanche- Generate very high number of alarms (around 100 alarms per second) and check that able to see those alarms in alarm ist |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Control builder

| - Test : Verify basic functionality of Ovation Control builder and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test: Run the listed tests using sheets. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# Pass/Fail |  |  |  |  |  |
| XPID | Manual/Auto/Cascade: | Raise/Lower Setpoint: |  | Raise/Lower Output: | Digital Entry Setpoint: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| MASTATION | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| XMA2 | Manual/ Auto: | Raise/Lower Bias |  | Raise/Lower Output: | Digital Entry Bias: | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| SETPOINT | NA | NA |  | Raise/Lower Output: | NA | Digital Entry Output: | Change Tuning Contants: | Other Basic Functionality: |
| PID | NA | NA |  | NA | NA | NA | Change Tuning Contants: | Other Basic Functionality: |
| Comments: |  |  |  |  |  |  |  |  |

| - Test: Run the listed tests using sheets. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  | Findings# |  |  |  |  |  |
|  | KEYBOARD |  | HIGHLOWMON |  | TRANSFER | ONESHOT |  |  |
| Basic Functionality |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |
| - Test: The Control Logic Navigation application – Verify the basic functionality of the Control Logic Navigator. |  |  |  |  |  |  |  |  |
| Date: |  | Initials: |  | Pass/Fail/NA: |  |  | Findings # |  |
| Comments: |  |  |  |  |  |  |  |  |

| - Test : Verify that able to save the Control sheet in Standalone Controller using “save the database in standalone controller” SAC operation and connect (using Standalone Controller database) fetches down Control sheet to Standalone Station |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create/Import a new Control sheet |  | P/F/F#/NA: |
| - Save the Control sheet using “save the database in standalone controller” SAC operation in standalone Controller |  | P/F/F#/NA: |
| - Disconnect the Controller (using normal disconnect which deletes database from SAC station) |  | P/F/F#/NA: |
| - Connect to SAC Controller using option to use standalone Controller database |  | P/F/F#/NA: |
| - Verify that newly created Control sheet is available |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Graphic builder

| - Test: Verify the Basic Functionality of the Graphic Builder Mark each test result as “P” or “F” (Pass/ Fail). Note : This test should be marked as NA for Solaris Windows Opcons. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date: | Initials: | Findings# |  |  |  |
| a) verify an existing graphic can be edited and saved. |  |  |  |  | Pass/Fail: |
| b) verify that the same graphic can be compiled and loaded. |  |  |  |  | Pass/Fail: |
| c) verify that the same graphic displays and updates correctly. |  |  |  |  | Pass/Fail: |
| d) Create a new graphic and repeat tests a, b, and c. |  |  |  |  | Pass/Fail: |
| Comments: |  |  |  |  |  |
| - Test: Verify screen copies of the following items can be done. |  |  |  |  |  |
| a) Custom Graphics |  |  | P/F/F#: | Initials, Date: |  |
| b) Error Screen |  |  | P/F/F#: | Initials, Date: |  |
| Comments: |  |  |  |  |  |

| - Test : Verify that able to save the graphic in Standalone Controller using “save the database in standalone controller” SAC operation and connect (using Standalone Controller database) fetches down graphics to Standalone Station |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create/Import a new graphic |  | P/F/F#/NA: |
| - Save the graphic using “save the database in standalone controller” SAC operation in standalone Controller |  | P/F/F#/NA: |
| - Disconnect the Controller (using normal disconnect which deletes database from SAC station) |  | P/F/F#/NA: |
| - Connect to SAC Controller using option to use standalone Controller database |  | P/F/F#/NA: |
| - Verify that newly created graphic is available |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify other functionalities of Ovation Graphic builder and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Signal Diagram Viewer

| - Test : Verify that the basic functionalities of Ovation Signal Diagram Viewer and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Trend

| - Test: Perform Live Trends using the point types listed. Verify the Trend Values and Trend Timestamps are both correct. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | Initials: |  |  |  | Findings# |  |  |  |  |  |  |  |  |  |  |  |
|  | Fast OPP LA | Fast OPPLD | Fast OPPLP | Fast OPPDA |  | Fast OPP DD | Fast OPP DP | Slow OPP LA | Slow OPP LD |  | Slow OPP LP | Slow OPPDA | Slow OPPDD | Slow OPPDP |  |  |
| Values OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Timestamps OK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Trend configuration –change default values for analog/digital points (in Admin Tool for Solaris, in Studio-Configuration-Trend-Trend default for Windows), check the same in trend window of operator station. Verify correct operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Test: Display 4 different Live Trends on the available windows of the Opcon. Verify correct operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| - Test: Tabular Trend. Verify the Trend Values and Trend Timestamps are both correct. Mark each test result as “P” or “F” (Pass/ Fail). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Trend Values Pass/Fail/F#: |  |  |  |  | Trend Timestamps Pass/Fail/F#: |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Test:Trend Groups : verify correct operation of live and historical trend groups. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: | Initials: |  |  |  | Pass/Fail |  |  |  |  | Findings# |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| - Test : Verify other functionalities of Ovation Trend and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Point review

| - Test : Verify that the basic functionalities of Point review and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Point information

| - Test : Verify the basic functionalities of Point information and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Machine works

| - Test : Verify that the basic functionalities of Ovation Machine works and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Sensor Calibrate

| - Test : Verify the basic functionalities of Sensor Calibrate and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Controller Diagnostics

| - Test : Verify the basic functionalities of Controller Diagnostics and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Session Manager

| - Test : Verify the basic functionalities of Ovation Session Manager and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

      - Error log

| - Test : Verify the basic functionalities of Error log and list down below the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

    - Software Interfaces

| SRF Notes The Standalone Controller & Tools will contain software interfaces needed to communicate with other devices/systems. These will be the protocols that are supported for Third-Party communications, either natively via the Third-Party I/O drivers, or via the Embedded Ethernet Links provided by the CPS (Communication Protocols Suite). This does NOT include communications with SIS (Safety Instrumented Systems), Foundation Fieldbus, DeviceNet, or Ovation Multi-Network. Time-synchronization will be provided by the user by specifying a NTP server. The controller requires a NTP server in order to timestamp the alarm and error messages |  |  |
| --- | --- | --- |
| - Test : Determine if Time-synchronization works properly by specifying an NTP server. |  |  |
| Date(s): | Initials: |  |
| - Establish physical connectivity with NTP server and define NTP server related setting in Developer studio. Download the settings in SAC contrller. |  | P/F/F#/NA: |
| - Verify if Time-synchronization with NTP is working fine (refer test cases for NTP tests SVTP) |  | P/F/F#/NA: |
| - Wait for some time (like 15 minutes) and check 7th bit of HC status word of drop point. It should be set. |  | P/F/F#/NA: |
| Comments: |  |  |

    - Hardware Interfaces

| SRF Notes The Standalone Controller & Tools will contain the same hardware interfaces used in an Ovation Controller on a traditional Ovation system. This includes all types of I/O modules except Foundation Fieldbus and DeviceNet. |  |  |
| --- | --- | --- |
| - Test : Verify that Standalone Controller & Tools supports standard I/O modules (Note down Elecetronic module no./personality module/firmware revision number) and list down the verified operations & tests |  |  |
| Date(s): | Initials: |  |
| - Verify the basic functionalities of below mentioned standard IO Modules (Note down Elecetronic module no./personality module/firmware revision number) and list down the verified operations & tests - Analog Input module - Analog Output module - Digital Input module - Digital Output module - HART IO modules |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify the basic functionalities of Bus modules (Note down Elecetronic module no./personality module/firmware revision number) and list down the verified operations & tests (except Foundation Fieldbus and DeviceNet) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify the basic functionalities of Speciality modules (Note down Elecetronic module no./personality module/firmware revision number) and list down the verified operations & tests |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify the support for Remote node interface (RNI). Verify the basic functionalities of RNI (Note down Elecetronic module no./personality module/firmware revision number etc. used in testing) and list down the verified operations & tests. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

  - Performance Testing

| SRF Notes - A standalone controller application should have equivalent performance as compared to a non-standalone controller - Controller control task execution time - Controller CPU loading - Time for clear/load (Note, there will be slightly longer time expected for a load due to the extra HMI fields that are required to be on the controller). - Engineering tools should be able to save/restore a configuration within 5 minutes or less. |  |  |
| --- | --- | --- |
| - Test : Determine if Standalone Controller has same Controller control task execution time as of a non-standalone controller |  |  |
| Date(s): | Initials: |  |
| - Create a Database with some points (approx. 70-80% of total Controller point capacity) and Control sheets (approx 70-80% of points should be used in Control sheets) distributed in all 5 Control tasks. Add same database (with same points and Control sheets distributed in all 5 Control tasks) in both Standalone and non-standalone controller (should be of same Controller type). Load both the Controller with this same point database. |  | P/F/F#/NA: |
| - Verify, by using Control diagnostics, if both the Controller has equivalent control task execution time |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Determine if Standalone Controller has same Controller CPU loading as of a non-standalone controller |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a Database with some points (approx. 70-80% of total Controller point capacity) and Control sheets (approx 70-80% of points should be used in Control sheets) distributed in all 5 Control tasks. Add same database (with same points and Control sheets distributed in all 5 Control tasks) in both Standalone and non-standalone controller (should be of same Controller type). Load both the Controller with this same point database. |  | P/F/F#/NA: |
| - Verify, by using Control diagnostics, if both the Controller has equivalent control task execution time |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Determine if Standalone Controller has same Time for clear/load as of a non-standalone controller. (Note:- there will be slightly longer time expected for a load due to the extra HMI fields that are required to be on the controller) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Add same database (with same points and Control sheets distributed in all 5 Control tasks) in both Standalone and non-standalone controller (should be of same Controller type). Verify if both the Controller has equivalent Time for clear/load. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Determine if Engineering tools should be able to save a configuration within 5 minutes or less |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a configuration using engineering tools in Ovation Standalone & tools software (details about configuration is to be clarified from developer) |  | P/F/F#/NA: |
| - Verify if Engineering tools should be able to save this configuration within 5 minutes or less |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Determine if Engineering tools should be able to restore a configuration within 5 minutes or less |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Make major changes in existing configuration using engineering tools in Ovation Standalone & tools software (details about configuration is to be clarified from developer) or export a new configuration |  | P/F/F#/NA: |
| - Verify if Engineering tools should be able to restore configuration within 5 minutes or less |  | P/F/F#/NA: |
| Comments: |  |  |

  - Testing hardware and software environment

| SRF Notes The Controller portion of the Standalone Controller & Tools will apply to the following types of Controller Hardware: - OCC100 - OCR3000 - OMC100 (not yet released) - Next Generation Virtual Controller (not yet released) Operating System will be the same as non-Standalone Controllers, VxWorks 7. The Tools portion of the Standalone Controller & Tools is targeted for Windows 10 operating system. No specific hardware platform is required, however recommended specs will be captured and recorded in the user documentation if needed. Internet browser is required for the initial setup. (Microsoft Edge is the supported browser). Fixes for Standalone Tools software and controller software will be done with patches. |  |  |
| --- | --- | --- |
| - Test : Verify Ovation Standlone Controller & tools software with OCC100 using different Ovation tools |  |  |
| Date(s): | Initials: |  |
| - Verify Ovation Standlone Controller & tools software with OCC100 using following Ovation tools - Ovation Operator Graphics - Ovation Developer’s Studio - Ovation Alarm System - Ovation Control Builder - Ovation Graphics Builder - Ovation Signal Diagram Viewer - Ovation Trend - Point Information - Point Review - Ovation Machine Works - Sensor Calibrate - Controller Diagnostics |  | P/F/F#/NA: |
| - Refer tests in section HMI interface for this checking. Same tests are applicable here. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify support of Microsoft Edge Internet browser for the initial setup |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Open Microsoft Edge and try to connect to standalone Controller |  | P/F/F#/NA: |
| - Verify that able to perform the initial configurations (password settings) for the Controller using internet browser |  |  |
| Comments: |  |  |

  - Security testing

| SRF Notes This SRF satisfies security requirements of IEC 62443 4-2 SL1, each requirement is described in section 15. |  |  |
| --- | --- | --- |
| - Test : Verification of security requirements of IEC 62443 4-2 SL1 |  |  |
| Date(s): | Initials: |  |
| - Refer section 5.10 for IEC 62443 4-2 SL1 testing |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

  - Documentation

| SRF Notes User manual(s) shall be developed to assist the user in the operation of the Standalone Controller & Tools. A final list of documentation requirements will be developed with the Technical Writing group during implementation. |  |  |
| --- | --- | --- |
| - Test : To be discussed with documentation team |  |  |
| Date(s): | Initials: |  |
| a) |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

  - Testing Functional Specification

    - Controller

| SRF Notes The controller source code (common) will be updated to run in a standalone fashion depending on a new configuration file parameter set by Developer’s Studio. The controller code that will accept this type of change will be for the OCC100, OCR3000, OMC100. [Source Req 1.1] To not have explicit networking requirements for a controller pair, the standalone controllers will not communicate DDBs (Dynamic Data Blocks) to each other over the network. All communications will occur over the backplane. If the controllers communicated over a network, it is possible that DDBs would interfere with each other. [Source Req 1.11] No changes in the controller code will be required to handle the maximum number of points. This is currently done via a configuration parameter set by Developer’s Studio. [Source Req. 1.2] The controller code will handle storing a predefined list of files/folders from the standalone tools. These files will include things like the database, licensing files, control sheets, graphics, etc. It will be everything needed to engineer and operate the standalone controller, (except for the software applications themselves). [Source Req 1.3] When the controller is running in a redundant configuration, it will send the configuration files to the backup controller so that the files are available for runtime use (operator graphics, signal diagrams, etc.) if the primary controller becomes offline. [Source Req 1.4] All algorithms will be supported with the exception [Source Req 1.5]: - SIS algorithms - Fieldbus algorithms - Persisval algorithm (this requires a database server) Algorithm templates/symbols will need to be stored on the controller so that when an algorithm is patched, the corresponding template files will always be “in-sync” with the patched version of the algorithm. The tool (database and control builder) will need to use the version of the templates/symbols that were from the controller. [Source Req 1.5] Controller bumpless transfer will perform the same as in a traditional Ovation system. The controller can support secure communications via a Virtual Private Network (VPN). The controller will implement a VPN natively in controller and will require a router to terminate the other end of the VPN in the remote location (i.e. Control Room). [Source Req 1.10] The Standalone Tools will support booting a controller from a blank flash (i.e. from the factory) for the initial configuration, or during a re-format of the flash drive during a field troubleshooting process. The controller will support the standard SSH connection for advanced\field troubleshooting. In a standard Ovation system, the SSH authentication is done via RADIUS, however for the Standalone Controller, the authentication will be done via the local user account information stored on the controller. Only users with the Administrator role will be permitted access. If no account information is available (no user yet created) SSH access to the controller will be denied. |  |  |
| --- | --- | --- |
| - Test : Verify if able to define & configure supported Controller types using Developer Studio in a Standalone environment. |  |  |
| Date(s): | Initials: |  |
| - Open Ovation developer studio using Standlone tools. |  | P/F/F#/NA: |
| - Verify if able to define a new simplex Controller using Developer Studio in a Standalone environment |  | P/F/F#/NA: |
| - Verify if able to configure a new Redundant Controller using Developer Studio in a Standalone environment |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify maximum number of points for Controller in Standalone environment Determine if maximum number of points (This is currently done via a configuration parameter set by Developer’s Studio) limt works in same way as in traditional Controller |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Open Developer studio and set maximum number of points parameter. For OCC100 Controller it should be 10000 points and for OCR3000 it should be 64000 points. |  | P/F/F#/NA: |
| - For OCC100, create a configuration with 10K points and verify that OCC100 Controller will be loaded without any error with these many points |  | P/F/F#/NA: |
| - For OCR3000, create a configuration with 64K points and verify that OCR3000 Controller will be loaded without any error with these many points |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify Controller redundancy from “availability of configurtion files for runtime use” perspective Determine if When the controller is running in a redundant configuration, it will send the configuration files to the backup controller so that the files are available for runtime use (operator graphics, signal diagrams, etc) if the primary controller becomes offline |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a configuration with operator graphics, signal diagrams, etc and load a pair of Controller with this configuration |  | P/F/F#/NA: |
| - Fail In-Control (primary Controller) Controller and verify configuration files are still available for runtime use (operator graphics, signal diagrams, etc) from backup Controller |  | P/F/F#/NA: |
| - Fail In-Control (backup Controller) Controller and verify configuration files are still available for runtime use (operator graphics, signal diagrams, etc) from primary Controller |  | P/F/F#/NA: |
| - Fail In-Control (primary Controller) Controller and verify configuration files are still available for runtime use (operator graphics, signal diagrams, etc) from backup Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify support of standard Algorithms in Standalone environment Note:-Determine if All algorithms will be supported with the exception SIS algorithms/Fieldbus algorithms/Persisval algorithm (this requires a database server) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that all type of standard & APC algorithms are supported in Standalone environment |  | P/F/F#/NA: |
| - Refer & execute BASIC_FUNCTIONS_ SVTP_rev1.V.docx SVTP for Standard Ovation Algorithm checking for checking support of Standard algorithms in Standalone environment |  | P/F/F#/NA: |
| - Refer & execute OPTIONAL_SW_SVTP_rev1.V.docx SVTP for APC Algorithms checking for checking support of APC algorithms in Standalone environment |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify support of APC Algorithms in Standalone environment Note:-Determine if All algorithms will be supported with the exception SIS algorithms/Fieldbus algorithms/Persisval algorithm (this requires a database server) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that all type of standard & APC algorithms are supported in Standalone environment |  | P/F/F#/NA: |
| - Refer & execute BASIC_FUNCTIONS_ SVTP_rev1.V.docx SVTP for Standard Ovation Algorithm checking for checking support of Standard algorithms in Standalone environment |  | P/F/F#/NA: |
| - Refer & execute OPTIONAL_SW_SVTP_rev1.V.docx SVTP for APC Algorithms checking for checking support of APC algorithms in Standalone environment |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if all required Algorithm templates/symbols stored on the controller Determine if Algorithm templates/symbols will need to be stored on the controller (Algorithm templates/symbols will need to be stored on the controller so that when an algorithm is patched, the corresponding template files will always be “in-sync” with the patched version of the algorithm. The tool (database and control builder) will need to use the version of the templates/symbols that were from the controller) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Need to discuss with Development team on how to execute this test case |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify Controller redundancy for bumpless transfer of Control Determine if Controller bumpless transfer will perform the same as in a traditional Ovation system |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer & execute steps from SVTP for Ovation Controller testing for checking bumpless transfer |  | P/F/F#/NA: |
| - Fail In-Control (primary Controller) Controller and verify that the transfer of Control was bumpless |  | P/F/F#/NA: |
| - Fail In-Control (backup Controller) Controller and verify that the transfer of Control was bumpless |  | P/F/F#/NA: |
| - Fail In-Control (primary Controller) Controller and verify that the transfer of Control was bumpless |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify Controller support for secure communications via a Virtual Private Network (VPN) in a standlone environment Determine if controller can support secure communications via a Virtual Private Network (VPN). (The controller will implement a VPN natively in controller and will require a router to terminate the other end of the VPN in the remote location (i.e. Control Room)) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure Controller with VPN network |  | P/F/F#/NA: |
| - Refer & execute standard Ovation Controller SVTP for this checking |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Controller is able to bootup from a blank flash (i.e. from the factory) for the initial configuration in a standlone environment Determine if Standalone Tools will support booting a controller from a blank flash (i.e. from the factory) for the initial configuration, or during a re-format of the flash drive during a field troubleshooting process |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect Controller with blank flash to a standalone setup (no other Controller should be present as standlone supports only one Controller) |  | P/F/F#/NA: |
| - Configure the parameters for the Controller in Ovation developer studio |  | P/F/F#/NA: |
| - Verify if Controller is able to bootup from a blank flash (i.e. from the factory) for the initial configuration and it can be configured further. Check in the error log file for the bootup messages. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Controller is able to bootup from a re-formatted flash (i.e. from the factory) for the initial configuration in a standlone environment Determine if Standalone Tools will support booting a controller from a blank flash (i.e. from the factory) for the initial configuration, or during a re-format of the flash drive during a field troubleshooting process |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect Controller with re-formatted flash to a standalone setup (no other Controller should be present as standlone supports only one Controller) |  | P/F/F#/NA: |
| - Configure the parameters for the Controller in Ovation developer studio |  | P/F/F#/NA: |
| - Verify if Controller is able to bootup from a blank flash (i.e. from the factory) for the initial configuration and it can be configured further |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that the Controller supports SSH in a standalone environment Determine if The controller will support the standard SSH connection for advanced\field troubleshooting (In a standard Ovation system, the SSH authentication is done via RADIUS, however for the Standalone Controller, the authentication will be done via the local user account information stored on the controller. Only users with the Administrator role will be permitted access. If no account information is available (no user yet created) SSH access to the controller will be denied) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create administrator & non-administrator users for a Controller using security configuation |  | P/F/F#/NA: |
| - Verify if able to establish a ssh connection to Controller using administrator users |  | P/F/F#/NA: |
| - Verify attempt to establish a ssh connection to Controller using non administrator users should be failed |  | P/F/F#/NA: |
| Comments: |  |  |

    - Tools

| SRF Notes The tools for Standalone Controllers will be installed as part of the Ovation Standalone Software, will not require a server class computer or operating system, and will not require the computer to be part of a domain. [Source Req 2.1] [Source Req 2.2] The tools for Standalone Controllers will require an Ovation license – tied to the computer on which the software is installed. This will be similar to the Ovation licenses utilized on the Database Server of a standard Ovation system. [Source Req 2.5] The computer on which the tools for Standalone Controllers is installed will not be considered an Ovation drop – and installation of the software will not be permitted on an Ovation drop. [Source Req 2.4] The tools for Standalone Controller will include a new application which will serve as the primary user interface where various engineering functions are performed, and where Ovation Engineering and HMI applications are initiated or launched. Ovation user applications (Engineering or HMI) will be launched from this new application. The new application will feature the following functionality: - Permit the user to connect to (and disconnect from) a Standalone Controller. A username and password will be required to connect to a Standalone Controller. The tools for Standalone Controller will only permit the connection to one Standalone Controller at a time. [Source Req. 3.2] - Launch Ovation engineering tools applications such as Ovation Developer Studio and Ovation Engineering Audit Viewer. [Source Req. 2.13] - Launch Ovation HMI applications such as the Standalone Controller Alarm Window, Trend, Graphics, Point Information, Point Review, the Ovation Error Log, Signal Diagram Viewer, and Ovation Machine Works. [Source Req. 3.4] - Launch Ovation Utility applications such as Controller Diagnostics and Sensor Calibrate. [Source Req. 3.4] - Permit the user to create a new Standalone Controller database. - Permit the user to archive an existing Standalone Controller database to disk. [Source Req. 2.9] - Permit the user to restore a previously archived Standalone Controller database from disk. |  |  |
| --- | --- | --- |
| 5.9.2.i Test : Verify that Ovation Standalone Software get installed (along with all the tools) on a non server grade, non Ovation machine and machine is also not a member of any domain |  |  |
| Date(s): | Initials: |  |
| - Refer & execute tests mentioned in installation tests section |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.ii Test : Verify that tools for Standalone Controllers will require an Ovation license – tied to the computer on which the software is installed. This will be similar to the Ovation licenses utilized on the Database Server of a standard Ovation system |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer & execute tests mentioned in licensing tests section |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.iii Test : Verify that the computer on which the tools for Standalone Controllers is installed will not be considered an Ovation drop |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer & execute tests mentioned in installation tests section |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.iv Test : Verify that installation of the software will not be permitted on an Ovation drop |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try to install Ovation standalone & tools software on an Ovation drop |  | P/F/F#/NA: |
| - Installation attempt should be failed as it is not permitted |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.v Test : Verify that for connecting to Controller, username and password is required |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Establish physical connectivity between Controller and Standalone setup |  | P/F/F#/NA: |
| - Perform initial configuration setting on Controller using internet browser |  | P/F/F#/NA: |
| - Verify if able to connect to Controller using username and password |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.vi Test : Verify that tools for Standalone tools will only permit the connection to one Standalone Controller at a time |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify if able to connect to Controller using username and password |  | P/F/F#/NA: |
| - Try connecting to Controller by some other user and it shouldn’t be allowed as Standalone tools will only permit the connection to one Standalone Controller at a time |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.vii Test : Verify if Standalone application Launch Ovation engineering tools applications such as Ovation Developer Studio |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Launch Standalone application on an standlone machine |  | P/F/F#/NA: |
| - Go to tools section and open Ovation Developer Studio |  | P/F/F#/NA: |
| - Refer & execute tests mentioned in HMI interface section for proper working of Ovation developer studio when launched from standalone application |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.viii Test : Verify if Standalone application Launch Ovation engineering tools applications such as Ovation Engineering Audit Viewer |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Launch Standalone application on an standlone machine |  | P/F/F#/NA: |
| - Go to tools section and open Ovation Engineering Audit Viewer |  | P/F/F#/NA: |
| - Verify basic functionalities of Ovation Engineering Audit Viewer and list down below the verified operations & tests. (Refer Ovation basic functionality checking SVTP) |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.ix Test : Verify if Standalone application Launch Ovation HMI applications such as the Standalone Controller Alarm Window, Trend, Graphics, Point Information, Point Review, the Ovation Error Log, Signal Diagram Viewer, and Ovation Machine Works |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer & execute tests mentioned in HMI interface section. |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.x Test : Verify if Standalone application Launch Ovation Utility applications such as Controller Diagnostics and Sensor Calibrate |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer & execute tests mentioned in HMI interface section. |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.xi Test : Verify if Standalone application Permit the user to create a new Standalone Controller database |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - On a newly created setup install Ovation standlone & tools software |  | P/F/F#/NA: |
| - On launching Ovation standlone, option for creating new empty database should appear |  | P/F/F#/NA: |
| - Verify that able to selet that option and it creates empty database without any error |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.xii Test : Verify if Standalone application Permit the user to archive an existing Standalone Controller database to disk |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Simplex Standalone Controller and perform archive an existing Standalone Controller database to disk operation |  | P/F/F#/NA: |
| - Verify if archive of database happens without any error |  | P/F/F#/NA: |
| - Connect to primary Redundant Standalone Controller and perform archive an existing Standalone Controller database to disk operation |  | P/F/F#/NA: |
| - Verify if archive of database happens without any error |  | P/F/F#/NA: |
| - Connect to secondary Redundant Standalone Controller and perform archive an existing Standalone Controller database to disk operation |  | P/F/F#/NA: |
| - Verify if archive of database happens without any error |  | P/F/F#/NA: |
| - Compare archived database from primary and seconday are same |  | P/F/F#/NA: |
| Comments: |  |  |

| 5.9.2.xiii Test : Verify if Standalone application Permit the user to restore a previously archived Standalone Controller database from disk |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Standalone Controller and select option to restore previously archived Standalone Controller database from disk |  | P/F/F#/NA: |
| - Verify if restoration of database happens without any error |  | P/F/F#/NA: |
| Comments: |  |  |

      - Database

| SRF Notes The installation of the tools for Standalone Controller will include the installation of Microsoft SQL Server Express, which will be used to configure a Standalone Controller. The database will run on the computer where the Ovation Standalone Software has been installed but stored (maintained) on the Standalone Controller. [Source Req. 2.6] |  |  |
| --- | --- | --- |
| - Test : Verify that Database will run on the computer where the Ovation Standalone Software has been installed but stored (maintained) on the Standalone Controller |  |  |
| Date(s): | Initials: |  |
| - Refer & execute Database related tests in tools section |  | P/F/F#/NA: |
| Comments: |  |  |

      - User Accounts

| SRF Notes User accounts will be maintained in (and authenticated by) the Standalone Controller. As it relates specifically to the Standalone Controller, there will be 3 different “User Types” to which a user may be assigned: - Operator: The user will not be able to perform any engineering functions. All Engineering Tools applications will consider the database to be in a read-only mode. (Reference Section 14.2.5.3 for more information about read-only mode in Ovation Developer Studio.) - Engineer: The user will be able to perform engineering functions and make modifications to the database. - Administrator: The user will be able to perform engineering functions and make modifications to the database, user accounts, and Ovation security configurations. These user accounts will be used for the purpose of connecting and gaining access to a Standalone Controller’s runtime and engineering/configuration data. They will not be associated in any way with the computer’s Windows user. [Source Req. 2.7] The Ovation Security Manager (launched from Ovation Developer Studio) will be responsible for creating and maintaining users in the Standalone Controller and defining allow/deny access to Ovation functionality for those users. Although the Ovation Security Manager will provide the user interface to create/modify/delete user accounts and update/reset existing user passwords, the underlying functionality for these operations will be performed by the Standalone Controller itself. [Source Req. 1.12] [Source Req. 2.10] |  |  |
| --- | --- | --- |
| - Test : Verify user accounts in Standalone environment Note: Refer Ovation Security manager SVTP for the detailed steps for this test. |  |  |
| Date(s): | Initials: |  |
| - Verify if able to create three type of user accounts which are operator, Engineer and Administrator using Ovation Security Manager. |  | P/F/F#/NA: |
| - Verify that Ovation Security Manager (launched from Ovation Developer Studio) will be responsible for creating and maintaining users in the Standalone Controller. |  | P/F/F#/NA: |
| - Verify that Ovation Security Manager (launched from Ovation Developer Studio) will be responsible for defining allow/deny access to Ovation functionality for these three users. |  | P/F/F#/NA: |
| - Verify that Ovation Security Manager will provide the user interface to modify user accounts. Verify that while working on Standalone Controller with this user account, modified access and previliges are available. |  | P/F/F#/NA: |
| - Verify that Ovation Security Manager will provide the user interface to delete user accounts. Verify that with deleted user account, Standalone Controller should not be accessible. |  | P/F/F#/NA: |
| - Verify that Ovation Security Manager will provide the user interface to update/reset existing user passwords. |  | P/F/F#/NA: |
| - Verify that operator users is only allowed to have applicable access and previliges as defined in Ovation security manager. |  | P/F/F#/NA: |
| - Verify that Engineer users is only allowed to have applicable access and previliges as defined in Ovation security manager. |  | P/F/F#/NA: |
| - Verify that Administrator users is only allowed to have applicable access and previliges as defined in Ovation security manager. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that operator user will not be able to perform any engineering functions. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Login to Standalone Controller with operator user |  | P/F/F#/NA: |
| - Verify that operator user will not be able to perform any engineering functions and All Engineering Tools applications will consider the database to be in a read-only mode. Refer Ovation Security manager SVTP for the detailed steps for this test |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that Engineer user will be able to perform engineering functions and make modifications to the database |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Login to Standalone Controller with Engineer user |  | P/F/F#/NA: |
| - Verify that Engineer user will be able to perform engineering functions and make modifications to the database. Refer Ovation Security manager SVTP for the detailed steps for this test |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that Administrator user will be able to perform engineering functions and make modifications to the database, user accounts, and Ovation security configurations |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Login to Standalone Controller with Administrator user |  | P/F/F#/NA: |
| - Verify that Administrator user will be able to perform engineering functions and make modifications to the database, user accounts, and Ovation security configurations. Refer Ovation Security manager SVTP for the detailed steps for this test |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify that Administrator user will not be associated in any way with the computer’s Windows user |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Login to Standalone Controller with Administrator user |  | P/F/F#/NA: |
| - Verify that Administrator user will not be associated in any way with the computer’s Windows user. These user accounts will be used for the purpose of connecting and gaining access to a Standalone Controller’s runtime and engineering/configuration data .Refer Ovation Security manager SVTP for the detailed steps for this test |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify user passwords properties like being able to configure the minimum length, complexity, and how often it expires |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that user shouldn’t be able to setup password shorted than minimum length |  | P/F/F#/NA: |
| - Verify the complexity requirement of password |  | P/F/F#/NA: |
| - Verify that the password work as per the expiration period set or never expire as per the setting |  |  |
| Comments: |  |  |

      - Connect Operation

| SRF Notes To connect to a Standalone Controller, the user will need to provide a valid username and password – authenticated by the Standalone Controller. The tools for Standalone Controller software will support the following example use cases when connecting to a Standalone Controller: - Use Case 1: The user Connects to the Standalone Controller and uploads the database (and supporting files) to the computer. This will be considered the “typical” scenario. (Note that this will replace any Standalone Controller database which was previously running in the computer.) If the user is defined with the role of Operator, they will still be able to run Ovation Developer Studio (subject to the user’s Ovation security configuration), but the application will execute in read-only mode. (Reference Section 14.2.5.3 for more information about read-only mode in Ovation Developer Studio.) - Use Case 2: The user Connects to the Standalone Controller with the intention of using a database which is already running in the computer. There are several situations where this would be applicable: - Initial configuration of a Standalone Controller (e.g., no database currently exists in the Standalone Controller). - Off-line configuration of a new database (e.g., new control scheme/functionality) – completely replacing the database on (and the application currently running in) the Standalone Controller. - Off-line modification of a Standalone Controller. For example, the user Disconnects from the Standalone Controller but keeps the database locally on the computer to make “off-line” engineering modifications to the database. (Reference Section 14.2.4 for more information about Disconnect.) Note that this use case will not be applicable for users defined with the role of Operator. Checks will be performed to verify that the database running locally on the computer is compatible with the database currently stored in the Standalone Controller. If an incompatibility is detected, the user will be notified and given the following options: - Abort the Connection attempt. - Utilize the database on the Standalone Controller – in which case the database currently on the computer will be deleted and the database will be uploaded from the Standalone Controller. - Utilize the database currently on the computer. Note that since the database has been detected to be incompatible with the database stored on (and application running in) the Standalone Controller, the Standalone Controller will need to be cleared. Once Connected to the Standalone Controller, the Ovation HMI and utility applications can be executed, regardless of the user’s defined role. [Source Req. 3.1] Unless the user is defined with the role of Operator, the Standalone Controller will implicitly mark its database as locked (or “signed out”). [Source Req. 2.11] However, only one user will have the ability to Connect and lock a Standalone Controller’s database at any one time. If a non-Operator user attempts to Connect to a Standalone Controller whose database is already locked, they will be notified and given the following options: - Abort the Connection attempt. - Continue with the Connection, but without locking the database and operating in read-only mode. - Override the database lock. In the case of a redundant Standalone Controller, Connection for engineering purpose will require the availability of (and explicit connection to) the primary half of the redundant Standalone Controller. If the primary half is not available, the user will still be able to perform a Connect for the purposes of operator functionality (including access to the database in a read-only mode). (Reference Section 14.2.5.3 for more information about read-only mode in Ovation Developer Studio.) Note, if the primary controller is lost, and a database backup is not available offline, the user can still recover the database from the backup controller and use that as a starting point to recover the primary controller. Best practice should be for the user to always archive the database in another location following any engineering changes to the application. |  |  |
| --- | --- | --- |
| - Test : Verify that to connect to a Standalone Controller, valid username and password is required |  |  |
| Date(s): | Initials: |  |
| - Establish physical connectivity between Controller and Standalone setup |  | P/F/F#/NA: |
| - Perform initial configuration setting on Controller using internet browser |  | P/F/F#/NA: |
| - Verify if able to connect to Controller using username and password |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify database upload to database (and supporting files) to the computer |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to a Standalone Controller, valid username and password |  | P/F/F#/NA: |
| - During connection, select uploads the database (and supporting files) to the computer |  | P/F/F#/NA: |
| - Verify that this operation gets performed without any error and it will replace any Standalone Controller database which was previously running in the computer |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Operator user can run Ovation Developer Studio in read-only mode only |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Login to Ovation standalone setup using Operator users |  | P/F/F#/NA: |
| - Verify that Ovation Developer Studio is opned in read-only mode by trying changing configuration. Attempt to change configuration should be failed. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if user will be able to perform Initial configuration of a Standalone Controller (e.g., no database currently exists in the Standalone Controller) |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to newly added Controller using internet browser |  | P/F/F#/NA: |
| - Verify if user will be able to perform Initial configuration of a Standalone Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify downloading new database (performed offline) to already running Controller with some database |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a new Database (e.g., new control scheme/functionality) offline on Standalone machine when not connected to Controller |  | P/F/F#/NA: |
| - Connect to Controller which is already running with some database and select the option to utilize the database stored on the standalone station |  | P/F/F#/NA: |
| - Verify that able to completely replace database on Standlone Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify downloading modified database (performed offline) to already running Controller with some database |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Make changes to existing database offline on Standalone machine when not connected to Controller |  | P/F/F#/NA: |
| - Connect to Controller which is already running with some database and select option to utilize database stored on the station |  | P/F/F#/NA: |
| - Perform required Download/reboot/clear/load operations and Verify that able to replace database on Standlone Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Checks will be performed to verify that the database running locally on the computer is compatible with the database currently stored in the Standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | P/F/F#/NA: |  |
| - Try connecting to Standalone Controller from Standalone machine where some database, which is not same as running in Controller,is present |  | P/F/F#/NA: |
| - Verify if Checks will be performed to verify that the database running locally on the computer is compatible with the database currently stored in the Standalone Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify options available on detection of incompatibilityof Database between Standalone station and Standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | P/F/F#/NA: |  |
| - Create new database which is incompatible (A “non-compatible” database would be one which is created from scratch (e.g., via create new database, followed by text-based imports and control sheet imports) or a database which is defined as a template database) with database running on Standalone Controller. Try connecting to controller when this database is utilized by engineering tools. |  | P/F/F#/NA: |
| - Verify that if an incompatibility is detected, the user will be notified and given the following options- -Abort the Connection attempt. -Utilize the database on the Standalone Controller – in which case the database currently on the computer will be deleted and the database will be uploaded from the Standalone Controller. -Utilize the database currently on the computer. Note that since the database has been detected to be incompatible with the database stored on (and application running in) the Standalone Controller, the Standalone Controller will need to be cleared |  | P/F/F#/NA: |
| - Verify that on detecting incompatibility, if the user select “Abort the Connection attempt” then this option Aborts the Connection |  | P/F/F#/NA: |
| - Verify that on detecting incompatibility, if the user select “Utilize the database on the Standalone Controller – in which case the database currently on the computer will be deleted and the database will be uploaded from the Standalone Controller” then this option deletes database currently on the computer and the database will be uploaded from the Standalone Controller |  | P/F/F#/NA: |
| - Verify that on detecting incompatibility, if the user select “Utilize the database currently on the computer. Note that since the database has been detected to be incompatible with the database stored on (and application running in) the Standalone Controller, the Standalone Controller will need to be cleared” then this option prompts to clear the Controller. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Database which is compatible is older than what exists in the Controller then it could be loaded to standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | P/F/F#/NA: |  |
| - Perform Restore operation of an older database present in Archive |  |  |
| - Try connecting to Standalone Controller from Standalone machine where this older database is present with engineering tools |  | P/F/F#/NA: |
| - Verify if able to load this older database into Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Database which is compatible is newer than what exists in the Controller then it could be loaded to standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | P/F/F#/NA: |  |
| - Make changes to existing database of Controller (For example, user Disconnects from Standalone Controller, but keeps the database for engineering purposes. User makes engineering changes to the database via Ovation Developer Studio while not connected) |  |  |
| - Try connecting to Standalone Controller from Standalone machine where this newer database is present with engineering tools |  | P/F/F#/NA: |
| - Verify if able to load this newer database into Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Once Connected to the Standalone Controller, the Ovation HMI and utility applications can be executed, regardless of the user’s defined role |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Standalone Controller using Operator user |  | P/F/F#/NA: |
| - Verify if able to execute all the Ovation HMI and utility applications. Refer HMI interface test cases for detailed test steps. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Unless the user is defined with the role of Operator, the Standalone Controller will implicitly mark its database as locked(or “signed out”). |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to standalone Controller and lock the Database |  | P/F/F#/NA: |
| - Try connecting to Controller with other user and should get notification pop-up that Database lock is already with first user. |  |  |
| - Select the appropriate option and verify it works correct way |  |  |
| Comments: |  |  |

| - Test : Verify if only one user will have the ability to Connect and lock a Standalone Controller’s database at any one time |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to standalone Controller and lock the Database |  | P/F/F#/NA: |
| - Try connecting to Controller with other user and should get notification pop-up that Database lock is already with first user and from the available options select override the lock option |  |  |
| - Try to perform control operation for which lock is required from first user and verify that first user is not allowed to perform these operation which requires database lock. |  |  |
| Comments: |  |  |

| - Test : Verify non-Operator user attempts to Connect to a Standalone Controller whose database is already locked |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to a Standalone Controller with Operator user an dlock the database |  | P/F/F#/NA: |
| - Try connecting with non-Operator user |  | P/F/F#/NA: |
| - Verify if a non-Operator user attempts to Connect to a Standalone Controller whose database is already locked, they will be notified and given the following options: 1) Abort the Connection attempt 2) Continue with the Connection, but without locking the database and operating in read-only mode. 3) Override the database lock |  | P/F/F#/NA: |
| - Verify if user selects “Abort the Connection attempt” then connection attempt aborts |  | P/F/F#/NA: |
| - Verify if user selects “Continue with the Connection, but without locking the database and operating in read-only mode” then connection continues without locking the database and there is read-only mode |  | P/F/F#/NA: |
| - Verify if user selects “Override the database lock” then it actually Override the database lock |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify Connection for engineering purpose will require the availability of the primary half of the redundant Standalone Controller |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure a redundant standalone Controller pair on Standalone setup |  | P/F/F#/NA: |
| - Connect to primary Controller for engineering purpose (use either administrator user or engineer user having engineer roles, aceess & privileges) and this connection attempt should be successful |  | P/F/F#/NA: |
| - Disconnect and try connecting to secondary Controller (as per dev studio). Irrespective of user role, connection to secondary Controller should always be in read-only mode. |  | P/F/F#/NA: |
| - Fail or disconnect primary Controller |  | P/F/F#/NA: |
| - Try connecting to secondary Controller (as per dev studio). Irrespective of user role, connection to secondary Controller should always be in read-only mode. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if the primary half is not available, the user will still be able to perform a Connect for the purposes of operator functionality including access to the database in a read-only mode |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure a redundant standalone Controller pair on Standalone setup |  | P/F/F#/NA: |
| - Connect to primary Controller for operator purpose (logged in with any user having atleast operator roles, access & privileges) and this connection attempt should be successful |  | P/F/F#/NA: |
| - Disconnect and try connecting to secondary Controller (as per dev studio). This attempt should be successful without any error. |  | P/F/F#/NA: |
| - Fail or disconnect primary Controller. |  | P/F/F#/NA: |
| - Try connecting to secondary Controller (as per dev studio). This attempt should be successful but user should only have operator functionality & access to the database in a read-only mode |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if the primary controller is lost, and a database backup is not available offline, the user can still recover the database from the backup controller and use that as a starting point to recover the primary controller. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure a redundant standalone Controller pair on Standalone setup |  | P/F/F#/NA: |
| - Make sure that no Database backup is available on Standalone station |  | P/F/F#/NA: |
| - Fail or disconnect primary Controller. |  | P/F/F#/NA: |
| - Try connecting to secondary Controller (as per dev studio) and try recovering database. This attempt should be successful. |  | P/F/F#/NA: |
| - Make functional primary Controller and Use database recovered in previous step |  | P/F/F#/NA: |
| - Verify if primary Controller is fully recovered with this database |  | P/F/F#/NA: |
| Comments: |  |  |

      - Disconnect Operation

| SRF Notes The Disconnect operation will close the connection with the Standalone Controller. All HMI applications will be terminated, and the user will be logged out of the Standalone Controller. In addition, if the Standalone Controller database is not locked (e.g., Operator user), the database on the workstation will be deleted/removed. If the Standalone Controller database is locked, the tools for software will support several options when disconnecting [Source Req. 2.12]: - Disconnect (Normal): The Standalone Controller database (and supporting files) will be downloaded to the Standalone Controller, the Standalone Controller will indicate that its database is no longer locked, and the database on the workstation will be deleted/removed. This will be the typical use case. - Disconnect (Engineer): The Standalone Controller database (and supporting files) will be downloaded to the Standalone Controller and the Standalone Controller will indicate that its database is still locked by the user, and the database on the workstation will not be deleted/removed. This use case is appropriate if additional engineering functions are intended to be performed in an offline (or disconnected) state. |  |  |
| --- | --- | --- |
| - Test : Verification of disconnect operation |  |  |
| Date(s): | Initials: |  |
| - Connect to Controller and open HMI applications e.g. PI, alarms etc. |  | P/F/F#/NA: |
| - Disconnect from the Controller |  | P/F/F#/NA: |
| - Verify if user will be logged out of the Standalone Controller |  | P/F/F#/NA: |
| - Verify if All HMI applications will be terminated |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verification of disconnect operation when Standalone Controller database is not locked |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and Operator user and make sure that Database is not locked |  | P/F/F#/NA: |
| - Disconnect from the Controller |  | P/F/F#/NA: |
| - Verify if the database on the workstation will be deleted/removed |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verification of disconnect operation when Standalone Controller database is locked |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and make sure that Database is locked |  | P/F/F#/NA: |
| - Disconnect from the Controller |  | P/F/F#/NA: |
| - Verify that if on Disconnect, the tools for software will provide following two options- Disconnect (Normal) or Disconnect (Engineer) |  | P/F/F#/NA: |
| - Verify that if user selects “Disconnect (Normal)” option then The Standalone Controller database (and supporting files) will be downloaded to the Standalone Controller, the Standalone Controller will indicate that its database is no longer locked, and the database on the workstation will be deleted/removed |  | P/F/F#/NA: |
| - Verify that if user selects “Disconnect (Engineer)” then The Standalone Controller database (and supporting files) will be downloaded to the Standalone Controller and the Standalone Controller will indicate that its database is still locked by the user, and the database on the workstation will not be deleted/removed |  | P/F/F#/NA: |
| Comments: |  |  |

      - Ovation Developer Studio

| SRF Notes The Ovation Developer Studio for Standalone Controller (in general) will look and operate like Ovation Developer Studio on a standard Ovation system. There will be functional differences, however, in the version used for engineering a Standalone Controller. |  |  |
| --- | --- | --- |
| - Test : Verify if Ovation Developer Studio for Standalone Controller (in general) will look and operate like Ovation Developer Studio on a standard Ovation system. |  |  |
| Date(s): | Initials: |  |
| - Refer test steps in HMI inerface section for this test |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

        - Standalone Controller

| SRF Notes The standalone controller database will be limited to the definition of 1 Standalone Controller, which will not be an Ovation drop (e.g., no Drop ID specification). [Source Req. 2.3] The Engineering Tools for Standalone Controller software will prevent the user from defining received points for the Standalone Controller. This is further enforced since the single Standalone Controller is the only entity where Ovation points can be defined in a Standalone Controller database. [Source Req. 1.8] The only supported Standalone Controller drop types/styles will be OCR3000 and OCC100. The OMC100 and OCRVirt will be supported in the future. [Source Req. 1.1] Standalone Controller drop types/styles will have the same configurations as their counterparts in Ovation with respect to redundancy (simplex/redundant) and Ovation point counts. [Source Req. 1.2] [Source Req. 1.3] The list of configurable I/O Drivers for the Standalone Controller will be the same as their counterparts in Ovation with the following omissions [Source Req. 1.6] [Source Req. 1.7]: - Ovation SIS and Ovation SIS CHARMs - Foundation Fieldbus (this implies that Foundation Fieldbus modules will also not be supported) - DeviceNet (this implies that DeviceNet modules will also not be supported) - Ovation Multi-Network (ExternalOvationNetwork) Standalone Controllers will not support Q-Line modules. Note that this is implicitly enforced since none of the supported Standalone Controller drop types/styles support Q-Line in a standard Ovation system. [Source Req. 1.6] |  |  |
| --- | --- | --- |
| - Test : Verify thet Engineering Tools will prevent the user from defining received points for the Standalone Controller |  |  |
| Date(s): | Initials: |  |
| - Connect to standalone Controller |  | P/F/F#/NA: |
| - Open Control builder application and try to use received point in Control sheet |  | P/F/F#/NA: |
| - Verify that using received point is not allowed |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Determine if only supported Standalone Controller drop types/styles will be OCR3000 and OCC100 |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to standalone Controller |  | P/F/F#/NA: |
| - Open Developer studio application and Go to Controller settings |  | P/F/F#/NA: |
| - Verify that only supported Standalone Controller drop types/styles will be OCR3000 and OCC100 |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify support of IO drivers |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Configure a standalone Controller and check support I/O drivers as shown below- Refer & execute CONTROLLER_SVTP_rev5.14.docx for detailed steps for this checking |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Standalone Controllers do not support Q-Line modules. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Confiure a Standalone Controller and try adding Q-Line modules |  | P/F/F#/NA: |
| - Verify if Standalone Controllers will not support Q-Line modules |  | P/F/F#/NA: |
| Comments: |  |  |

        - License Manager

| SRF Notes The licensing of Standalone Controller related items (e.g., point License Tiers, ELC and Embedded Link protocols, etc.) will be based on the MAC address of the Standalone Controller (primary side if redundant). These will be licenses separate from the license used for the Ovation Standalone software itself. When launched from Ovation Developer Studio, the License Manager will utilize the MAC address as obtained from the connected Standalone Controller. If running in a disconnected state, the MAC address as defined in the database will be used. [Source Req. 1.9] |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Covered in Licensing requirement section |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

        - Read-only Mode

| SRF Notes The Ovation Developer Studio will support operation in a read-only mode. This will be employed if the connected user is an Operator or if any user has connected to a Standalone Controller which has been locked (for engineering) by another user from another computer. The Ovation Developer Studio running in read-only mode will have the following differences: - The following Operations are disabled, regardless of the user’s Ovation security configuration: Insert New…, Delete, Purge, Copy, Load, Download, Reboot, Clear, Reconcile, Create Baseline…, Control Options…, Import (Graphics), Coefficient Calc, and Restore. - When launched from Ovation Developer Studio, the Ovation Graphics Builder will run in read-only mode. - Ovation Developer Studio will not launch the Ovation Control Builder. |  |  |
| --- | --- | --- |
| - Test : Verification of Read-only mode |  |  |
| Date(s): | Initials: |  |
| - Verify if connected user is an Operator then Ovation Developer Studio will support operation in a read-only mode |  | P/F/F#/NA: |
| - Verify if any user has connected to a Standalone Controller which has been locked (for engineering) by another user from another computer then Ovation Developer Studio will support operation in a read-only mode |  | P/F/F#/NA: |
| - Verify that regardless of user, if Ovation Developer Studio running in read-only mode then following oprations will be disabled “Insert New…, Delete, Purge, Copy, Load, Download, Reboot, Clear, Reconcile, Create Baseline…, Control Options…, Import (Graphics), Coefficient Calc, and Restore” |  | P/F/F#/NA: |
| - Verify if launched from Ovation Developer Studio, the Ovation Graphics Builder will run in read-only mode |  | P/F/F#/NA: |
| - Verify in read-only mode if Ovation Developer Studio will not launch the Ovation Control Builder |  | P/F/F#/NA: |
| Comments: |  |  |

        - Operations

| SRF Notes A new right-click Operation will be defined for the Standalone Controller database object. This operation will permit the user to perform the following [Source Req. 2.8]: - Perform an explicit download of the Standalone Controller database (and supporting files) to the Standalone Controller. - Enable/disable the implicit download of the Standalone Controller database (and supporting files) to the Standalone Controller immediately following each successful Load to the Standalone Controller. The following Operations will be disabled unless the user is currently connected to the Standalone Controller in a locked state: - Load - Download - Reboot - Clear - Reconcile - Restore |  |  |
| --- | --- | --- |
| - Test : Verify new right-click Operation |  |  |
| Date(s): | Initials: |  |
| - Verify if right-click Operation will permit the user to perform an explicit download of the Standalone Controller database (and supporting files) to the Standalone Controller |  | P/F/F#/NA: |
| - Verify if right-click Operation will permit the user to Enable the implicit download of the Standalone Controller database (and supporting files) to the Standalone Controller immediately following each successful Load to the Standalone Controller |  | P/F/F#/NA: |
| - Verify if right-click Operation will permit the user to disable the implicit download of the Standalone Controller database (and supporting files) to the Standalone Controller immediately following each successful Load to the Standalone Controller |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verfy if Operations will be disabled unless the user is currently connected to the Standalone Controller in a locked state |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to the Standalone Controller in a locked state |  | P/F/F#/NA: |
| - Verify if user is currently connected to the Standalone Controller in a unlocked state then Load/Download/Reboot/Clear/Reconcile/Restore will be disabled |  | P/F/F#/NA: |
| Comments: |  |  |

    - HMI

| SRF Notes The HMI Applications will be installed as part of the Ovation Standalone Software and will not require the computer to be part of a domain. The HMI Applications will be updated to run in a standalone mode based on a new configuration parameter set by Developer’s Studio. The Standalone HMI Applications can be initiated after the user is connected to the Standalone Controller. When the user connects as an Operator, the data that the HMI Applications use, such as configuration, data files, etc., will be uploaded and installed. [Source Req 3.1] A user can only connect to one controller at a time from a specific computer. [Source Req 3.2] Multiple users (operators, engineers, or administrators) will be able to connect to the same Standalone Controller providing they connect from different machines. The Standalone Controller will allow at least three simultaneous connections. [Source Req 3.3] Once the user is connected, they will be able to initiate the HMI Applications. When the user disconnects from the Standalone Controller, any running HMI Applications will terminate. The following HMI Applications will be supported in the Standalone Mode. [Source Req 3.4] - Graphics - Point Information - Trend - Point Review - Standalone Alarm Window - Signal Diagram - Ovation Machine Works - Sensor Calibrate - Controller Diagnostics - Session Manager - Error Log The Standalone HMI Alarm Software will only provide the current points in alarm. This supports only an “Alarm List” none of the other “List” types are available. The Standalone HMI Software will not provide the following: - Alarm Printer - Audible Alarm - Alarm Graphics Groups (However the priority icon will be supported) - Alert Details (Fieldbus is not being supported) - Ovation Keyboard The Standalone HMI Applications will support the Ovation Security Rules, which enables or disables the ability to perform the Operator Functions (such as scan on, scan off, etc.) based on the user that is currently logged into the Standalone Controller. |  |  |
| --- | --- | --- |
| - Test : Verify if the HMI Applications will be installed as part of the Ovation Standalone Software |  |  |
| Date(s): | Initials: |  |
| - Install Standalone software |  | P/F/F#/NA: |
| - Verify if following HMI application installed as part of the Ovation Standalone Software and will not require the computer to be part of a domain - Graphics - Point Information - Trend - Point Review - Standalone Alarm Window - Signal Diagram - Ovation Machine Works - Sensor Calibrate - Controller Diagnostics - Session Manager - Error Log |  | P/F/F#/NA: |
| - Refer & execute tests mentioned in HMI interface section |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if a user can only connect to one controller at a time from a specific computer |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to a Standalone Controller using some user |  | P/F/F#/NA: |
| - Try connecting to some other Verify Standalone Controller from same computer using same user. This shouldn’t be allowed. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Multiple users (operators, engineers, or administrators) will be able to connect to the same Standalone Controller providing they connect from different machines. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to a Standalone Controller using some user |  | P/F/F#/NA: |
| - Try connecting to same Controller using some other user using some other machine |  | P/F/F#/NA: |
| - Try connecting to same Controller using same user using some other machine (e.g. multiple login as administrator) |  |  |
| - Verify that the as per user previliges database is locked and one cannot Load or Download from the Ovation Developer Studio if another user has “taken control” of the Standalone Controller |  |  |
| Comments: |  |  |

| - Test : Verify if Standalone HMI Alarm Software will only provide the current points in alarm. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to standalone Controller and open up the alarm application |  | P/F/F#/NA: |
| - Verify if The Standalone HMI Alarm Software will only provide the current points in alarm. (This supports only an “Alarm List” none of the other “List” types are available) |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Standalone HMI Software will not provide Alarm Printer, Audible Alarm,Alarm Graphics Groups (However the priority icon will be supported),Alert Details (Fieldbus is not being supported),Ovation Keyboard |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify if Standalone HMI Software will not provide - Alarm Printer, - Audible Alarm, - Alarm Graphics Groups (However the priority icon will be supported), - Alert Details (Fieldbus is not being supported),Ovation Keyboard |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : Verify if Standalone HMI Applications will support the Ovation Security Rules |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify if The Standalone HMI Applications will support the Ovation Security Rules, which enables or disables the ability to perform the Operator Functions (such as scan on, scan off, etc.) based on the user that is currently logged into the Standalone Controller. Refer & execute security section of BASIC_FUNCTIONS_ SVTP_rev1.V.docx for this testing & test steps. |  | P/F/F#/NA: |
| Comments: |  |  |

    - Communication Protocols testing

| SRF Notes The Standalone Controller shall support any of the Communication Protocols available for the Controllers within the Communication Protocols Suite (CPS). The CPS software will be installed via the CPS 3.3 release software. Protocols will be configured using the CPS configuration tools the same way as in the traditional Ovation system. This includes the native “Embedded Ethernet Protocol” embedded in the OCC100, OCR3000, OMC100 (future), OCRVirt (future) and the Ethernet Link Communications (ELC) modules. [Source Req 1.5] |  |  |
| --- | --- | --- |
| - Test :Verify if Standalone Controller support for Communication Protocols Suite (CPS) |  |  |
| Date(s): | Initials: |  |
| - For Embedded Ethernet Protocol, Refer & execute section 5.1,5.2,5.7,5.9 (For TCP Modbus, For serial Allen Bradley-DF1 will be used) CPS_Embedded_SVTP_rev2.1.doc. |  | P/F/F#/NA: |
| - For Ethernet Link Communications (ELC) modules, Refer & execute section 5.1,5.2,5.7,5.9 (For TCP Modbus, For serial Allen Bradley-DF1 will be used) CPS_SVTP_rev2.2.docx. |  | P/F/F#/NA: |
| - Refer & execute “ELC Misc SVTP” for final regression. |  | P/F/F#/NA: |
| Comments: |  |  |

  - IEC62443 4-2 Security Level 1 testing

    - Identification and Authentication Control (IAC)

| SRF Notes |  |  |
| --- | --- | --- |
| - Test : To verify that the Standalone Controller will authenticate human users via username/password. |  |  |
| Date(s): | Initials: |  |
| - Connect to Controller using SAC tools and verify that it always ask to enter username/password. In no case, connection should be allowed without entering username/password. |  | P/F/F#/NA: |
| - Verif if in case username/password is not set (factory reset Controller), connection should be refused. |  | P/F/F#/NA: |
| - Try to connect to Controller using SSH and verify if it always ask for username and password. In case username/password is not set (factory reset Controller), connection should be refused. |  |  |
| Comments: |  |  |

| - Test : To verify that the Standalone Controller will manage accounts associated with the controller. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and access Security manager UI. Verify if able to manage user accounts from this security UI. Assign operator,engineer & administrator roles to these users. |  | P/F/F#/NA: |
| - Verify that operator are getting access/privileges as per their assigned access/privileges. |  | P/F/F#/NA: |
| - Verify that engineer are getting access/privileges as per their assigned access/privileges. |  |  |
| - Verify that administrator are getting access/privileges as per their assigned access/privileges. |  |  |
| Comments: |  |  |

| - Test : To verify that the Standalone Controller will manage identifiers to ensure that unique identifiers are used for each user account |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and access Security manager UI. |  | P/F/F#/NA: |
| - Try to create more than one user with same name or identifiers. This operation should not be allowed. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Standalone Controller shipped from the factory will have no initial authenticator information. The Standalone Controller will force the user to define an Administrator password during the initial setup. The Standalone Controller will have an option to force periodic refresh of passwords (passwords expire – default is never expire, duration of expiration will be configurable). |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect (Physical network connection) a Standalone Controller shipped from the factory to the standalone station and boot it up (MAC id will be attached to IP defined in Developer studio) |  | P/F/F#/NA: |
| - Try to perform some operation like initial download but these opeartions shouldn’t be allowed or there shouldn’t be any option to do these kind of operations |  | P/F/F#/NA: |
| - Open the web browser and enter the URL for initial configuration, initial setup confiuration page should appear |  |  |
| - Check that if Standalone Controller force the user to define an Administrator password during the initial setup |  |  |
| - Check if using Security UI, there is option to force periodic refresh of passwords |  |  |
| - Verify if “passwords expire – default is never expire” works correctly |  |  |
| - Configure password expire duration using security UI and confirm if password expires after that duration |  |  |
| - Once the password is expires (e.g. Administrator password) then able to setup the new password using security UI or initial setup webpage |  |  |
| Comments: |  |  |

| - Test : To verify that Standalone Controller will have the ability to enforce password strength, based on minimum length, and variety of characters. Prevention of password reuse is not required. Note, the controller will not allow this to be configurable. It will use a hard-coded password strength algorithm. This will simplify the design of the password strength. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and access Security manager UI |  | P/F/F#/NA: |
| - Try to set password which doesn’t fullfill minimum length and confirm that this operation fails |  | P/F/F#/NA: |
| - Try to set password which doesn’t fullfill variety of characters and confirm that this operation fails |  |  |
| - Try to set a password which is already set earlier and confirm that it is allowed |  |  |
| - Confirm that there is no option to change minimum length requirement for setting password |  |  |
| - Confirm that there is no option to change “variety of characters” requirement for setting password |  |  |
| Comments: |  |  |

| - Test : To verify that The Standalone Controller will obscure feedback of the password when being entered by the user, i.e. display asterisks. It will also not give any clue to whether the username or password is invalid for a failed authentication attempt, such as “unknown username”. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try to connect to any Controller and enter the username & password |  | P/F/F#/NA: |
| - Verify that feedback of the password is obscured i.e. when user enters the password he/she cant see the characters instead asterisks should be displayed. |  | P/F/F#/NA: |
| - Try to connect to any Controller and enter any invalid username or password |  |  |
| - Verify that there shouldn’t be any pop-up or information display anywhere in the system (check in all type of logs error log,status log, Audit viewer, windows event viewer) that its failed authentication |  |  |
| Comments: |  |  |

| - Test : To verify that in case of “Unsuccessful login attempts” controller will limit consecutive attempts using a hard-coded algorithm. Note- The algorithm will not be configurable. This will simplify the design |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try connecting to Controller with invalid username/password multiple times. After some failed attempts, there should be message that one can attempt only after some time (some seconds). |  | P/F/F#/NA: |
| - In case of further failed attempts (after waiting for time period in step1) the waiting time should increase and this process should contnue. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Standalone Controller will have the optional capability to display a customizable System Use Notification that will be displayed during user access before authentication |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to the Controller using web interface and execute “PUT” API after filling message in PUT API interface |  | P/F/F#/NA: |
| - Verify if message is displayed either by GET API or by trying login to Controller |  | P/F/F#/NA: |
| Comments: |  |  |

    - Use Control

| - Test : To verify that The Standalone Controller and Tools will have role-based policies to enforce that the authenticated users can perform the requested action based on their assigned responsibilities. Note, controller diagnostics currently does not check for user role for module firmware download and reboot. Future enhancement will be to add a check for “is role enabled” for controller diagnostics to see if the user is authorized for controller diagnostics. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a user having operator role and privileges |  | P/F/F#/NA: |
| - Verify it can only perform assigned tasks and specifically verify if it is not allowed to perform any engineering or administrative task e.g. loading of Controller or changing roles of other users |  | P/F/F#/NA: |
| - Create a user having engineer role and privileges |  |  |
| - Verify it can only perform assigned tasks and specifically verify if it is not allowed to perform any administrative task e.g. changing roles of other users |  |  |
| - Create a user having administrative role and privileges |  |  |
| - Verify it can only perform assigned tasks and specifically verify if it is allowed to perform engineering or administrative task e.g. loading of Controller or changing roles of other users |  |  |
| Comments: |  |  |

| - Test : To verify that The Ovation Controller does not have wireless access |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| NA |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that controller web interface will use a limited amount of Java Script, but it will not execute arbitrary Java Script. All web pages that are hosted on the controller will be standard and released via the signed binary image |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to SAC Controller using WinSPC application |  | P/F/F#/NA: |
| - Try to copy some unsigned (any file) to “romfs” directory, this operation shouldn’t be allowed |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that controller implements a session-lock internally and expires after 1 hour. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller using web interface and wait for 1 hour and check if ask to re-enter the credential to use web interface further. |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Events can be monitored and audited using the Error Log and Audit Viewer. Note:- Operator events are not supported at this time.To support auditable events from the controller’s perspective, the controller would require significant changes. At this time, we will handle auditing the same as it is done in an Traditional Ovation System. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and generate some events e.g. Load of Controller, archive of database etc. |  | P/F/F#/NA: |
| - Verify if same can be verified with correct details in Error Log and Audit Viewer |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Audit information will be stored in the database which archived in the controller. Note:- Capacity of audit-information is limited to a specific size |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to redundant Controller and generate some events e.g. Load of Controller, archive of database etc. |  | P/F/F#/NA: |
| - Fail the In Control Controller and restore the database from secondary Controller and verify if able to get these events |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Controller response to audit processing failures |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| N.A. (Note:- controller does not directly process audit information so this will not be an issue) |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Controller creates timestamps based on the configured NTP time source |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect to Controller and generate some events e.g. Load of Controller, archive of database etc. |  | P/F/F#/NA: |
| - Verify if the events are based on the configured NTP time source |  | P/F/F#/NA: |
| Comments: |  |  |

    - System Integrity (SI)

| - Test : To verify that The controller will use typical methods for verifying/preserving integrity of communications. This includes checksums/crcs/sequence numbers. In some cases, this is limited to the protocol which already exists. All new communications to the controller that is related to the Standalone feature will use HTTPS which has various checks for integrity |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Capture the network packets between Standalone Controller and station using wireshark for HTTP packets and verify if it implements checksums/crcs/sequence numbers. |  | P/F/F#/NA: |
| - Capture the network packets between Standalone Controller and station using wireshark for HTTPS packets and verify if it implements checksums/crcs/sequence numbers. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that The controller will use the standard application signing that verifies the loaded software has been signed. The signing process happens as part of the official software build process. Loading of unsigned software will result in an error, and the software will not execute |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| Testing steps are below : The purpose of this test is to verify that the controller(s) will not load unsigned versions of specific software. - Verify OCR3000 will not boot unsigned binary from network. - On DB Server - Make backup copy of signed kernel – c:\tftpboot\vxworks.ocr3000 - Copy unsigned kernel to c:\tftpboot\vxworks.ocr3000 - Restart CBS service (controller boot service) - Format OCR3000 disk (use serial cable and ‘F’ command using boot menu -or- put controller in new slot) - Verify controller is booting from DB server by monitoring BOOTP and TFTP messages in Ovation Error Log - Verify controller will not start and does not indicate “ss_rpc: ready to be downloaded” - Error message to putty console: Attempting to load “/bd0/boot/xWorks” from disk ... file not found. Attempting to load from the network ... Loading... Unable to read Module Info – attempt copy to RamDisk Loading Image in 20M ram disk Instantiating /bootDrv:0 as rawFs, device = 0x40001 Formatting /bootDrv:0 for DOSFS Instantiating /bootDrv:0 as rawFs, device = 0x40001 Formatting...Retrieved old volume params with %38 confidence: Volume Parameters: FAT type: FAT32, sectors per cluster 0 0 FAT copies, 0 clusters, 0 sectors per FAT Sectors reserved 0, hidden 0, FAT sectors 0 Root dir entries 0, sysId (null) , serial number d390000 Label:” “ ... Disk with 40000 sectors of 512 bytes will be formatted with: Volume Parameters: FAT type: FAT16, sectors per cluster 2 2 FAT copies, 19904 clusters, 79 sectors per FAT Sectors reserved 1, hidden 0, FAT sectors 158 Root dir entries 512, sysId VXDOS16 , serial number d390000 Label:”boot “ ... OK. Copying to RamDisk Key Validation failed. - Restore original signed kernel – c:\tftpboot\vxworks.ocr3000 - Restart CBS service (controller boot service) - Reboot controller & Query/Download as normal. |  | P/F/F#/NA: |
| - Verify OCR3000 will not load unsigned monoliths (*.out) files - On DB Server - Make backup copy of signed monolith – C:\Ovation\Embedded\controller\ocr3000\boot\ocr3000Ctlr.out - Copy unsigned kernel to C:\Ovation\Embedded\controller\ocr3000\boot\ ocr3000Ctlr.out - Query/Download OCR3000 - Restart OCR3000 - Verify controller does not boot and is not available on network - Serial cable connection during boot should show specific error message: # # ocr3000_startup.scr # ld < /bd0/boot/ocr3000Ctlr.out ld(): error loading file (errno = 0x61001f). - Type “printErrno 0x61001f” and verify the error is “SIG_KEY_INVALID” -> printErrno 0x61001f errno = 0x61001f : S_loadElfLib_SIG_KEY_INVALID. - Restore original signed monolith – C:\Ovation\Embedded\controller\ocr3000\boot\ ocr3000Ctlr - Use serial cable to format flash disk (press any key during boot, then ‘?’ for help, do format command “F”) - Reboot with the “@” command. - Controller should boot, then query download as normal. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that documentation will be updated to indicate to the user how to verify all security features are working properly |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify the documentation |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that The controller will not execute if the main software application has been tampered with. Additional software that is loaded besides the main software will result in an error message if the signature checks fail, and the software will not be loaded |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| This will include following to checks - Execute the 2nd test mentioned in 5.10.3.2 Verify OCR3000 will not load unsigned monoliths (*.out) files |  | P/F/F#/NA: |
| - Change the Startup script to include loading of unsighned *.out file. Download the Controller and reboot the Controller. Using Console verify that this *.out should not get loaded. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that The controller will use typical methods for input validation. Controller inputs include hardwired/networked input/output. These values are checked according to point ranges defined by the engineering tools. Changes to values such as setpoints are performed by network communications and are also subject to range checks during the handling of the setpoint change message |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Create a Control sheet using setpoint algo and load the standalone Controller with this sheet. |  | P/F/F#/NA: |
| - Try to set values which are out of range e.g. instead of setting up set point to 95 add additional 0 and try to set 950. This shouldn’t be set. |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that The controller will use its standard method for deterministic outputs. This includes the “Timeout Action” and “Timeout Selection” feature that exists on the I/O Modules |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that “Timeout Action” works properly on an IO module |  | P/F/F#/NA: |
| - Verify that “Timeout Selection” works properly on an IO module |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Error Handling The controller will not provide any error message to assist an attacker in knowing why an authentication failed. This includes: - Webpage access - Access from the Standalone Tools - Error messages in the Ovation Error Log - Error messages returned in the HTTPS response - Error messages in the Controller’s Error Buffer - Error messages in the Controller’s serial output |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try to login to Controller using non authorised users or by proving wrong credentials. |  | P/F/F#/NA: |
| - Verify that the information about failed authentication has not appeared anywhere in following application/places- - Webpage access - Access from the Standalone Tools - Error messages in the Ovation Error Log - Error messages returned in the HTTPS response - Error messages in the Controller’s Error Buffer - Error messages in the Controller’s serial output |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Controller and Tools will support patching similar to Ovation. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Try with example patch (Development will provide) and verify that patching happens without any issues. |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify that Integrity of the boot process |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify OCR3000 will not boot unsigned kernel from flash - On DB Server - Make backup copy of signed kernel – C:\Ovation\Embedded\controller\ocr3000\boot\vxWorks - Copy unsigned kernel to C:\Ovation\Embedded\controller\ocr3000\boot\vxWorks - Query/Download OCR3000 - Restart OCR3000 - Verify controller does not boot and is not available on network - Serial cable connection during boot should show specific error message: Attempting to load “/bd0/boot/xWorks” from disk ... Loading /bd0/boot/xWorks ... Key Validation failed. - Verify controller will give up and boot from network and start ss_rpc (ss_rpc: ready to be downloaded) - Restore original signed kernel – C:\Ovation\Embedded\controller\ocr3000\boot\vxWorks - Query download as normal. |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

    - Data Confidentiality (DC)

| - Test : To verify Information confidentiality. Note:- Ovation does not use confidential information. The VPN file has a pre-shared key that is stored openly at rest. The user must protect access to the controller if the pre-shared key is sensitive. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that no file should be there with name password (except VPN file). (Note:- Use WinSPC application to check the same) |  | P/F/F#/NA: |

| - Test : To verify that use of cryptography. The Standalone controller makes use of 2 different types of cryptography. The main cryptography method is for the HTTPS connection between the controller and the tools. The secondary method is for the VPN connection (ESP packets) which is an optional feature. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that the Standalone controller uses 2 different types of cryptography: HTTPS & VPN connections. |  | P/F/F#/NA: |
| - Verify the HTTPS connection between the controller and tools can be successfully estabilished and works properly. i) Verify that the HTTPS requires the use of certificates to provide the private and public keys needed to encrypt, decrypt, sign, and verify the request. ii) Verify the HTTPS connection can be succesfully estabilished by login to the controller portal using HTTPS instead of HTTP in the url (for ex: https://192.168.100.45:9292/v1/login) via the Edge browser. (Note:- for HTTP port 9191 will be used while for HTTPS port 9292 will be used ) iii) Verify that on successful login to the controller portal, the connection made is secure as the warning message saying “Not secure” should not appear on the browser. iv) Capture the network packets between Standalone Controller and station using wireshark for HTTPS packets, Network packets should show these messages as TLS packets. Verify if it implements all securuty related measures like checksums/crcs/sequence numbers. Also, Verify that there is no information available like username, password etc. |  | P/F/F#/NA: |
| - Verify the VPN connection between the controller and tools can be successfully estabilished and works properly. - Establish the VPN connection between controller and tools - Capture the network packets between Standalone Controller and station using wireshark and verify if it implements checksums/crcs/sequence numbers. - Capture the network packets between Standalone Controller and station using wireshark, Network packets should show these messages as ESP packets. - Verify that there is no information available like username, password etc. |  | P/F/F#/NA: |
| Comments: |  |  |

    - Restricted Data Flow (RDF)

| - Test : Network segmentation To verify that the controller supports network segmentation by the way of configurable IPv4 addresses, network routes, default gateways |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Access the Developer Studio |  | P/F/F#/NA: |
| - Use the system tree to navigate to the Controller Networking (Network item): Systems > Networks >UNIT>SAC controller>Configuration> Controller Networking |  |  |
| - The Controller Networking dialog box appears showing the Networking Configuration tab. |  |  |
| - Verify if IPv4 addresses, network routes, default gateways are configurable and work as per configuration |  |  |
| Comments: |  |  |

    - Timely Response to Events (TRE)

| - Test : To verify Audit log accessibility. Audit logs are accessible by the standard Ovation Audit Viewer and Ovation Error Log Viewer. Note:- The Error Log Viewer will only record log information while PC hosting the log viewer is running the error log server that is started at boot time. The controller will not buffer log message that are sent to the Error Log. The controller will also use the “printErrorBuffer” advanced command for field/remote advanced troubleshooting of standalone controllers. This buffer is the same that is available in the standard Ovation controller. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that the Error Log Viewer will only record log information while PC hosting the log viewer is running the error log server that is started at boot time. |  | P/F/F#/NA: |
| - Verify that the controller will not buffer log message that are sent to the Error Log. |  | P/F/F#/NA: |
| - Verify that standalone controller can use the “printErrorBuffer” advanced command for field/remote advanced troubleshooting of standalone controllers. |  |  |
| Comments: |  |  |

    - Resource Availability (RA)

| - Test : To verify the Denial of service protection. The controller will use standard practices for Denial-of-Service protection. This includes limiting the impact of the login process such that an attacker cannot prevent a valid user from logging in. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify in case of invalid login attempts, it shouldn’t disable the user accounts and its always available |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Resource management. The controller uses a priority-based operating system that prioritize the essential controller functions so that any ancillary security function cannot adversely impact the essential control functions. Note:- The controller does not support network scans or anti-virus checks. The only function that is applicable is patching, which is done through the download/reboot process which does not affect the control functions. This is the same as in a Standard Ovation System. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer achilles testing for this checking. |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Control system backup. The standalone controller will be able to have backups by saving the database from the controller to an offline location using the standalone tools. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify the controller database can be saved to offline location using SAC tools : - Open the developer studio using the SAC tools software from the SAC station - Right click on the SAC controller configured in the studio - Select SAC operations option from the list - click on “Save database to Standalone controller” option and click ok - Verify that in General options : “Auto Archive after load” option appears and it can be checked. |  | P/F/F#/NA: |
| - Verify the controller database can be saved by using the option Archive DB to disk from Sac software - Click on database tab - Click on archive DB to disk option to save the database |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Control system recovery and reconstitution. The standalone controller will be able to be recovered and reconstituted from the backup database using the standalone tools. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Verify that the backup database can be recovered using the “Restore databse from archive option” in the database tab from sac tools |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Network and security configuration settings. The Ovation Controller will not have any explicit security settings. The network settings are provided by the standard Ovation settings for IP Address, Subnet Mask, Speed/Duplex, Default Gateway, Route, and Shared Address. These settings are managed from Developer’s Studio in the same way an in a Traditional Ovation system. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Access the Developer Studio. - Use the system tree to navigate to the Controller Networking (Network item): - Systems > Networks >UNIT>SAC controller>Configuration> Controller Networking - The Controller Networking dialog box appears showing the Networking Configuration tab. - Verify that the Network and security configuration settings can be done as per the requirement. |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

| - Test : To verify the Least functionality. Controller will limit the ports that are not needed. Controller will limit the functions available via the Rest Server. |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Refer Achilles test results to verify the open ports |  | P/F/F#/NA: |
| - To verify any open ports because of APIs in rest server (To be done in later phase) |  | P/F/F#/NA: |
| Comments: |  |  |

  - Miscellaneous tests

| - Test : Perform miscellaneous operations on your assigned setups and list down the operations/tests with results |  |  |
| --- | --- | --- |
| Date(s): | Initials: |  |
| - Connect multiple Standalone Stations (each station has individual Satnadlone Controller or pair) using a switch (unmanged) and check that able to connect to Controllers from their respective stations |  | P/F/F#/NA: |
| - In above scenario, check what happens if try to connect other SAC Controller using database of some other SAC Controller (ideally incompatible database should be detected) |  | P/F/F#/NA: |
| - Perform failure testing like unplug the network cable while uploading the database to the controller and verify the behaviour. Also verify that it can be recovered by resending the database after the connection is restored (for this one needs to load the Controller again) |  | P/F/F#/NA: |
| - Perform failure testing like power off the Controller while uploading the database to the controller and verify the behaviour. Also verify that it can be recovered by resending the database after the Controller power is restored (for this one needs to load the Controller again) |  | P/F/F#/NA: |
| - Check the size limit of graphic (which is 3Mbytes) by creating a haevy graphic size and verify that able to load graphic of approx. equal to maximum allowed size |  | P/F/F#/NA: |
| - Check for continuesly connecting to Controller from SAC Station for a very long period of time (e.g. couple of days) and check that connection remains active and there is no timeout |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
|  |  | P/F/F#/NA: |
| Comments: |  |  |

- Approvals

This section contains the Test Review Approval Form (TRAF) for this Software Validation
 Test procedure.

---------------------------------------------------------------------------------------------------

Note:

The Test Review Approval Form is used only during the review of this SVTP. 

It should NOT be filled in when executing this test procedure.  

Any recommended changes to this test procedure which are discovered during testing should be filed as SVTP findings in the Findings system.

Test Review Approval Form

SVTP:  SINGLE_SRF_Mult_Tests _SVTP_Template

NOTE : This form is to be used only during the SVTP review process.

-Validation Engineer checks “Yes” if procedure has been modified else checks “No” :

Test Procedure - modified? 	Yes  ____ 	No ____

- Validation Engineer checks appropriate entry. If “b:” is selected, chapter numbers must be listed. If “c” is checked, development review and signature is not required.

Modification Type:	Dev. Review Required

a. New Test Procedure - 	Yes  ____

(Requires review of whole procedure)

b. Significant Test Procedure modifications - 	Yes  ____

(Requires review of Chapters ___________________)

c. No change or Minor Test Procedure modifications -	No    ____

___________________________________________________________________________

# Development Review:	____Responsible Engineer

Print Name of Dev Engineer for ”a” or “b” type changes:     _______________________

Check if Test Procedure was Reviewed and Approved: 	               _______________

Check if Test Procedure was Reviewed and requires changes:          _______________

-Sign-off, both Dev and Val for “a” or “b” changes, Val only for “c” changes :

Development Engineer Signature:	__________________	__/__/__

Validation Engineer Signature:	__________________	__/__/__

- Test Sign-Off Form

This section includes the test sign-off form for this Software Validation Test Procedure.

---------------------------------------------------------------------------------------------------

Instructions:

For Each Administarive  Section (1 - 4), give a ‘Pass’ mark if the description and reference information is accurate and complete.

In Section 5, for each Test Section (or feature), give a ‘Pass’ mark if all actions and results were executed correctly with no errors.

If any part of the test failed, give the test section a ‘Fail’ mark.

In case of a test procedure error or a required test modification, mark the ‘TP’ column.

If a section of the test is Not Applicable to the tested  Software Release, mark the ‘N/A’ column.

If any SDRs were written against the Test section, mark the ‘Yes’ box in the ‘SDR’s Written’ section. Otherwise mark the ‘No’ Box.

If an SDR  was written, attach a copy of the source file (when applicable) which was used to
discover the problem.

When a section of the test is skipped, mark the ‘Pass’ column as ‘SK’ and add a short explanation in the Comments box (e.g. No Hardware, Feature not released, etc.).  Also, make sure there is a detailed explanation in the Test Section for the reason why this section of the test was skipped

Fill in the required Test information at the top of the form, Sign and Date the form at the bottom.

---------------------------------------------------------------------------------------------------

Test Record Sign-Off

SVTP:  SINGLE_SRF_Mult_Tests _SVTP_Template

| Record Software and Equipment Used Information |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item: | Drop # | OS | Model | Other Info |
| Ovation Software Level | n/a | n/a | n/a |  |
| Database Server |  |  |  |  |
| Opcon/Engineering Station |  |  |  |  |
| Controller |  |  |  |  |

| Test Procedure Section | Test Score |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- |
|  | Pass | Fail | N/A |  |  |
| Document Revision Index and Record of Changes |  |  | X |  |  |
| 1.0 Software Test Identifier |  |  | X |  |  |
| 2.0 Purpose |  |  | X |  |  |
| 3.0 Approach |  |  | X |  |  |
| 4.0 Features |  |  | X |  |  |
| 5.0 Procedure Steps |  |  | X |  |  |
| 5.1 SRF 2347 |  |  |  |  |  |
| 5.2 SRF 2347 |  |  |  |  |  |
| 5.3 SRF 2347 |  |  |  |  |  |
| 5.4 SRF 2347 |  |  |  |  |  |
| 5.5 SRF 2347 |  |  |  |  |  |

| Tester Name: | Tester Initials: | Tester Signature: | Date: |
| --- | --- | --- | --- |

Emerson Automation Solutions

Product Development Department

200 Beta Drive

Pittsburgh, PA 15238

The standalone controller may be either simplex or redundant.