| PWS DIRECTION STATEMENT REQUIREMENTS DOCUMENT |  |  |  |  |
| --- | --- | --- | --- | --- |
| Project Name | Web HMI | Date Submitted | 8/27/2025 |  |
| Created By: | Scott Szymanski | SRF /SDR # | 2435 |  |
| Product Dev Mgr(s) | Rick Kephart | Revision | 1.0 |  |
| Justification: Customer CCL or Strategic Items | Strategic |  |  |  |
| Hardware Requirements |  |  |  |  |
| System Constraints | Ovation 3.8, Ovation 4.0 |  |  |  |
| Assumption | None |  |  |  |
| Risks | None |  |  |  |

| Req. Number | Description |
| --- | --- |
| - Web HMI Applications |  |
| 1.1 | All applications shall be hosted by the Data Hub and be accessible from the Data Hub’s home page. The Data Hub will provide the authentication to only allow authorized users to access the applications. |
| 1.2 | All applications shall show the connection status with the Data Hub so users know if the application is being updated. |
| 1.3 | Dynamic values in the applications shall have a once a second refresh rate unless otherwise stated |
| 1.4 | All applications shall support multinetworking points |
| 1.5 | All applications shall support droplet points. |
| 1.6 | All applications shall support a light and dark theme. Note: Alarm colors and other standard Ovation colors that denote important state information to the operator should not be modified based on the theme. |
| 1.7 | All applications shall support the standard Ovation security for user roles and point security groups for control actions. A new “Web Console” permission will be added to the security manager for these applications. |
| 1.8 | All applications shall support localizations for operators to see text in their native language. |
| 1.9 | All applications shall support saving the user preferences. These preferences shall be able to be saved at the user, role or system level. These preferences should be stored separately from the desktop app preferences. |
| 1.10 | Each application will require its own license. |
| 2.0 Point Information |  |
| 2.1 | The application shall attempt to match the look and behavior of the desktop version to minimize the need for operator training. |
| 2.2 | The application shall display all the point’s record fields based on the point type. |
| 2.3 | The application shall display the current value and change the color based on the point’s alarm state and quality |
| 2.4 | The application shall display the alarm point icon based on the configuration defined in Dev Studio. |
| 2.5 | The users shall be able to search for points on the system |
| 2.6 | The application shall display I/O hardware information. |
| 2.7 | The application shall display the point ancillary fields. |
| 2.8 | The application shall support the ribbon bar functionality to modify point attributes such as scan, test mode, alarm checking, acknowledge/reset alarms, etc. |
| 2.9 | The application shall provide a confirmation dialog before issuing actions such as removing a point from scan from the ribbon bar. |
| 2.10 | The application shall support standard right-click mouse functionality to navigate to other Web HMI apps, perform operations like alarm shelving. The web app should show the current active window (green icon on status bar). |
| 2.11 | The application shall support being able to display the “Where Used” references for a point on the system. |
| 2.12 | The application shall support modifying point record fields that can be changed using the desktop application such as analog alarm limits. |
| 2.13 | The application shall send the appropriate operator event messages to the OPH when the user modifies the state of the point. |
| 3.0 Signal Diagrams |  |
| 3.1 | The application shall match the look and behavior of the desktop version to minimize the need for training. |
| 3.2 | The signal diagram SVG files shall be used to render the control sheets in the web application without modification or translation. This keeps the obfuscation in place to protect Emerson’s IP. |
| 3.3 | The application shall allow panning and zooming of the control sheets |
| 3.4 | The application shall zoom to full screen when the user double clicks on an empty part of the signal diagram canvas. |
| 3.5 | The users shall be able to select an algorithm to display the current values of all the points associated with the algorithm (Algorithm summary tab) |
| 3.6 | The users shall be able to select an algorithm to display the current tuning constants associated with the algorithm (Properties Summary Tab). The application shall display the green checkmark or yellow warning icon to indicate if the associated algorithm has been loaded properly on the system. |
| 3.7 | The user shall be able to change the value of tuning constants for an algorithm (Properties Summary Tab). The application shall validate the user input to make sure the entered value is within the valid range for that parameter. |
| 3.8 | The user shall be able to send control actions for KEYBOARDS, SETPOINT, and MASTATION (Algorithm Control Tab). Energy management algorithms and Fieldbus algorithms also support control actions. |
| 3.9 | The application shall send the appropriate operator event messages to the OPH when the user changes control state or tunes an algorithm. |
| 3.10 | The application shall show the function summary tab information for the active control sheet. |
| 3.11 | The application shall show the current value for a point on the signal line |
| 3.12 | The application shall show the pin labels for the algorithms. |
| 3.13 | The application shall properly calculate and show the state of the Fast Boolean logic. |
| 3.14 | The application shall change the color of the signal lines for the following conditions: - Timed out - magenta - Scan off - blue - Alarm - magenta - Bad quality - gray - Local mode - cyan - Manual Mode - red - Tracking – green - Digital True / False state - red |
| 3.15 | The users shall be able to select a signal diagram to view from a list of all the control sheets on the system |
| 3.16 | The users shall be able to use the keyboard arrow keys to traverse through the control sheets on the system |
| 3.17 | The application shall support page connectors to navigate to other control sheets where a point is used. The navigation menu shall be supported on all algorithms to match the behavior of the desktop signal diagram viewer. |
| 3.18 | The application shall support all algorithm overlays to indicate the following conditions: - Timed out – hourglass - Off scan – No symbol - Alarm – bell - Bad quality – Exclamation mark - Raise and Lower inhibits |
| 3.19 | The application shall be able to display the permissives for a control sheet. This is a separate application in the desktop version that is typically called from the graphics. |
| 3.20 | The users shall be able to explode control macros and view the logic. |
| 3.21 | The application shall support the find point feature on the toolbar to find all control sheets where a point is referenced |
| 3.22 | The application shall support the sequence function charts for the SCTask algorithm. This is called the SFC Overview. |
| 3.23 | The application shall support rendering the SFC algorithms that are not drawn in the SVG files like standard algorithms. |
| 3.24 | The application shall support standard right-click mouse functionality to navigate to other Web HMI apps and perform operations like alarm shelving. |
| 3.25 | The application will not support droplets. This functionality is also not supported in the desktop application. |
| 3.26 | The application shall support the green checkmark functionality in the lower right corner of the application to indicate to the user whether the control sheet has been properly loaded and is up-to-date. The SHEETMON algorithm provides this functionality. |
| 3.27 | The application shall support the custom tuning windows for advanced algorithms including SIS. (This will probably not make it in initial release) |
| 3.28 | The application shall support the contextual help documentation links for algorithms. |
| 3.29 | The application shall support password protected control sheets and macros. The application shall prompt the user for the password and only open the file if the correct password is provided. |
| 4.0 View HMI |  |
| 4.1 | The application shall match the look and behavior of the desktop version to minimize the need for training. |
| 4.2 | The web application shall display the html graphic files without modification or translation. |
| 4.3 | The web application shall support all the toolbox widgets in the web environment. |
| 4.4 | The web application shall support all the application programs in the web environment. |
| 4.5 | The web application shall support a read-only mode for customers that do not wish to modify the system remotely. |
| 4.6 | The application shall support standard right-click mouse functionality to navigate to other Web HMI apps and perform operations like alarm shelving. |
| 4.7 | The application shall support each user being able to save their own preferences such as the default and home displays. |
| 4.8 | The application shall support the localization functionality from the desktop version. |